## EQUIPS
EQUIPS DEL SISTEMA DE CONTROL
Tipologia | Identificació instal·lació
SENSORS / SENYALS
ALARMES
QUADRES DE CONTROL
BUS
SOFTWARE
HARDWARE
ELEMENTS DE REGULACIÓ

## FREQÜÈNCIES
FREQÜÈNCIES DE MANTENIMENT D'ELEMENTS DE CONTROL
MENSUAL
SISTEMES I EQUIPS DE REGULACIÓ I CONTROL
Inspecció de l'estat dels elements emissors i receptors d'alarmes
Simulació d'alarmes i comprovació de la seva notificació sobre els terminals
o impressores predefinides
Comprovació de la notificació remota d'alarmes
ANUAL
SISTEMES I EQUIPS DE REGULACIÓ I CONTROL
Inspecció i collament de connexions elèctriques
Comprovació i neteja de fitxers en els discos durs
Verificació d'espais ocupats en discos durs i disponibilitats de memòria
Avaluació de l'obsolescència del hardware instal·lat, sistema operatiu i software d'aplicació
Comprovació i actualització, si escau, de la documentació tècnica del sistema de control
Verificació de l'estat dels quadres de control. Neteja interior, collament de connexions
i protecció antihumitat
Verificació d'esquemes de conexionnat de quadres de control i actualització, si escau
Inspecció de programes i gràfics implantats incloent simulació per canvi de variables
CADA 2 ANYS
SISTEMES I EQUIPS DE REGULACIÓ I CONTROL
Verificació d'estat i funcionament de reòstats de regulació analògica. Ajust, si escau
Verificació d'estat i funcionament de pressòstats. Correcció de fuites i ajust, si escau
Verificació d'estat de tubs capil·lars de pressòstats i sensors de pressió.
Neteja o substitució, si escau
Verificació d'estat i funcionament de humidostats. Ajust, si escau
Verificació d'estat i funcionament de programadors de lleves i controladors per etapes.
Ajust, si procedeix
Verificació d'estat i funcionament de vàlvules de regulació d'acord
amb el senyal de comandament. Comprovació de recorreguts i finals de carrera i ajust, si escau
Verificació d'estat i funcionament de comportes de regulació d'acord
amb el senyal de comandament. Comprovació de recorreguts i finals de carrera i ajust, si escau
Verificació d'estat i funcionament de temporitzadors i programadors.
Collament de connexions elèctriques i ajust, si escau
Comprovació del funcionament del conjunt del sistema de regulació i control
Inspecció de circuits elèctrics d'alimentació: fonts de tensió estabilitzada,
interruptors, proteccions i senyalització, i de les seves connexions
Inspecció de circuits de senyal i “busos” de comunicació. Verificació de cablejats
i connexions
Verificació d'estat i actuació de sensors i controls de temperatura i termòstats
Verificació d'estat i actuació de controls de pressió, transductors i pressòstats
Verificació d'estat i actuació de controls d'humitat, sondes i humidostats.
Comprovació d'entrades analògiques i digitals en mòduls i centraletes. Connexions i senyals
Comprovació de sortides analògiques i digitals en mòduls i centraletes. Connexions i senyals
Comprovació d'entrades de senyals en actuadors, servomotors, vàlvules automàtiques
i receptors
Verificació de dades i paràmetres de configuració en el controlador principal i ajust, si escau
Verificació de lògiques de control i comprovació del comportament del sistema en funció
de la programació establerta. Modificacions i ajustos, si escau.
Comprovació general d'estat i funcionament de pantalles, teclats,
impressores i perifèrics
Verificació de l'estat de discos durs de l'ordinador central (escanejat i desfragmentació
si escau)
Verificació del canvi d'horari hivern/estiu
Verificació del funcionament de la impressió d'informes, gràfics o tendències
Comprovació de l'arrencada del lloc central de gestió després d'una fallada del subministrament de tensió
Verificació de funcionament dels Sistemes d'Alimentació Ininterrompuda (SAI)
Inspecció de l'estabilitat i precisió dels bucles de control, seqüències i horaris
Comprovació de l'estat i actuació sondes i sensors i llaços de regulació
Verificació de reglatges i valors de consigna. Ajust i calibratge d'elements de regulació
NORMATIVA
Compliment de les operacions i freqüències establertes per les legislacions vigents

## BACNET
|  |  | (All) | (All)
MSA_BM_Cl_MFZCE.Estado_vent_imp | 192.168.4.21 | BV:11:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_MFZCE.Orden_recuperador | 192.168.4.21 | BV:12:PRESENT-VALUE | Read | Always
MSA_BM_Cl_MFZCE.Orden_humectador | 192.168.4.21 | BV:13:PRESENT-VALUE | Read | Always
MSA_BM_Cl_MFZCE.Mando_EXD | 192.168.4.21 | BV:14:PRESENT-VALUE | Read | Always
MSA_BM_Cl_MFZCE.Temp_retorno | 192.168.4.21 | AI:1201:PRESENT-VALUE | Read | Always
MSA_BM_Cl_MFZCE.HR_retorno | 192.168.4.21 | AI:1202:PRESENT-VALUE | Read | Always
MSA_BM_Cl_MFZCE.Temp_impulsion | 192.168.4.21 | AI:1401:PRESENT-VALUE | Read | Always
MSA_BM_Cl_MFZCE.HR_impulsion | 192.168.4.21 | AI:1402:PRESENT-VALUE | Read | Always
MSA_BM_Cl_MFZCE.Calidad_Aire | 192.168.4.21 | AI:2104:PRESENT-VALUE | Read | Always
MSA_BM_Cl_MFZCE.Cons_temp_retorno | 192.168.4.21 | AV:11:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_MFZCE.Zona_Muerta | 192.168.4.21 | AV:12:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_MFZCE.Max_temp_impulsion | 192.168.4.21 | AV:13:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_MFZCE.Min_temp_impulsion | 192.168.4.21 | AV:14:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_MFZCE.Cons_HR_retorno | 192.168.4.21 | AV:15:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_MFZCE.Lim_max_HR_impulsion | 192.168.4.21 | AV:18:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_MFZCE.Consigna_CO2 | 192.168.4.21 | AV:19:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_MFZCE.Minimo_aire_renovacion | 192.168.4.21 | AV:20:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_MFZCE.Maximo_aire_renovacion | 192.168.4.21 | AV:21:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_MFZCE.Mando_valvula | 192.168.4.21 | AO:1402:PRESENT-VALUE | Read | Always
MSA_BM_Cl_MFZCE.Mando_comp_recup | 192.168.4.21 | AO:1104:PRESENT-VALUE | Read | Always
MSA_BM_Cl_MFZCE.Mando_comp_exterior | 192.168.4.21 | AO:1201:PRESENT-VALUE | Read | Always
MSA_BM_Cl_MFZCE.Mando_comp_bypass_ret | 192.168.4.21 | AO:1202:PRESENT-VALUE | Read | Always
MSA_BM_Cl_MFZCE.Mando_humectador | 192.168.4.21 | AO:2402:PRESENT-VALUE | Read | Always
MSA_BM_Cl_MFZCA.Estado_vent_imp | 192.168.4.21 | BV:31:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_MFZCA.Orden_recuperador | 192.168.4.21 | BV:32:PRESENT-VALUE | Read | Always
MSA_BM_Cl_MFZCA.Orden_humectador | 192.168.4.21 | BV:33:PRESENT-VALUE | Read | Always
MSA_BM_Cl_MFZCA.Mando_EXD | 192.168.4.21 | BV:34:PRESENT-VALUE | Read | Always
MSA_BM_Cl_MFZCA.Temp_retorno | 192.168.4.21 | AI:1203:PRESENT-VALUE | Read | Always
MSA_BM_Cl_MFZCA.HR_retorno | 192.168.4.21 | AI:1204:PRESENT-VALUE | Read | Always
MSA_BM_Cl_MFZCA.Temp_impulsion | 192.168.4.21 | AI:1403:PRESENT-VALUE | Read | Always
MSA_BM_Cl_MFZCA.HR_impulsion | 192.168.4.21 | AI:1404:PRESENT-VALUE | Read | Always
MSA_BM_Cl_MFZCA.Calidad_Aire | 192.168.4.21 | AI:2201:PRESENT-VALUE | Read | Always
MSA_BM_Cl_MFZCA.Cons_temp_retorno | 192.168.4.21 | AV:31:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_MFZCA.Zona_Muerta | 192.168.4.21 | AV:32:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_MFZCA.Max_temp_impulsion | 192.168.4.21 | AV:33:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_MFZCA.Min_temp_impulsion | 192.168.4.21 | AV:34:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_MFZCA.Cons_HR_retorno | 192.168.4.21 | AV:35:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_MFZCA.Lim_max_HR_impulsion | 192.168.4.21 | AV:38:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_MFZCA.Consigna_CO2 | 192.168.4.21 | AV:39:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_MFZCA.Minimo_aire_renovacion | 192.168.4.21 | AV:40:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_MFZCA.Maximo_aire_renovacion | 192.168.4.21 | AV:41:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_MFZCA.Mando_valvula | 192.168.4.21 | AO:1403:PRESENT-VALUE | Read | Always
MSA_BM_Cl_MFZCA.Mando_comp_recup | 192.168.4.21 | AO:1203:PRESENT-VALUE | Read | Always
MSA_BM_Cl_MFZCA.Mando_comp_exterior | 192.168.4.21 | AO:1204:PRESENT-VALUE | Read | Always
MSA_BM_Cl_MFZCA.Mando_comp_bypass_ret | 192.168.4.21 | AO:1301:PRESENT-VALUE | Read | Always
MSA_BM_Cl_MFZCA.Mando_humectador | 192.168.4.21 | AO:2403:PRESENT-VALUE | Read | Always
MSA_BM_Cl_ESE.Estado_vent_imp | 192.168.4.21 | BV:51:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_ESE.Orden_recuperador | 192.168.4.21 | BV:52:PRESENT-VALUE | Read | Always
MSA_BM_Cl_ESE.Orden_humectador | 192.168.4.21 | BV:53:PRESENT-VALUE | Read | Always
MSA_BM_Cl_ESE.Mando_EXD | 192.168.4.21 | BV:54:PRESENT-VALUE | Read | Always
MSA_BM_Cl_ESE.Temp_retorno | 192.168.4.21 | AI:1103:PRESENT-VALUE | Read | Always
MSA_BM_Cl_ESE.HR_retorno | 192.168.4.21 | AI:1104:PRESENT-VALUE | Read | Always
MSA_BM_Cl_ESE.Temp_impulsion | 192.168.4.21 | AI:1303:PRESENT-VALUE | Read | Always
MSA_BM_Cl_ESE.HR_impulsion | 192.168.4.21 | AI:1304:PRESENT-VALUE | Read | Always
MSA_BM_Cl_ESE.Calidad_Aire | 192.168.4.21 | AI:2103:PRESENT-VALUE | Read | Always
MSA_BM_Cl_ESE.Cons_temp_retorno | 192.168.4.21 | AV:51:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_ESE.Zona_Muerta | 192.168.4.21 | AV:52:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_ESE.Max_temp_impulsion | 192.168.4.21 | AV:53:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_ESE.Min_temp_impulsion | 192.168.4.21 | AV:54:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_ESE.Cons_HR_retorno | 192.168.4.21 | AV:55:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_ESE.Lim_max_HR_impulsion | 192.168.4.21 | AV:58:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_ESE.Consigna_CO2 | 192.168.4.21 | AV:59:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_ESE.Minimo_aire_renovacion | 192.168.4.21 | AV:60:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_ESE.Maximo_aire_renovacion | 192.168.4.21 | AV:61:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_ESE.Mando_valvula | 192.168.4.21 | AO:1401:PRESENT-VALUE | Read | Always
MSA_BM_Cl_ESE.Mando_comp_recup | 192.168.4.21 | AO:1101:PRESENT-VALUE | Read | Always
MSA_BM_Cl_ESE.Mando_comp_exterior | 192.168.4.21 | AO:1102:PRESENT-VALUE | Read | Always
MSA_BM_Cl_ESE.Mando_comp_bypass_ret | 192.168.4.21 | AO:1103:PRESENT-VALUE | Read | Always
MSA_BM_Cl_ESE.Mando_humectador | 192.168.4.21 | AO:2401:PRESENT-VALUE | Read | Always
MSA_BM_Cl_ESD.Estado_vent_imp | 192.168.4.21 | BV:71:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_ESD.Orden_recuperador | 192.168.4.21 | BV:72:PRESENT-VALUE | Read | Always
MSA_BM_Cl_ESD.Orden_humectador | 192.168.4.21 | BV:73:PRESENT-VALUE | Read | Always
MSA_BM_Cl_ESD.Mando_EXD | 192.168.4.21 | BV:74:PRESENT-VALUE | Read | Always
MSA_BM_Cl_ESD.Temp_retorno | 192.168.4.21 | AI:1301:PRESENT-VALUE | Read | Always
MSA_BM_Cl_ESD.HR_retorno | 192.168.4.21 | AI:1302:PRESENT-VALUE | Read | Always
MSA_BM_Cl_ESD.Temp_impulsion | 192.168.4.21 | AI:2101:PRESENT-VALUE | Read | Always
MSA_BM_Cl_ESD.HR_impulsion | 192.168.4.21 | AI:2102:PRESENT-VALUE | Read | Always
MSA_BM_Cl_ESD.Calidad_Aire | 192.168.4.21 | AI:2202:PRESENT-VALUE | Read | Always
MSA_BM_Cl_ESD.Cons_temp_retorno | 192.168.4.21 | AV:71:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_ESD.Zona_Muerta | 192.168.4.21 | AV:72:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_ESD.Max_temp_impulsion | 192.168.4.21 | AV:73:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_ESD.Min_temp_impulsion | 192.168.4.21 | AV:74:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_ESD.Cons_HR_retorno | 192.168.4.21 | AV:75:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_ESD.Lim_max_HR_impulsion | 192.168.4.21 | AV:78:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_ESD.Consigna_CO2 | 192.168.4.21 | AV:79:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_ESD.Minimo_aire_renovacion | 192.168.4.21 | AV:80:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_ESD.Maximo_aire_renovacion | 192.168.4.21 | AV:81:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_ESD.Mando_valvula | 192.168.4.21 | AO:1404:PRESENT-VALUE | Read | Always
MSA_BM_Cl_ESD.Mando_comp_recup | 192.168.4.21 | AO:1302:PRESENT-VALUE | Read | Always
MSA_BM_Cl_ESD.Mando_comp_exterior | 192.168.4.21 | AO:1303:PRESENT-VALUE | Read | Always
MSA_BM_Cl_ESD.Mando_comp_bypass_ret | 192.168.4.21 | AO:1304:PRESENT-VALUE | Read | Always
MSA_BM_Cl_ESD.Mando_humectador | 192.168.4.21 | AO:2404:PRESENT-VALUE | Read | Always
MSA_BT_Cl_MFZCE.Estado_vent_imp | 192.168.4.31 | BV:11:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_MFZCE.Orden_recuperador | 192.168.4.31 | BV:12:PRESENT-VALUE | Read | Always
MSA_BT_Cl_MFZCE.Orden_humectador | 192.168.4.31 | BV:13:PRESENT-VALUE | Read | Always
MSA_BT_Cl_MFZCE.Mando_EXD | 192.168.4.31 | BV:14:PRESENT-VALUE | Read | Always
MSA_BT_Cl_MFZCE.Temp_retorno | 192.168.4.31 | AI:1201:PRESENT-VALUE | Read | Always
MSA_BT_Cl_MFZCE.HR_retorno | 192.168.4.31 | AI:1202:PRESENT-VALUE | Read | Always
MSA_BT_Cl_MFZCE.Temp_impulsion | 192.168.4.31 | AI:1401:PRESENT-VALUE | Read | Always
MSA_BT_Cl_MFZCE.HR_impulsion | 192.168.4.31 | AI:1402:PRESENT-VALUE | Read | Always
MSA_BT_Cl_MFZCE.Calidad_Aire | 192.168.4.31 | AI:2104:PRESENT-VALUE | Read | Always
MSA_BT_Cl_MFZCE.Cons_temp_retorno | 192.168.4.31 | AV:11:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_MFZCE.Zona_Muerta | 192.168.4.31 | AV:12:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_MFZCE.Max_temp_impulsion | 192.168.4.31 | AV:13:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_MFZCE.Min_temp_impulsion | 192.168.4.31 | AV:14:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_MFZCE.Cons_HR_retorno | 192.168.4.31 | AV:15:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_MFZCE.Lim_max_HR_impulsion | 192.168.4.31 | AV:18:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_MFZCE.Consigna_CO2 | 192.168.4.31 | AV:19:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_MFZCE.Minimo_aire_renovacion | 192.168.4.31 | AV:20:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_MFZCE.Maximo_aire_renovacion | 192.168.4.31 | AV:21:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_MFZCE.Mando_valvula | 192.168.4.31 | AO:1402:PRESENT-VALUE | Read | Always
MSA_BT_Cl_MFZCE.Mando_comp_recup | 192.168.4.31 | AO:1104:PRESENT-VALUE | Read | Always
MSA_BT_Cl_MFZCE.Mando_comp_exterior | 192.168.4.31 | AO:1201:PRESENT-VALUE | Read | Always
MSA_BT_Cl_MFZCE.Mando_comp_bypass_ret | 192.168.4.31 | AO:1202:PRESENT-VALUE | Read | Always
MSA_BT_Cl_MFZCE.Mando_humectador | 192.168.4.31 | AO:2402:PRESENT-VALUE | Read | Always
MSA_BT_Cl_MFZCA.Estado_vent_imp | 192.168.4.31 | BV:31:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_MFZCA.Orden_recuperador | 192.168.4.31 | BV:32:PRESENT-VALUE | Read | Always
MSA_BT_Cl_MFZCA.Orden_humectador | 192.168.4.31 | BV:33:PRESENT-VALUE | Read | Always
MSA_BT_Cl_MFZCA.Mando_EXD | 192.168.4.31 | BV:34:PRESENT-VALUE | Read | Always
MSA_BT_Cl_MFZCA.Temp_retorno | 192.168.4.31 | AI:1203:PRESENT-VALUE | Read | Always
MSA_BT_Cl_MFZCA.HR_retorno | 192.168.4.31 | AI:1204:PRESENT-VALUE | Read | Always
MSA_BT_Cl_MFZCA.Temp_impulsion | 192.168.4.31 | AI:1403:PRESENT-VALUE | Read | Always
MSA_BT_Cl_MFZCA.HR_impulsion | 192.168.4.31 | AI:1404:PRESENT-VALUE | Read | Always
MSA_BT_Cl_MFZCA.Calidad_Aire | 192.168.4.31 | AI:2201:PRESENT-VALUE | Read | Always
MSA_BT_Cl_MFZCA.Cons_temp_retorno | 192.168.4.31 | AV:31:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_MFZCA.Zona_Muerta | 192.168.4.31 | AV:32:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_MFZCA.Max_temp_impulsion | 192.168.4.31 | AV:33:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_MFZCA.Min_temp_impulsion | 192.168.4.31 | AV:34:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_MFZCA.Cons_HR_retorno | 192.168.4.31 | AV:35:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_MFZCA.Lim_max_HR_impulsion | 192.168.4.31 | AV:38:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_MFZCA.Consigna_CO2 | 192.168.4.31 | AV:39:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_MFZCA.Minimo_aire_renovacion | 192.168.4.31 | AV:40:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_MFZCA.Maximo_aire_renovacion | 192.168.4.31 | AV:41:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_MFZCA.Mando_valvula | 192.168.4.31 | AO:1403:PRESENT-VALUE | Read | Always
MSA_BT_Cl_MFZCA.Mando_comp_recup | 192.168.4.31 | AO:1203:PRESENT-VALUE | Read | Always
MSA_BT_Cl_MFZCA.Mando_comp_exterior | 192.168.4.31 | AO:1204:PRESENT-VALUE | Read | Always
MSA_BT_Cl_MFZCA.Mando_comp_bypass_ret | 192.168.4.31 | AO:1301:PRESENT-VALUE | Read | Always
MSA_BT_Cl_MFZCA.Mando_humectador | 192.168.4.31 | AO:2403:PRESENT-VALUE | Read | Always
MSA_BT_Cl_ESE.Estado_vent_imp | 192.168.4.31 | BV:51:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_ESE.Orden_recuperador | 192.168.4.31 | BV:52:PRESENT-VALUE | Read | Always
MSA_BT_Cl_ESE.Orden_humectador | 192.168.4.31 | BV:53:PRESENT-VALUE | Read | Always
MSA_BT_Cl_ESE.Mando_EXD | 192.168.4.31 | BV:54:PRESENT-VALUE | Read | Always
MSA_BT_Cl_ESE.Temp_retorno | 192.168.4.31 | AI:1103:PRESENT-VALUE | Read | Always
MSA_BT_Cl_ESE.HR_retorno | 192.168.4.31 | AI:1104:PRESENT-VALUE | Read | Always
MSA_BT_Cl_ESE.Temp_impulsion | 192.168.4.31 | AI:1303:PRESENT-VALUE | Read | Always
MSA_BT_Cl_ESE.HR_impulsion | 192.168.4.31 | AI:1304:PRESENT-VALUE | Read | Always
MSA_BT_Cl_ESE.Calidad_Aire | 192.168.4.31 | AI:2103:PRESENT-VALUE | Read | Always
MSA_BT_Cl_ESE.Cons_temp_retorno | 192.168.4.31 | AV:51:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_ESE.Zona_Muerta | 192.168.4.31 | AV:52:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_ESE.Max_temp_impulsion | 192.168.4.31 | AV:53:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_ESE.Min_temp_impulsion | 192.168.4.31 | AV:54:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_ESE.Cons_HR_retorno | 192.168.4.31 | AV:55:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_ESE.Lim_max_HR_impulsion | 192.168.4.31 | AV:58:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_ESE.Consigna_CO2 | 192.168.4.31 | AV:59:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_ESE.Minimo_aire_renovacion | 192.168.4.31 | AV:60:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_ESE.Maximo_aire_renovacion | 192.168.4.31 | AV:61:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_ESE.Mando_valvula | 192.168.4.31 | AO:1401:PRESENT-VALUE | Read | Always
MSA_BT_Cl_ESE.Mando_comp_recup | 192.168.4.31 | AO:1101:PRESENT-VALUE | Read | Always
MSA_BT_Cl_ESE.Mando_comp_exterior | 192.168.4.31 | AO:1102:PRESENT-VALUE | Read | Always
MSA_BT_Cl_ESE.Mando_comp_bypass_ret | 192.168.4.31 | AO:1103:PRESENT-VALUE | Read | Always
MSA_BT_Cl_ESE.Mando_humectador | 192.168.4.31 | AO:2401:PRESENT-VALUE | Read | Always
MSA_BT_Cl_ESD.Estado_vent_imp | 192.168.4.31 | BV:71:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_ESD.Orden_recuperador | 192.168.4.31 | BV:72:PRESENT-VALUE | Read | Always
MSA_BT_Cl_ESD.Orden_humectador | 192.168.4.31 | BV:73:PRESENT-VALUE | Read | Always
MSA_BT_Cl_ESD.Mando_EXD | 192.168.4.31 | BV:74:PRESENT-VALUE | Read | Always
MSA_BT_Cl_ESD.Temp_retorno | 192.168.4.31 | AI:1301:PRESENT-VALUE | Read | Always
MSA_BT_Cl_ESD.HR_retorno | 192.168.4.31 | AI:1302:PRESENT-VALUE | Read | Always
MSA_BT_Cl_ESD.Temp_impulsion | 192.168.4.31 | AI:2101:PRESENT-VALUE | Read | Always
MSA_BT_Cl_ESD.HR_impulsion | 192.168.4.31 | AI:2102:PRESENT-VALUE | Read | Always
MSA_BT_Cl_ESD.Calidad_Aire | 192.168.4.31 | AI:2202:PRESENT-VALUE | Read | Always
MSA_BT_Cl_ESD.Cons_temp_retorno | 192.168.4.31 | AV:71:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_ESD.Zona_Muerta | 192.168.4.31 | AV:72:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_ESD.Max_temp_impulsion | 192.168.4.31 | AV:73:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_ESD.Min_temp_impulsion | 192.168.4.31 | AV:74:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_ESD.Cons_HR_retorno | 192.168.4.31 | AV:75:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_ESD.Lim_max_HR_impulsion | 192.168.4.31 | AV:78:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_ESD.Consigna_CO2 | 192.168.4.31 | AV:79:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_ESD.Minimo_aire_renovacion | 192.168.4.31 | AV:80:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_ESD.Maximo_aire_renovacion | 192.168.4.31 | AV:81:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_ESD.Mando_valvula | 192.168.4.31 | AO:1404:PRESENT-VALUE | Read | Always
MSA_BT_Cl_ESD.Mando_comp_recup | 192.168.4.31 | AO:1302:PRESENT-VALUE | Read | Always
MSA_BT_Cl_ESD.Mando_comp_exterior | 192.168.4.31 | AO:1303:PRESENT-VALUE | Read | Always
MSA_BT_Cl_ESD.Mando_comp_bypass_ret | 192.168.4.31 | AO:1304:PRESENT-VALUE | Read | Always
MSA_BT_Cl_ESD.Mando_humectador | 192.168.4.31 | AO:2404:PRESENT-VALUE | Read | Always
MSA_UT_Cl_MFZCE.Estado_vent_imp | 192.168.4.41 | BV:11:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_MFZCE.Orden_recuperador | 192.168.4.41 | BV:12:PRESENT-VALUE | Read | Always
MSA_UT_Cl_MFZCE.Orden_humectador | 192.168.4.41 | BV:13:PRESENT-VALUE | Read | Always
MSA_UT_Cl_MFZCE.Mando_EXD | 192.168.4.41 | BV:14:PRESENT-VALUE | Read | Always
MSA_UT_Cl_MFZCE.Temp_retorno | 192.168.4.41 | AI:1201:PRESENT-VALUE | Read | Always
MSA_UT_Cl_MFZCE.HR_retorno | 192.168.4.41 | AI:1202:PRESENT-VALUE | Read | Always
MSA_UT_Cl_MFZCE.Temp_impulsion | 192.168.4.41 | AI:1401:PRESENT-VALUE | Read | Always
MSA_UT_Cl_MFZCE.HR_impulsion | 192.168.4.41 | AI:1402:PRESENT-VALUE | Read | Always
MSA_UT_Cl_MFZCE.Calidad_Aire | 192.168.4.41 | AI:2104:PRESENT-VALUE | Read | Always
MSA_UT_Cl_MFZCE.Cons_temp_retorno | 192.168.4.41 | AV:11:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_MFZCE.Zona_Muerta | 192.168.4.41 | AV:12:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_MFZCE.Max_temp_impulsion | 192.168.4.41 | AV:13:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_MFZCE.Min_temp_impulsion | 192.168.4.41 | AV:14:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_MFZCE.Cons_HR_retorno | 192.168.4.41 | AV:15:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_MFZCE.Lim_max_HR_impulsion | 192.168.4.41 | AV:18:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_MFZCE.Consigna_CO2 | 192.168.4.41 | AV:19:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_MFZCE.Minimo_aire_renovacion | 192.168.4.41 | AV:20:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_MFZCE.Maximo_aire_renovacion | 192.168.4.41 | AV:21:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_MFZCE.Mando_valvula | 192.168.4.41 | AO:1402:PRESENT-VALUE | Read | Always
MSA_UT_Cl_MFZCE.Mando_comp_recup | 192.168.4.41 | AO:1104:PRESENT-VALUE | Read | Always
MSA_UT_Cl_MFZCE.Mando_comp_exterior | 192.168.4.41 | AO:1201:PRESENT-VALUE | Read | Always
MSA_UT_Cl_MFZCE.Mando_comp_bypass_ret | 192.168.4.41 | AO:1202:PRESENT-VALUE | Read | Always
MSA_UT_Cl_MFZCE.Mando_humectador | 192.168.4.41 | AO:2402:PRESENT-VALUE | Read | Always
MSA_UT_Cl_MFZCA.Estado_vent_imp | 192.168.4.41 | BV:31:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_MFZCA.Orden_recuperador | 192.168.4.41 | BV:32:PRESENT-VALUE | Read | Always
MSA_UT_Cl_MFZCA.Orden_humectador | 192.168.4.41 | BV:33:PRESENT-VALUE | Read | Always
MSA_UT_Cl_MFZCA.Mando_EXD | 192.168.4.41 | BV:34:PRESENT-VALUE | Read | Always
MSA_UT_Cl_MFZCA.Temp_retorno | 192.168.4.41 | AI:1203:PRESENT-VALUE | Read | Always
MSA_UT_Cl_MFZCA.HR_retorno | 192.168.4.41 | AI:1204:PRESENT-VALUE | Read | Always
MSA_UT_Cl_MFZCA.Temp_impulsion | 192.168.4.41 | AI:1403:PRESENT-VALUE | Read | Always
MSA_UT_Cl_MFZCA.HR_impulsion | 192.168.4.41 | AI:1404:PRESENT-VALUE | Read | Always
MSA_UT_Cl_MFZCA.Calidad_Aire | 192.168.4.41 | AI:2201:PRESENT-VALUE | Read | Always
MSA_UT_Cl_MFZCA.Cons_temp_retorno | 192.168.4.41 | AV:31:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_MFZCA.Zona_Muerta | 192.168.4.41 | AV:32:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_MFZCA.Max_temp_impulsion | 192.168.4.41 | AV:33:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_MFZCA.Min_temp_impulsion | 192.168.4.41 | AV:34:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_MFZCA.Cons_HR_retorno | 192.168.4.41 | AV:35:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_MFZCA.Lim_max_HR_impulsion | 192.168.4.41 | AV:38:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_MFZCA.Consigna_CO2 | 192.168.4.41 | AV:39:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_MFZCA.Minimo_aire_renovacion | 192.168.4.41 | AV:40:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_MFZCA.Maximo_aire_renovacion | 192.168.4.41 | AV:41:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_MFZCA.Mando_valvula | 192.168.4.41 | AO:1403:PRESENT-VALUE | Read | Always
MSA_UT_Cl_MFZCA.Mando_comp_recup | 192.168.4.41 | AO:1203:PRESENT-VALUE | Read | Always
MSA_UT_Cl_MFZCA.Mando_comp_exterior | 192.168.4.41 | AO:1204:PRESENT-VALUE | Read | Always
MSA_UT_Cl_MFZCA.Mando_comp_bypass_ret | 192.168.4.41 | AO:1301:PRESENT-VALUE | Read | Always
MSA_UT_Cl_MFZCA.Mando_humectador | 192.168.4.41 | AO:2403:PRESENT-VALUE | Read | Always
MSA_UT_Cl_ESE.Estado_vent_imp | 192.168.4.41 | BV:51:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_ESE.Orden_recuperador | 192.168.4.41 | BV:52:PRESENT-VALUE | Read | Always
MSA_UT_Cl_ESE.Orden_humectador | 192.168.4.41 | BV:53:PRESENT-VALUE | Read | Always
MSA_UT_Cl_ESE.Mando_EXD | 192.168.4.41 | BV:54:PRESENT-VALUE | Read | Always
MSA_UT_Cl_ESE.Temp_retorno | 192.168.4.41 | AI:1103:PRESENT-VALUE | Read | Always
MSA_UT_Cl_ESE.HR_retorno | 192.168.4.41 | AI:1104:PRESENT-VALUE | Read | Always
MSA_UT_Cl_ESE.Temp_impulsion | 192.168.4.41 | AI:1303:PRESENT-VALUE | Read | Always
MSA_UT_Cl_ESE.HR_impulsion | 192.168.4.41 | AI:1304:PRESENT-VALUE | Read | Always
MSA_UT_Cl_ESE.Calidad_Aire | 192.168.4.41 | AI:2103:PRESENT-VALUE | Read | Always
MSA_UT_Cl_ESE.Cons_temp_retorno | 192.168.4.41 | AV:51:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_ESE.Zona_Muerta | 192.168.4.41 | AV:52:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_ESE.Max_temp_impulsion | 192.168.4.41 | AV:53:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_ESE.Min_temp_impulsion | 192.168.4.41 | AV:54:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_ESE.Cons_HR_retorno | 192.168.4.41 | AV:55:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_ESE.Lim_max_HR_impulsion | 192.168.4.41 | AV:58:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_ESE.Consigna_CO2 | 192.168.4.41 | AV:59:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_ESE.Minimo_aire_renovacion | 192.168.4.41 | AV:60:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_ESE.Maximo_aire_renovacion | 192.168.4.41 | AV:61:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_ESE.Mando_valvula | 192.168.4.41 | AO:1401:PRESENT-VALUE | Read | Always
MSA_UT_Cl_ESE.Mando_comp_recup | 192.168.4.41 | AO:1101:PRESENT-VALUE | Read | Always
MSA_UT_Cl_ESE.Mando_comp_exterior | 192.168.4.41 | AO:1102:PRESENT-VALUE | Read | Always
MSA_UT_Cl_ESE.Mando_comp_bypass_ret | 192.168.4.41 | AO:1103:PRESENT-VALUE | Read | Always
MSA_UT_Cl_ESE.Mando_humectador | 192.168.4.41 | AO:2401:PRESENT-VALUE | Read | Always
MSA_UT_Cl_ESD.Estado_vent_imp | 192.168.4.41 | BV:71:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_ESD.Orden_recuperador | 192.168.4.41 | BV:72:PRESENT-VALUE | Read | Always
MSA_UT_Cl_ESD.Orden_humectador | 192.168.4.41 | BV:73:PRESENT-VALUE | Read | Always
MSA_UT_Cl_ESD.Mando_EXD | 192.168.4.41 | BV:74:PRESENT-VALUE | Read | Always
MSA_UT_Cl_ESD.Temp_retorno | 192.168.4.41 | AI:1301:PRESENT-VALUE | Read | Always
MSA_UT_Cl_ESD.HR_retorno | 192.168.4.41 | AI:1302:PRESENT-VALUE | Read | Always
MSA_UT_Cl_ESD.Temp_impulsion | 192.168.4.41 | AI:2101:PRESENT-VALUE | Read | Always
MSA_UT_Cl_ESD.HR_impulsion | 192.168.4.41 | AI:2102:PRESENT-VALUE | Read | Always
MSA_UT_Cl_ESD.Calidad_Aire | 192.168.4.41 | AI:2202:PRESENT-VALUE | Read | Always
MSA_UT_Cl_ESD.Cons_temp_retorno | 192.168.4.41 | AV:71:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_ESD.Zona_Muerta | 192.168.4.41 | AV:72:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_ESD.Max_temp_impulsion | 192.168.4.41 | AV:73:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_ESD.Min_temp_impulsion | 192.168.4.41 | AV:74:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_ESD.Cons_HR_retorno | 192.168.4.41 | AV:75:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_ESD.Lim_max_HR_impulsion | 192.168.4.41 | AV:78:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_ESD.Consigna_CO2 | 192.168.4.41 | AV:79:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_ESD.Minimo_aire_renovacion | 192.168.4.41 | AV:80:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_ESD.Maximo_aire_renovacion | 192.168.4.41 | AV:81:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_ESD.Mando_valvula | 192.168.4.41 | AO:1404:PRESENT-VALUE | Read | Always
MSA_UT_Cl_ESD.Mando_comp_recup | 192.168.4.41 | AO:1302:PRESENT-VALUE | Read | Always
MSA_UT_Cl_ESD.Mando_comp_exterior | 192.168.4.41 | AO:1303:PRESENT-VALUE | Read | Always
MSA_UT_Cl_ESD.Mando_comp_bypass_ret | 192.168.4.41 | AO:1304:PRESENT-VALUE | Read | Always
MSA_UT_Cl_ESD.Mando_humectador | 192.168.4.41 | AO:2404:PRESENT-VALUE | Read | Always
MSA_UM_Cl_MFZCE.Estado_vent_imp | 192.168.4.51 | BV:11:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_MFZCE.Orden_recuperador | 192.168.4.51 | BV:12:PRESENT-VALUE | Read | Always
MSA_UM_Cl_MFZCE.Orden_humectador | 192.168.4.51 | BV:13:PRESENT-VALUE | Read | Always
MSA_UM_Cl_MFZCE.Mando_EXD | 192.168.4.51 | BV:14:PRESENT-VALUE | Read | Always
MSA_UM_Cl_MFZCE.Temp_retorno | 192.168.4.51 | AI:1201:PRESENT-VALUE | Read | Always
MSA_UM_Cl_MFZCE.HR_retorno | 192.168.4.51 | AI:1202:PRESENT-VALUE | Read | Always
MSA_UM_Cl_MFZCE.Temp_impulsion | 192.168.4.51 | AI:1401:PRESENT-VALUE | Read | Always
MSA_UM_Cl_MFZCE.HR_impulsion | 192.168.4.51 | AI:1402:PRESENT-VALUE | Read | Always
MSA_UM_Cl_MFZCE.Calidad_Aire | 192.168.4.51 | AI:2104:PRESENT-VALUE | Read | Always
MSA_UM_Cl_MFZCE.Cons_temp_retorno | 192.168.4.51 | AV:11:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_MFZCE.Zona_Muerta | 192.168.4.51 | AV:12:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_MFZCE.Max_temp_impulsion | 192.168.4.51 | AV:13:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_MFZCE.Min_temp_impulsion | 192.168.4.51 | AV:14:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_MFZCE.Cons_HR_retorno | 192.168.4.51 | AV:15:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_MFZCE.Lim_max_HR_impulsion | 192.168.4.51 | AV:18:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_MFZCE.Consigna_CO2 | 192.168.4.51 | AV:19:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_MFZCE.Minimo_aire_renovacion | 192.168.4.51 | AV:20:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_MFZCE.Maximo_aire_renovacion | 192.168.4.51 | AV:21:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_MFZCE.Mando_valvula | 192.168.4.51 | AO:1402:PRESENT-VALUE | Read | Always
MSA_UM_Cl_MFZCE.Mando_comp_recup | 192.168.4.51 | AO:1104:PRESENT-VALUE | Read | Always
MSA_UM_Cl_MFZCE.Mando_comp_exterior | 192.168.4.51 | AO:1201:PRESENT-VALUE | Read | Always
MSA_UM_Cl_MFZCE.Mando_comp_bypass_ret | 192.168.4.51 | AO:1202:PRESENT-VALUE | Read | Always
MSA_UM_Cl_MFZCE.Mando_humectador | 192.168.4.51 | AO:2402:PRESENT-VALUE | Read | Always
MSA_UM_Cl_MFZCA.Estado_vent_imp | 192.168.4.51 | BV:31:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_MFZCA.Orden_recuperador | 192.168.4.51 | BV:32:PRESENT-VALUE | Read | Always
MSA_UM_Cl_MFZCA.Orden_humectador | 192.168.4.51 | BV:33:PRESENT-VALUE | Read | Always
MSA_UM_Cl_MFZCA.Mando_EXD | 192.168.4.51 | BV:34:PRESENT-VALUE | Read | Always
MSA_UM_Cl_MFZCA.Temp_retorno | 192.168.4.51 | AI:1203:PRESENT-VALUE | Read | Always
MSA_UM_Cl_MFZCA.HR_retorno | 192.168.4.51 | AI:1204:PRESENT-VALUE | Read | Always
MSA_UM_Cl_MFZCA.Temp_impulsion | 192.168.4.51 | AI:1403:PRESENT-VALUE | Read | Always
MSA_UM_Cl_MFZCA.HR_impulsion | 192.168.4.51 | AI:1404:PRESENT-VALUE | Read | Always
MSA_UM_Cl_MFZCA.Calidad_Aire | 192.168.4.51 | AI:2201:PRESENT-VALUE | Read | Always
MSA_UM_Cl_MFZCA.Cons_temp_retorno | 192.168.4.51 | AV:31:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_MFZCA.Zona_Muerta | 192.168.4.51 | AV:32:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_MFZCA.Max_temp_impulsion | 192.168.4.51 | AV:33:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_MFZCA.Min_temp_impulsion | 192.168.4.51 | AV:34:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_MFZCA.Cons_HR_retorno | 192.168.4.51 | AV:35:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_MFZCA.Lim_max_HR_impulsion | 192.168.4.51 | AV:38:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_MFZCA.Consigna_CO2 | 192.168.4.51 | AV:39:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_MFZCA.Minimo_aire_renovacion | 192.168.4.51 | AV:40:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_MFZCA.Maximo_aire_renovacion | 192.168.4.51 | AV:41:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_MFZCA.Mando_valvula | 192.168.4.51 | AO:1403:PRESENT-VALUE | Read | Always
MSA_UM_Cl_MFZCA.Mando_comp_recup | 192.168.4.51 | AO:1203:PRESENT-VALUE | Read | Always
MSA_UM_Cl_MFZCA.Mando_comp_exterior | 192.168.4.51 | AO:1204:PRESENT-VALUE | Read | Always
MSA_UM_Cl_MFZCA.Mando_comp_bypass_ret | 192.168.4.51 | AO:1301:PRESENT-VALUE | Read | Always
MSA_UM_Cl_MFZCA.Mando_humectador | 192.168.4.51 | AO:2403:PRESENT-VALUE | Read | Always
MSA_UM_Cl_ESE.Estado_vent_imp | 192.168.4.51 | BV:51:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_ESE.Orden_recuperador | 192.168.4.51 | BV:52:PRESENT-VALUE | Read | Always
MSA_UM_Cl_ESE.Orden_humectador | 192.168.4.51 | BV:53:PRESENT-VALUE | Read | Always
MSA_UM_Cl_ESE.Mando_EXD | 192.168.4.51 | BV:54:PRESENT-VALUE | Read | Always
MSA_UM_Cl_ESE.Temp_retorno | 192.168.4.51 | AI:1103:PRESENT-VALUE | Read | Always
MSA_UM_Cl_ESE.HR_retorno | 192.168.4.51 | AI:1104:PRESENT-VALUE | Read | Always
MSA_UM_Cl_ESE.Temp_impulsion | 192.168.4.51 | AI:1303:PRESENT-VALUE | Read | Always
MSA_UM_Cl_ESE.HR_impulsion | 192.168.4.51 | AI:1304:PRESENT-VALUE | Read | Always
MSA_UM_Cl_ESE.Calidad_Aire | 192.168.4.51 | AI:2103:PRESENT-VALUE | Read | Always
MSA_UM_Cl_ESE.Cons_temp_retorno | 192.168.4.51 | AV:51:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_ESE.Zona_Muerta | 192.168.4.51 | AV:52:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_ESE.Max_temp_impulsion | 192.168.4.51 | AV:53:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_ESE.Min_temp_impulsion | 192.168.4.51 | AV:54:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_ESE.Cons_HR_retorno | 192.168.4.51 | AV:55:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_ESE.Lim_max_HR_impulsion | 192.168.4.51 | AV:58:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_ESE.Consigna_CO2 | 192.168.4.51 | AV:59:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_ESE.Minimo_aire_renovacion | 192.168.4.51 | AV:60:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_ESE.Maximo_aire_renovacion | 192.168.4.51 | AV:61:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_ESE.Mando_valvula | 192.168.4.51 | AO:1401:PRESENT-VALUE | Read | Always
MSA_UM_Cl_ESE.Mando_comp_recup | 192.168.4.51 | AO:1101:PRESENT-VALUE | Read | Always
MSA_UM_Cl_ESE.Mando_comp_exterior | 192.168.4.51 | AO:1102:PRESENT-VALUE | Read | Always
MSA_UM_Cl_ESE.Mando_comp_bypass_ret | 192.168.4.51 | AO:1103:PRESENT-VALUE | Read | Always
MSA_UM_Cl_ESE.Mando_humectador | 192.168.4.51 | AO:2401:PRESENT-VALUE | Read | Always
MSA_UM_Cl_ESD.Estado_vent_imp | 192.168.4.51 | BV:71:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_ESD.Orden_recuperador | 192.168.4.51 | BV:72:PRESENT-VALUE | Read | Always
MSA_UM_Cl_ESD.Orden_humectador | 192.168.4.51 | BV:73:PRESENT-VALUE | Read | Always
MSA_UM_Cl_ESD.Mando_EXD | 192.168.4.51 | BV:74:PRESENT-VALUE | Read | Always
MSA_UM_Cl_ESD.Temp_retorno | 192.168.4.51 | AI:1301:PRESENT-VALUE | Read | Always
MSA_UM_Cl_ESD.HR_retorno | 192.168.4.51 | AI:1302:PRESENT-VALUE | Read | Always
MSA_UM_Cl_ESD.Temp_impulsion | 192.168.4.51 | AI:2101:PRESENT-VALUE | Read | Always
MSA_UM_Cl_ESD.HR_impulsion | 192.168.4.51 | AI:2102:PRESENT-VALUE | Read | Always
MSA_UM_Cl_ESD.Calidad_Aire | 192.168.4.51 | AI:2202:PRESENT-VALUE | Read | Always
MSA_UM_Cl_ESD.Cons_temp_retorno | 192.168.4.51 | AV:71:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_ESD.Zona_Muerta | 192.168.4.51 | AV:72:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_ESD.Max_temp_impulsion | 192.168.4.51 | AV:73:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_ESD.Min_temp_impulsion | 192.168.4.51 | AV:74:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_ESD.Cons_HR_retorno | 192.168.4.51 | AV:75:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_ESD.Lim_max_HR_impulsion | 192.168.4.51 | AV:78:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_ESD.Consigna_CO2 | 192.168.4.51 | AV:79:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_ESD.Minimo_aire_renovacion | 192.168.4.51 | AV:80:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_ESD.Maximo_aire_renovacion | 192.168.4.51 | AV:81:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_ESD.Mando_valvula | 192.168.4.51 | AO:1404:PRESENT-VALUE | Read | Always
MSA_UM_Cl_ESD.Mando_comp_recup | 192.168.4.51 | AO:1302:PRESENT-VALUE | Read | Always
MSA_UM_Cl_ESD.Mando_comp_exterior | 192.168.4.51 | AO:1303:PRESENT-VALUE | Read | Always
MSA_UM_Cl_ESD.Mando_comp_bypass_ret | 192.168.4.51 | AO:1304:PRESENT-VALUE | Read | Always
MSA_UM_Cl_ESD.Mando_humectador | 192.168.4.51 | AO:2404:PRESENT-VALUE | Read | Always
MSA_BM_Exterior_Temperatura | 192.168.4.21 | AI:1101:PRESENT-VALUE | Read | Always
MSA_BM_Exterior_Humedad | 192.168.4.21 | AI:1102:PRESENT-VALUE | Read | Always
MSA_BT_Exterior_Temperatura | 192.168.4.31 | AI:1101:PRESENT-VALUE | Read | Always
MSA_BT_Exterior_Humedad | 192.168.4.31 | AI:1102:PRESENT-VALUE | Read | Always
MSA_UT_Exterior_Temperatura | 192.168.4.41 | AI:1101:PRESENT-VALUE | Read | Always
MSA_UT_Exterior_Humedad | 192.168.4.41 | AI:1102:PRESENT-VALUE | Read | Always
MSA_UM_Exterior_Temperatura | 192.168.4.51 | AI:1101:PRESENT-VALUE | Read | Always
MSA_UM_Exterior_Humedad | 192.168.4.51 | AI:1102:PRESENT-VALUE | Read | Always
MSA_BT_Bombas_UTAS_AF_Presion | 192.168.4.31 | AI:3301:PRESENT-VALUE | Read | Always
MSA_BT_Bombas_UTAS_AF_Consigna_presion | 192.168.4.31 | AV:101:PRESENT-VALUE | Read+Write | Always
MSA_BT_Bombas_UTAS_AF_1.Estado | 192.168.4.31 | BV:101:PRESENT-VALUE | Read+Write | Always
MSA_BT_Bombas_UTAS_AF_1.Mando_variador | 192.168.4.31 | AO:3201:PRESENT-VALUE | Read | Always
MSA_BT_Bombas_UTAS_AF_2.Estado | 192.168.4.31 | BV:102:PRESENT-VALUE | Read+Write | Always
MSA_BT_Bombas_UTAS_AF_2.Mando_variador | 192.168.4.31 | AO:3202:PRESENT-VALUE | Read | Always
MSA_BT_Bombas_UTAS_AC_Presion | 192.168.4.31 | AI:3401:PRESENT-VALUE | Read | Always
MSA_BT_Bombas_UTAS_AC_Consigna_presion | 192.168.4.31 | AV:103:PRESENT-VALUE | Read+Write | Always
MSA_BT_Bombas_UTAS_AC_1.Estado | 192.168.4.31 | BV:103:PRESENT-VALUE | Read+Write | Always
MSA_BT_Bombas_UTAS_AC_1.Mando_variador | 192.168.4.31 | AO:3203:PRESENT-VALUE | Read | Always
MSA_BT_Bombas_UTAS_AC_2.Estado | 192.168.4.31 | BV:104:PRESENT-VALUE | Read+Write | Always
MSA_BT_Bombas_UTAS_AC_2.Mando_variador | 192.168.4.31 | AO:3204:PRESENT-VALUE | Read | Always
MSA_BT_UTAS_IV_Cambio_Valvulas | 192.168.4.31 | BV:1111:PRESENT-VALUE | Read | Always
MSA_BT_UTAS_IV_Valvulas_en_Posicion | 192.168.4.31 | BV:1112:PRESENT-VALUE | Read+Write | Always
MSA_BT_UTAS_IV_Cambio_Bombas | 192.168.4.31 | BV:1110:PRESENT-VALUE | Read | Always
MSA_BT_UTAS_IV_Cambiando | 192.168.4.31 | BV:1108:PRESENT-VALUE | Read | Always
MSA_BT_UTAS_IV_Bombas_paradas | 192.168.4.31 | BV:1109:PRESENT-VALUE | Read+Write | Always
MSA_BT_Bombas_UTAS_Manual_horario_IV | 192.168.4.31 | BV:7:PRESENT-VALUE | Read+Write | Always
MSA_BT_Bombas_UTAS_Cambio_invierno_verano | 192.168.4.31 | BV:8:PRESENT-VALUE | Read+Write | Always
MSA_BT_Modo_IV | 192.168.4.31 | BV:1003:PRESENT-VALUE | Read | Always
MSA_BM_Bombas_UTAS_AF_Presion | 192.168.4.21 | AI:3301:PRESENT-VALUE | Read | Always
MSA_BM_Bombas_UTAS_AF_Consigna_presion | 192.168.4.21 | AV:101:PRESENT-VALUE | Read+Write | Always
MSA_BM_Bombas_UTAS_AF_1.Estado | 192.168.4.21 | BV:101:PRESENT-VALUE | Read+Write | Always
MSA_BM_Bombas_UTAS_AF_1.Mando_variador | 192.168.4.21 | AO:3201:PRESENT-VALUE | Read | Always
MSA_BM_Bombas_UTAS_AF_2.Estado | 192.168.4.21 | BV:102:PRESENT-VALUE | Read+Write | Always
MSA_BM_Bombas_UTAS_AF_2.Mando_variador | 192.168.4.21 | AO:3202:PRESENT-VALUE | Read | Always
MSA_BM_Bombas_UTAS_AC_Presion | 192.168.4.21 | AI:3401:PRESENT-VALUE | Read | Always
MSA_BM_Bombas_UTAS_AC_Consigna_presion | 192.168.4.21 | AV:103:PRESENT-VALUE | Read+Write | Always
MSA_BM_Bombas_UTAS_AC_1.Estado | 192.168.4.21 | BV:103:PRESENT-VALUE | Read+Write | Always
MSA_BM_Bombas_UTAS_AC_1.Mando_variador | 192.168.4.21 | AO:3203:PRESENT-VALUE | Read | Always
MSA_BM_Bombas_UTAS_AC_2.Estado | 192.168.4.21 | BV:104:PRESENT-VALUE | Read+Write | Always
MSA_BM_Bombas_UTAS_AC_2.Mando_variador | 192.168.4.21 | AO:3204:PRESENT-VALUE | Read | Always
MSA_BM_Bombas_UTAS_Manual_horario_IV | 192.168.4.21 | BV:7:PRESENT-VALUE | Read+Write | Always
MSA_BM_Bombas_UTAS_Cambio_invierno_verano | 192.168.4.21 | BV:8:PRESENT-VALUE | Read+Write | Always
MSA_BM_Modo_IV | 192.168.4.21 | BV:1003:PRESENT-VALUE | Read | Always
MSA_BM_UTAS_IV_Cambio_Valvulas | 192.168.4.21 | BV:1111:PRESENT-VALUE | Read | Always
MSA_BM_UTAS_IV_Valvulas_en_Posicion | 192.168.4.21 | BV:1112:PRESENT-VALUE | Read+Write | Always
MSA_BM_UTAS_IV_Cambio_Bombas | 192.168.4.21 | BV:1110:PRESENT-VALUE | Read | Always
MSA_BM_UTAS_IV_Cambiando | 192.168.4.21 | BV:1108:PRESENT-VALUE | Read | Always
MSA_BM_UTAS_IV_Bombas_paradas | 192.168.4.21 | BV:1109:PRESENT-VALUE | Read+Write | Always
MSA_UT_Bombas_UTAS_AF_Presion | 192.168.4.41 | AI:3301:PRESENT-VALUE | Read | Always
MSA_UT_Bombas_UTAS_AF_Consigna_presion | 192.168.4.41 | AV:101:PRESENT-VALUE | Read+Write | Always
MSA_UT_Bombas_UTAS_AF_1.Estado | 192.168.4.41 | BV:101:PRESENT-VALUE | Read+Write | Always
MSA_UT_Bombas_UTAS_AF_1.Mando_variador | 192.168.4.41 | AO:3201:PRESENT-VALUE | Read | Always
MSA_UT_Bombas_UTAS_AF_2.Estado | 192.168.4.41 | BV:102:PRESENT-VALUE | Read+Write | Always
MSA_UT_Bombas_UTAS_AF_2.Mando_variador | 192.168.4.41 | AO:3202:PRESENT-VALUE | Read | Always
MSA_UT_Bombas_UTAS_AC_Presion | 192.168.4.41 | AI:3401:PRESENT-VALUE | Read | Always
MSA_UT_Bombas_UTAS_AC_Consigna_presion | 192.168.4.41 | AV:103:PRESENT-VALUE | Read+Write | Always
MSA_UT_Bombas_UTAS_AC_1.Estado | 192.168.4.41 | BV:103:PRESENT-VALUE | Read+Write | Always
MSA_UT_Bombas_UTAS_AC_1.Mando_variador | 192.168.4.41 | AO:3203:PRESENT-VALUE | Read | Always
MSA_UT_Bombas_UTAS_AC_2.Estado | 192.168.4.41 | BV:104:PRESENT-VALUE | Read+Write | Always
MSA_UT_Bombas_UTAS_AC_2.Mando_variador | 192.168.4.41 | AO:3204:PRESENT-VALUE | Read | Always
MSA_UT_Bombas_UTAS_Manual_horario_IV | 192.168.4.41 | BV:7:PRESENT-VALUE | Read+Write | Always
MSA_UT_Bombas_UTAS_Cambio_invierno_verano | 192.168.4.41 | BV:8:PRESENT-VALUE | Read+Write | Always
MSA_UT_UTAS_IV_Cambio_Valvulas | 192.168.4.41 | BV:1111:PRESENT-VALUE | Read | Always
MSA_UT_UTAS_IV_Valvulas_en_Posicion | 192.168.4.41 | BV:1112:PRESENT-VALUE | Read+Write | Always
MSA_UT_UTAS_IV_Cambio_Bombas | 192.168.4.41 | BV:1110:PRESENT-VALUE | Read | Always
MSA_UT_UTAS_IV_Cambiando | 192.168.4.41 | BV:1108:PRESENT-VALUE | Read | Always
MSA_UT_UTAS_IV_Bombas_paradas | 192.168.4.41 | BV:1109:PRESENT-VALUE | Read+Write | Always
MSA_UT_Modo_IV | 192.168.4.41 | BV:1003:PRESENT-VALUE | Read | Always
MSA_UM_Bombas_UTAS_AF_Presion | 192.168.4.51 | AI:3301:PRESENT-VALUE | Read | Always
MSA_UM_Bombas_UTAS_AF_Consigna_presion | 192.168.4.51 | AV:101:PRESENT-VALUE | Read+Write | Always
MSA_UM_Bombas_UTAS_AF_1.Estado | 192.168.4.51 | BV:101:PRESENT-VALUE | Read+Write | Always
MSA_UM_Bombas_UTAS_AF_1.Mando_variador | 192.168.4.51 | AO:3201:PRESENT-VALUE | Read | Always
MSA_UM_Bombas_UTAS_AF_2.Estado | 192.168.4.51 | BV:102:PRESENT-VALUE | Read+Write | Always
MSA_UM_Bombas_UTAS_AF_2.Mando_variador | 192.168.4.51 | AO:3202:PRESENT-VALUE | Read | Always
MSA_UM_Bombas_UTAS_AC_Presion | 192.168.4.51 | AI:3401:PRESENT-VALUE | Read | Always
MSA_UM_Bombas_UTAS_AC_Consigna_presion | 192.168.4.51 | AV:103:PRESENT-VALUE | Read+Write | Always
MSA_UM_Bombas_UTAS_AC_1.Estado | 192.168.4.51 | BV:103:PRESENT-VALUE | Read+Write | Always
MSA_UM_Bombas_UTAS_AC_1.Mando_variador | 192.168.4.51 | AO:3203:PRESENT-VALUE | Read | Always
MSA_UM_Bombas_UTAS_AC_2.Estado | 192.168.4.51 | BV:104:PRESENT-VALUE | Read+Write | Always
MSA_UM_Bombas_UTAS_AC_2.Mando_variador | 192.168.4.51 | AO:3204:PRESENT-VALUE | Read | Always
MSA_UM_Bombas_UTAS_Manual_horario_IV | 192.168.4.51 | BV:7:PRESENT-VALUE | Read+Write | Always
MSA_UM_Bombas_UTAS_Cambio_invierno_verano | 192.168.4.51 | BV:8:PRESENT-VALUE | Read+Write | Always
MSA_UM_UTAS_IV_Cambio_Valvulas | 192.168.4.51 | BV:1111:PRESENT-VALUE | Read | Always
MSA_UM_UTAS_IV_Valvulas_en_Posicion | 192.168.4.51 | BV:1112:PRESENT-VALUE | Read+Write | Always
MSA_UM_UTAS_IV_Cambio_Bombas | 192.168.4.51 | BV:1110:PRESENT-VALUE | Read | Always
MSA_UM_UTAS_IV_Cambiando | 192.168.4.51 | BV:1108:PRESENT-VALUE | Read | Always
MSA_UM_UTAS_IV_Bombas_paradas | 192.168.4.51 | BV:1109:PRESENT-VALUE | Read+Write | Always
MSA_UM_Modo_IV | 192.168.4.51 | BV:1003:PRESENT-VALUE | Read | Always
MSA_BT_Depositos_AF_Temperatura_1 | 192.168.4.31 | AI:3101:PRESENT-VALUE | Read | Always
MSA_BT_Depositos_AF_Temperatura_2 | 192.168.4.31 | AI:3102:PRESENT-VALUE | Read | Always
MSA_BT_Depositos_AC_Temperatura_1 | 192.168.4.31 | AI:3103:PRESENT-VALUE | Read | Always
MSA_BT_Depositos_AC_Temperatura_2 | 192.168.4.31 | AI:3104:PRESENT-VALUE | Read | Always
MSA_BT_Colector_frio.Temp_salida_prim | 192.168.4.31 | AI:3105:PRESENT-VALUE | Read | Always
MSA_BT_Colector_frio.Temp_entrada_prim | 192.168.4.31 | AI:3106:PRESENT-VALUE | Read | Always
MSA_BT_Colector_frio.Temp_salida_secu | 192.168.4.31 | AI:3107:PRESENT-VALUE | Read | Always
MSA_BT_Colector_frio.Temp_entrada_secu | 192.168.4.31 | AI:3108:PRESENT-VALUE | Read | Always
MSA_BT_Colector_calor.Temp_salida_prim | 192.168.4.31 | AI:3201:PRESENT-VALUE | Read | Always
MSA_BT_Colector_calor.Temp_entrada_prim | 192.168.4.31 | AI:3202:PRESENT-VALUE | Read | Always
MSA_BT_Colector_calor.Temp_salida_secu | 192.168.4.31 | AI:3203:PRESENT-VALUE | Read | Always
MSA_BT_Colector_calor.Temp_entrada_secu | 192.168.4.31 | AI:3204:PRESENT-VALUE | Read | Always
MSA_BT_Disipadores_terreno_Temp_impuls | 192.168.4.31 | AI:3501:PRESENT-VALUE | Read | Always
MSA_BT_Disipadores_terreno_Temp_retorno | 192.168.4.31 | AI:3502:PRESENT-VALUE | Read | Always
MSA_BT_Bombas_ACS_PB_Presion | 192.168.4.31 | AI:3303:PRESENT-VALUE | Read | Always
MSA_BT_Bombas_ACS_PB_Consigna_presion | 192.168.4.31 | AV:105:PRESENT-VALUE | Read+Write | Always
MSA_BT_Bombas_ACS_PB_1.Estado | 192.168.4.31 | BV:105:PRESENT-VALUE | Read+Write | Always
MSA_BT_Bombas_ACS_PB_1.Mando_variador | 192.168.4.31 | AO:3301:PRESENT-VALUE | Read | Always
MSA_BT_Bombas_ACS_PB_2.Estado | 192.168.4.31 | BV:106:PRESENT-VALUE | Read+Write | Always
MSA_BT_Bombas_ACS_PB_2.Mando_variador | 192.168.4.31 | AO:3302:PRESENT-VALUE | Read | Always
MSA_BT_Bombas_ACS_Pinf_Presion | 192.168.4.31 | AI:3304:PRESENT-VALUE | Read | Always
MSA_BT_Bombas_ACS_Pinf_Consigna_presion | 192.168.4.31 | AV:107:PRESENT-VALUE | Read+Write | Always
MSA_BT_Bombas_ACS_P_Inf_1.Estado | 192.168.4.31 | BV:107:PRESENT-VALUE | Read+Write | Always
MSA_BT_Bombas_ACS_P_Inf_1.Mando_variador | 192.168.4.31 | AO:3401:PRESENT-VALUE | Read | Always
MSA_BT_Bombas_ACS_P_Inf_2.Estado | 192.168.4.31 | BV:108:PRESENT-VALUE | Read+Write | Always
MSA_BT_Bombas_ACS_P_Inf_2.Mando_variador | 192.168.4.31 | AO:3402:PRESENT-VALUE | Read | Always
MSA_BT_Bomba_AC_A_Geoterm_Presion | 192.168.4.31 | AI:3403:PRESENT-VALUE | Read | Always
MSA_BT_Bomba_AC_A_Geoterm_Consigna_presion | 192.168.4.31 | AV:109:PRESENT-VALUE | Read+Write | Always
MSA_BT_Bomba_AC_A_Geoterm_1.Estado | 192.168.4.31 | BV:109:PRESENT-VALUE | Read+Write | Always
MSA_BT_Bomba_AC_A_Geoterm_1.Mando_variador | 192.168.4.31 | AO:3303:PRESENT-VALUE | Read | Always
MSA_BT_Bomba_AC_A_Geoterm_2.Estado | 192.168.4.31 | BV:110:PRESENT-VALUE | Read+Write | Always
MSA_BT_Bomba_AC_A_Geoterm_2.Mando_variador | 192.168.4.31 | AO:3304:PRESENT-VALUE | Read | Always
MSA_BT_Circuito_AC_Vestuarios_Presion | 192.168.4.31 | AI:3402:PRESENT-VALUE | Read | Always
MSA_BT_Circuito_AC_Vestuarios_Consigna_presion | 192.168.4.31 | AV:111:PRESENT-VALUE | Read+Write | Always
MSA_BT_Bomba_AC_Vestuarios_1.Estado | 192.168.4.31 | BV:111:PRESENT-VALUE | Read+Write | Always
MSA_BT_Bomba_AC_Vestuarios_1.Mando_variador | 192.168.4.31 | AO:3403:PRESENT-VALUE | Read | Always
MSA_BT_Bomba_AC_Vestuarios_2.Estado | 192.168.4.31 | BV:112:PRESENT-VALUE | Read+Write | Always
MSA_BT_Bomba_AC_Vestuarios_2.Mando_variador | 192.168.4.31 | AO:3404:PRESENT-VALUE | Read | Always
MSA_BT_Bomba_AF_A_Geroterm_Presion | 192.168.4.31 | AI:3302:PRESENT-VALUE | Read | Always
MSA_BT_Bomba_AF_A_Geroterm_Consigna_presion | 192.168.4.31 | AV:113:PRESENT-VALUE | Read+Write | Always
MSA_BT_Bomba_AF_A_Geoterm_1.Estado | 192.168.4.31 | BV:113:PRESENT-VALUE | Read+Write | Always
MSA_BT_Bomba_AF_A_Geoterm_1.Mando_variador | 192.168.4.31 | AO:3601:PRESENT-VALUE | Read | Always
MSA_BT_Bomba_AF_A_Geoterm_2.Estado | 192.168.4.31 | BV:114:PRESENT-VALUE | Read+Write | Always
MSA_BT_Bomba_AF_A_Geoterm_2.Mando_variador | 192.168.4.31 | AO:3602:PRESENT-VALUE | Read | Always
MSA_BM_Depositos_Temperatura_AF_1 | 192.168.4.21 | AI:3101:PRESENT-VALUE | Read | Always
MSA_BM_Depositos_Temperatura_AF_2 | 192.168.4.21 | AI:3102:PRESENT-VALUE | Read | Always
MSA_BM_Depositos_Temperatura_AC_1 | 192.168.4.21 | AI:3103:PRESENT-VALUE | Read | Always
MSA_BM_Depositos_Temperatura_AC_2 | 192.168.4.21 | AI:3104:PRESENT-VALUE | Read | Always
MSA_BM_Colector_frio.Temp_salida_prim | 192.168.4.21 | AI:3105:PRESENT-VALUE | Read | Always
MSA_BM_Colector_frio.Temp_entrada_prim | 192.168.4.21 | AI:3106:PRESENT-VALUE | Read | Always
MSA_BM_Colector_frio.Temp_salida_secu | 192.168.4.21 | AI:3107:PRESENT-VALUE | Read | Always
MSA_BM_Colector_frio.Temp_entrada_secu | 192.168.4.21 | AI:3108:PRESENT-VALUE | Read | Always
MSA_BM_Colector_calor.Temp_salida_prim | 192.168.4.21 | AI:3201:PRESENT-VALUE | Read | Always
MSA_BM_Colector_calor.Temp_entrada_prim | 192.168.4.21 | AI:3202:PRESENT-VALUE | Read | Always
MSA_BM_Colector_calor.Temp_salida_secu | 192.168.4.21 | AI:3203:PRESENT-VALUE | Read | Always
MSA_BM_Colector_calor.Temp_entrada_secu | 192.168.4.21 | AI:3204:PRESENT-VALUE | Read | Always
MSA_BM_Bombas_ACS_PB_Presion | 192.168.4.21 | AI:3303:PRESENT-VALUE | Read | Always
MSA_BM_Bombas_ACS_PB_Consigna_presion | 192.168.4.21 | AV:105:PRESENT-VALUE | Read+Write | Always
MSA_BM_Bombas_ACS_PB_1.Estado | 192.168.4.21 | BV:105:PRESENT-VALUE | Read+Write | Always
MSA_BM_Bombas_ACS_PB_1.Mando_variador | 192.168.4.21 | AO:3301:PRESENT-VALUE | Read | Always
MSA_BM_Bombas_ACS_PB_2.Estado | 192.168.4.21 | BV:106:PRESENT-VALUE | Read+Write | Always
MSA_BM_Bombas_ACS_PB_2.Mando_variador | 192.168.4.21 | AO:3302:PRESENT-VALUE | Read | Always
MSA_BM_Bombas_ACS_Pinf_Presion | 192.168.4.21 | AI:3304:PRESENT-VALUE | Read | Always
MSA_BM_Bombas_ACS_Pinf_Consigna_presion | 192.168.4.21 | AV:107:PRESENT-VALUE | Read+Write | Always
MSA_BM_Bombas_ACS_P_Inf_1.Estado | 192.168.4.21 | BV:107:PRESENT-VALUE | Read+Write | Always
MSA_BM_Bombas_ACS_P_Inf_1.Mando_variador | 192.168.4.21 | AO:3401:PRESENT-VALUE | Read | Always
MSA_BM_Bombas_ACS_P_Inf_2.Estado | 192.168.4.21 | BV:108:PRESENT-VALUE | Read+Write | Always
MSA_BM_Bombas_ACS_P_Inf_2.Mando_variador | 192.168.4.21 | AO:3402:PRESENT-VALUE | Read | Always
MSA_BM_Bomba_AF_A_Geoterm_Presion | 192.168.4.21 | AI:3302:PRESENT-VALUE | Read | Always
MSA_BM_Bomba_AF_A_Geoterm_Consigna_presion | 192.168.4.21 | AV:109:PRESENT-VALUE | Read+Write | Always
MSA_BM_Bomba_AF_A_Geoterm_1.Estado | 192.168.4.21 | BV:109:PRESENT-VALUE | Read+Write | Always
MSA_BM_Bomba_AF_A_Geoterm_1.Mando_variador | 192.168.4.21 | AO:3403:PRESENT-VALUE | Read | Always
MSA_BM_Bomba_AF_A_Geoterm_2.Estado | 192.168.4.21 | BV:110:PRESENT-VALUE | Read+Write | Always
MSA_BM_Bomba_AF_A_Geoterm_2.Mando_variador | 192.168.4.21 | AO:3404:PRESENT-VALUE | Read | Always
MSA_BM_Bomba_AC_A_Geoterm_Presion | 192.168.4.21 | AI:3402:PRESENT-VALUE | Read | Always
MSA_BM_Bomba_AC_A_Geoterm_Consigna_presion | 192.168.4.21 | AV:111:PRESENT-VALUE | Read+Write | Always
MSA_BM_Bomba_AC_A_Geoterm_1.Estado | 192.168.4.21 | BV:111:PRESENT-VALUE | Read+Write | Always
MSA_BM_Bomba_AC_A_Geoterm_1.Mando_variador | 192.168.4.21 | AO:3303:PRESENT-VALUE | Read | Always
MSA_BM_Bomba_AC_A_Geoterm_2.Estado | 192.168.4.21 | BV:112:PRESENT-VALUE | Read+Write | Always
MSA_BM_Bomba_AC_A_Geoterm_2.Mando_variador | 192.168.4.21 | AO:3304:PRESENT-VALUE | Read | Always
MSA_BM_Disipadores_terreno_Temp_impuls | 192.168.4.21 | AI:3403:PRESENT-VALUE | Read | Always
MSA_BM_Disipadores_terreno_Temp_retorno | 192.168.4.21 | AI:3404:PRESENT-VALUE | Read | Always
MSA_UT_Depositos_AF_Temperatura_1 | 192.168.4.41 | AI:3101:PRESENT-VALUE | Read | Always
MSA_UT_Depositos_AF_Temperatura_2 | 192.168.4.41 | AI:3102:PRESENT-VALUE | Read | Always
MSA_UT_Depositos_AC_Temperatura_1 | 192.168.4.41 | AI:3103:PRESENT-VALUE | Read | Always
MSA_UT_Depositos_AC_Temperatura_2 | 192.168.4.41 | AI:3104:PRESENT-VALUE | Read | Always
MSA_UT_Colector_frio.Temp_salida_prim | 192.168.4.41 | AI:3105:PRESENT-VALUE | Read | Always
MSA_UT_Colector_frio.Temp_entrada_prim | 192.168.4.41 | AI:3106:PRESENT-VALUE | Read | Always
MSA_UT_Colector_frio.Temp_salida_secu | 192.168.4.41 | AI:3107:PRESENT-VALUE | Read | Always
MSA_UT_Colector_frio.Temp_entrada_secu | 192.168.4.41 | AI:3108:PRESENT-VALUE | Read | Always
MSA_UT_Colector_calor.Temp_salida_prim | 192.168.4.41 | AI:3201:PRESENT-VALUE | Read | Always
MSA_UT_Colector_calor.Temp_entrada_prim | 192.168.4.41 | AI:3202:PRESENT-VALUE | Read | Always
MSA_UT_Colector_calor.Temp_salida_secu | 192.168.4.41 | AI:3203:PRESENT-VALUE | Read | Always
MSA_UT_Colector_calor.Temp_entrada_secu | 192.168.4.41 | AI:3204:PRESENT-VALUE | Read | Always
MSA_UT_Disipadores_terreno_Temp_impuls | 192.168.4.41 | AI:3403:PRESENT-VALUE | Read | Always
MSA_UT_Disipadores_terreno_Temp_retorno | 192.168.4.41 | AI:3404:PRESENT-VALUE | Read | Always
MSA_UT_Bombas_ACS_PB_Presion | 192.168.4.41 | AI:3303:PRESENT-VALUE | Read | Always
MSA_UT_Bombas_ACS_PB_Consigna_presion | 192.168.4.41 | AV:105:PRESENT-VALUE | Read+Write | Always
MSA_UT_Bombas_ACS_PB_1.Estado | 192.168.4.41 | BV:105:PRESENT-VALUE | Read+Write | Always
MSA_UT_Bombas_ACS_PB_1.Mando_variador | 192.168.4.41 | AO:3301:PRESENT-VALUE | Read | Always
MSA_UT_Bombas_ACS_PB_2.Estado | 192.168.4.41 | BV:106:PRESENT-VALUE | Read+Write | Always
MSA_UT_Bombas_ACS_PB_2.Mando_variador | 192.168.4.41 | AO:3302:PRESENT-VALUE | Read | Always
MSA_UT_Bombas_ACS_Pinf_Presion | 192.168.4.41 | AI:3304:PRESENT-VALUE | Read | Always
MSA_UT_Bombas_ACS_Pinf_Consigna_presion | 192.168.4.41 | AV:106:PRESENT-VALUE | Read+Write | Always
MSA_UT_Bombas_ACS_P_Inf_1.Estado | 192.168.4.41 | BV:107:PRESENT-VALUE | Read+Write | Always
MSA_UT_Bombas_ACS_P_Inf_1.Mando_variador | 192.168.4.41 | AO:3401:PRESENT-VALUE | Read | Always
MSA_UT_Bombas_ACS_P_Inf_2.Estado | 192.168.4.41 | BV:108:PRESENT-VALUE | Read+Write | Always
MSA_UT_Bombas_ACS_P_Inf_2.Mando_variador | 192.168.4.41 | AO:3402:PRESENT-VALUE | Read | Always
MSA_UT_Bomba_AF_A_Geoterm_Presion | 192.168.4.41 | AI:3302:PRESENT-VALUE | Read | Always
MSA_UT_Bomba_AF_A_Geoterm_Consigna_presion | 192.168.4.41 | AV:109:PRESENT-VALUE | Read+Write | Always
MSA_UT_Bomba_AF_A_Geoterm_1.Estado | 192.168.4.41 | BV:109:PRESENT-VALUE | Read+Write | Always
MSA_UT_Bomba_AF_A_Geoterm_1.Mando_variador | 192.168.4.41 | AO:3403:PRESENT-VALUE | Read | Always
MSA_UT_Bomba_AF_A_Geoterm_2.Estado | 192.168.4.41 | BV:110:PRESENT-VALUE | Read+Write | Always
MSA_UT_Bomba_AF_A_Geoterm_2.Mando_variador | 192.168.4.41 | AO:3404:PRESENT-VALUE | Read | Always
MSA_UT_Bomba_AC_A_Geoterm_Presion | 192.168.4.41 | AI:3402:PRESENT-VALUE | Read | Always
MSA_UT_Bomba_AC_A_Geoterm_Consigna_presion | 192.168.4.41 | AV:111:PRESENT-VALUE | Read+Write | Always
MSA_UT_Bomba_AC_A_Geoterm_1.Estado | 192.168.4.41 | BV:111:PRESENT-VALUE | Read+Write | Always
MSA_UT_Bomba_AC_A_Geoterm_1.Mando_variador | 192.168.4.41 | AO:3303:PRESENT-VALUE | Read | Always
MSA_UT_Bomba_AC_A_Geoterm_2.Estado | 192.168.4.41 | BV:112:PRESENT-VALUE | Read+Write | Always
MSA_UT_Bomba_AC_A_Geoterm_2.Mando_variador | 192.168.4.41 | AO:3304:PRESENT-VALUE | Read | Always
MSA_UM_Depositos_AF_Temperatura_1 | 192.168.4.51 | AI:3101:PRESENT-VALUE | Read | Always
MSA_UM_Depositos_AF_Temperatura_2 | 192.168.4.51 | AI:3102:PRESENT-VALUE | Read | Always
MSA_UM_Depositos_AC_Temperatura_1 | 192.168.4.51 | AI:3103:PRESENT-VALUE | Read | Always
MSA_UM_Depositos_AC_Temperatura_2 | 192.168.4.51 | AI:3104:PRESENT-VALUE | Read | Always
MSA_UM_Colector_frio.Temp_salida_prim | 192.168.4.51 | AI:3105:PRESENT-VALUE | Read | Always
MSA_UM_Colector_frio.Temp_entrada_prim | 192.168.4.51 | AI:3106:PRESENT-VALUE | Read | Always
MSA_UM_Colector_frio.Temp_salida_secu | 192.168.4.51 | AI:3107:PRESENT-VALUE | Read | Always
MSA_UM_Colector_frio.Temp_entrada_secu | 192.168.4.51 | AI:3108:PRESENT-VALUE | Read | Always
MSA_UM_Colector_calor.Temp_salida_prim | 192.168.4.51 | AI:3201:PRESENT-VALUE | Read | Always
MSA_UM_Colector_calor.Temp_entrada_prim | 192.168.4.51 | AI:3202:PRESENT-VALUE | Read | Always
MSA_UM_Colector_calor.Temp_salida_secu | 192.168.4.51 | AI:3203:PRESENT-VALUE | Read | Always
MSA_UM_Colector_calor.Temp_entrada_secu | 192.168.4.51 | AI:3204:PRESENT-VALUE | Read | Always
MSA_UM_Disipadores_terreno_Temp_impuls | 192.168.4.51 | AI:3403:PRESENT-VALUE | Read | Always
MSA_UM_Disipadores_terreno_Temp_retorno | 192.168.4.51 | AI:3404:PRESENT-VALUE | Read | Always
MSA_UM_Bombas_ACS_PB_Presion | 192.168.4.51 | AI:3303:PRESENT-VALUE | Read | Always
MSA_UM_Bombas_ACS_PB_Consigna_presion | 192.168.4.51 | AV:105:PRESENT-VALUE | Read+Write | Always
MSA_UM_Bombas_ACS_PB_1.Estado | 192.168.4.51 | BV:105:PRESENT-VALUE | Read+Write | Always
MSA_UM_Bombas_ACS_PB_1.Mando_variador | 192.168.4.51 | AO:3301:PRESENT-VALUE | Read | Always
MSA_UM_Bombas_ACS_PB_2.Estado | 192.168.4.51 | BV:106:PRESENT-VALUE | Read+Write | Always
MSA_UM_Bombas_ACS_PB_2.Mando_variador | 192.168.4.51 | AO:3302:PRESENT-VALUE | Read | Always
MSA_UM_Bomba_AC_A_Geoterm_Presion | 192.168.4.51 | AI:3402:PRESENT-VALUE | Read | Always
MSA_UM_Bomba_AC_A_Geoterm_Consigna_presion | 192.168.4.51 | AV:107:PRESENT-VALUE | Read+Write | Always
MSA_UM_Bomba_AC_A_Geoterm_1.Estado | 192.168.4.51 | BV:107:PRESENT-VALUE | Read+Write | Always
MSA_UM_Bomba_AC_A_Geoterm_1.Mando_variador | 192.168.4.51 | AO:3303:PRESENT-VALUE | Read | Always
MSA_UM_Bomba_AC_A_Geoterm_2.Estado | 192.168.4.51 | BV:108:PRESENT-VALUE | Read+Write | Always
MSA_UM_Bomba_AC_A_Geoterm_2.Mando_variador | 192.168.4.51 | AO:3304:PRESENT-VALUE | Read | Always
MSA_UM_Bombas_ACS_Pinf_Presion | 192.168.4.51 | AI:3304:PRESENT-VALUE | Read | Always
MSA_UM_Bombas_ACS_Pinf_Consigna_presion | 192.168.4.51 | AV:109:PRESENT-VALUE | Read+Write | Always
MSA_UM_Bombas_ACS_P_Inf_1.Estado | 192.168.4.51 | BV:109:PRESENT-VALUE | Read+Write | Always
MSA_UM_Bombas_ACS_P_Inf_1.Mando_variador | 192.168.4.51 | AO:3401:PRESENT-VALUE | Read | Always
MSA_UM_Bombas_ACS_P_Inf_2.Estado | 192.168.4.51 | BV:110:PRESENT-VALUE | Read+Write | Always
MSA_UM_Bombas_ACS_P_Inf_2.Mando_variador | 192.168.4.51 | AO:3402:PRESENT-VALUE | Read | Always
MSA_UM_Bomba_AF_A_Geoterm_Presion | 192.168.4.51 | AI:3302:PRESENT-VALUE | Read | Always
MSA_UM_Bomba_AF_A_Geoterm_Consigna_presion | 192.168.4.51 | AV:111:PRESENT-VALUE | Read+Write | Always
MSA_UM_Bomba_AF_A_Geoterm_1.Estado | 192.168.4.51 | BV:111:PRESENT-VALUE | Read+Write | Always
MSA_UM_Bomba_AF_A_Geoterm_1.Mando_variador | 192.168.4.51 | AO:3403:PRESENT-VALUE | Read | Always
MSA_UM_Bomba_AF_A_Geoterm_2.Estado | 192.168.4.51 | BV:112:PRESENT-VALUE | Read+Write | Always
MSA_UM_Bomba_AF_A_Geoterm_2.Mando_variador | 192.168.4.51 | AO:3404:PRESENT-VALUE | Read | Always
MSA_BM_Extractor_cocina_1.Horario_estado | 192.168.4.21 | SCH:90:PRESENT-VALUE | Read | Always
MSA_BM_Extractor_cocina_1.Horario_B | 192.168.4.21 | SCH:90:WEEKLY-SCHEDULE | Read+Write | Always
MSA_BM_Extractor_cocina_1.Manual_horario | 192.168.4.21 | BV:91:PRESENT-VALUE | Read+Write | Always
MSA_BM_Extractor_cocina_1.Marcha_paro | 192.168.4.21 | BV:92:PRESENT-VALUE | Read+Write | Always
MSA_BM_Extractor_cocina_1.Orden_marcha | 192.168.4.21 | BV:93:PRESENT-VALUE | Read | Always
MSA_BM_Extractor_cocina_1.Potenciometro_demanda | 192.168.4.21 | AI:2301:PRESENT-VALUE | Read | Always
MSA_BM_Extractor_cocina_1.Estado | 192.168.4.21 | BV:94:PRESENT-VALUE | Read+Write | Always
MSA_BM_Extractor_cocina_1.Mando_EC | 192.168.4.21 | AO:2101:PRESENT-VALUE | Read | Always
MSA_BM_Extractor_cocina_2.Horario_estado | 192.168.4.21 | SCH:120:PRESENT-VALUE | Read | Always
MSA_BM_Extractor_cocina_2.Horario_B | 192.168.4.21 | SCH:120:WEEKLY-SCHEDULE | Read+Write | Always
MSA_BM_Extractor_cocina_2.Manual_horario | 192.168.4.21 | BV:121:PRESENT-VALUE | Read+Write | Always
MSA_BM_Extractor_cocina_2.Marcha_paro | 192.168.4.21 | BV:122:PRESENT-VALUE | Read+Write | Always
MSA_BM_Extractor_cocina_2.Orden_marcha | 192.168.4.21 | BV:123:PRESENT-VALUE | Read | Always
MSA_BM_Extractor_cocina_2.Potenciometro_demanda | 192.168.4.21 | AI:2302:PRESENT-VALUE | Read | Always
MSA_BM_Extractor_cocina_2.Estado | 192.168.4.21 | BV:124:PRESENT-VALUE | Read+Write | Always
MSA_BM_Extractor_cocina_2.Mando_EC | 192.168.4.21 | AO:2102:PRESENT-VALUE | Read | Always
MSA_BT_Extractor_cocina_1.Horario_estado | 192.168.4.31 | SCH:120:PRESENT-VALUE | Read | Always
MSA_BT_Extractor_cocina_1.Horario_B | 192.168.4.31 | SCH:120:WEEKLY-SCHEDULE | Read+Write | Always
MSA_BT_Extractor_cocina_1.Manual_horario | 192.168.4.31 | BV:121:PRESENT-VALUE | Read+Write | Always
MSA_BT_Extractor_cocina_1.Marcha_paro | 192.168.4.31 | BV:122:PRESENT-VALUE | Read+Write | Always
MSA_BT_Extractor_cocina_1.Orden_marcha | 192.168.4.31 | BV:123:PRESENT-VALUE | Read | Always
MSA_BT_Extractor_cocina_1.Potenciometro_demanda | 192.168.4.31 | AI:2401:PRESENT-VALUE | Read | Always
MSA_BT_Extractor_cocina_1.Estado | 192.168.4.31 | BV:124:PRESENT-VALUE | Read+Write | Always
MSA_BT_Extractor_cocina_1.Mando_EC | 192.168.4.31 | AO:2101:PRESENT-VALUE | Read | Always
MSA_BT_Extractor_cocina_2.Horario_estado | 192.168.4.31 | SCH:130:PRESENT-VALUE | Read | Always
MSA_BT_Extractor_cocina_2.Horario_B | 192.168.4.31 | SCH:130:WEEKLY-SCHEDULE | Read+Write | Always
MSA_BT_Extractor_cocina_2.Manual_horario | 192.168.4.31 | BV:131:PRESENT-VALUE | Read+Write | Always
MSA_BT_Extractor_cocina_2.Marcha_paro | 192.168.4.31 | BV:132:PRESENT-VALUE | Read+Write | Always
MSA_BT_Extractor_cocina_2.Orden_marcha | 192.168.4.31 | BV:133:PRESENT-VALUE | Read | Always
MSA_BT_Extractor_cocina_2.Potenciometro_demanda | 192.168.4.31 | AI:2402:PRESENT-VALUE | Read | Always
MSA_BT_Extractor_cocina_2.Estado | 192.168.4.31 | BV:134:PRESENT-VALUE | Read+Write | Always
MSA_BT_Extractor_cocina_2.Mando_EC | 192.168.4.31 | AO:2102:PRESENT-VALUE | Read | Always
MSA_UT_Extractor_cocina_1.Horario_estado | 192.168.4.41 | SCH:120:PRESENT-VALUE | Read | Always
MSA_UT_Extractor_cocina_1.Horario_B | 192.168.4.41 | SCH:120:WEEKLY-SCHEDULE | Read+Write | Always
MSA_UT_Extractor_cocina_1.Manual_horario | 192.168.4.41 | BV:121:PRESENT-VALUE | Read+Write | Always
MSA_UT_Extractor_cocina_1.Marcha_paro | 192.168.4.41 | BV:122:PRESENT-VALUE | Read+Write | Always
MSA_UT_Extractor_cocina_1.Orden_marcha | 192.168.4.41 | BV:123:PRESENT-VALUE | Read | Always
MSA_UT_Extractor_cocina_1.Potenciometro_demanda | 192.168.4.41 | AI:2301:PRESENT-VALUE | Read | Always
MSA_UT_Extractor_cocina_1.Estado | 192.168.4.41 | BV:124:PRESENT-VALUE | Read+Write | Always
MSA_UT_Extractor_cocina_1.Mando_EC | 192.168.4.41 | AO:2101:PRESENT-VALUE | Read | Always
MSA_UT_Extractor_cocina_2.Horario_estado | 192.168.4.41 | SCH:130:PRESENT-VALUE | Read | Always
MSA_UT_Extractor_cocina_2.Horario_B | 192.168.4.41 | SCH:130:WEEKLY-SCHEDULE | Read+Write | Always
MSA_UT_Extractor_cocina_2.Manual_horario | 192.168.4.41 | BV:131:PRESENT-VALUE | Read+Write | Always
MSA_UT_Extractor_cocina_2.Marcha_paro | 192.168.4.41 | BV:132:PRESENT-VALUE | Read+Write | Always
MSA_UT_Extractor_cocina_2.Orden_marcha | 192.168.4.41 | BV:133:PRESENT-VALUE | Read | Always
MSA_UT_Extractor_cocina_2.Potenciometro_demanda | 192.168.4.41 | AI:2302:PRESENT-VALUE | Read | Always
MSA_UT_Extractor_cocina_2.Estado | 192.168.4.41 | BV:134:PRESENT-VALUE | Read+Write | Always
MSA_UT_Extractor_cocina_2.Mando_EC | 192.168.4.41 | AO:2102:PRESENT-VALUE | Read | Always
MSA_BT_AG_Local_Com_02.Horario_estado | 192.168.4.31 | SCH:170:PRESENT-VALUE | Read | Always
MSA_BT_AG_Local_Com_02.Horario_B | 192.168.4.31 | SCH:170:WEEKLY-SCHEDULE | Read+Write | Always
MSA_BT_AG_Local_Com_02.Manual_horario | 192.168.4.31 | BV:171:PRESENT-VALUE | Read+Write | Always
MSA_BT_AG_Local_Com_02.Marcha_paro | 192.168.4.31 | BV:172:PRESENT-VALUE | Read+Write | Always
MSA_BT_AG_Local_Com_02_En_Marcha | 192.168.4.31 | BV:173:PRESENT-VALUE | Read | Always
MSA_BT_AG_Local_Com_02_AC.Autorizar | 192.168.4.31 | BV:174:PRESENT-VALUE | Read+Write | Always
MSA_BT_AG_Local_Com_02_AC.Presion_dif_primario | 192.168.4.31 | AI:4301:PRESENT-VALUE | Read | Always
MSA_BT_AG_Local_Com_02_AC.Temp_imp_secu | 192.168.4.31 | AI:4106:PRESENT-VALUE | Read | Always
MSA_BT_AG_Local_Com_02_AC.Temp_ret_secu | 192.168.4.31 | AI:4107:PRESENT-VALUE | Read | Always
MSA_BT_AG_Local_Com_02_AC.Consigna_temp_imp | 192.168.4.31 | AV:171:PRESENT-VALUE | Read+Write | Always
MSA_BT_AG_Local_Com_02_AC.Mando_valvula | 192.168.4.31 | AO:4301:PRESENT-VALUE | Read | Always
MSA_BT_AG_Local_Com_02_AF.Autorizar | 192.168.4.31 | BV:175:PRESENT-VALUE | Read+Write | Always
MSA_BT_AG_Local_Com_02_AF.Presion_dif_primario | 192.168.4.31 | AI:4302:PRESENT-VALUE | Read | Always
MSA_BT_AG_Local_Com_02_AF.Temp_imp_secu | 192.168.4.31 | AI:4108:PRESENT-VALUE | Read | Always
MSA_BT_AG_Local_Com_02_AF.Temp_ret_secu | 192.168.4.31 | AI:4201:PRESENT-VALUE | Read | Always
MSA_BT_AG_Local_Com_02_AF.Consigna_temp_imp | 192.168.4.31 | AV:172:PRESENT-VALUE | Read+Write | Always
MSA_BT_AG_Local_Com_02_AF.Mando_valvula | 192.168.4.31 | AO:4302:PRESENT-VALUE | Read | Always
MSA_BM_AG_Romanos.Horario_estado | 192.168.4.21 | SCH:180:PRESENT-VALUE | Read | Always
MSA_BM_AG_Romanos.Horario_B | 192.168.4.21 | SCH:180:WEEKLY-SCHEDULE | Read+Write | Always
MSA_BM_AG_Romanos.Manual_horario | 192.168.4.21 | BV:181:PRESENT-VALUE | Read+Write | Always
MSA_BM_AG_Romanos.Marcha_paro | 192.168.4.21 | BV:182:PRESENT-VALUE | Read+Write | Always
MSA_BM_AG_Romanos_En_Marcha | 192.168.4.21 | BV:183:PRESENT-VALUE | Read | Always
MSA_BM_AG_Romanos_AC.Autorizar | 192.168.4.21 | BV:184:PRESENT-VALUE | Read+Write | Always
MSA_BM_AG_Romanos_AC.Presion_dif_primario | 192.168.4.21 | AI:4403:PRESENT-VALUE | Read | Always
MSA_BM_AG_Romanos_AC.Temp_imp_secu | 192.168.4.21 | AI:4207:PRESENT-VALUE | Read | Always
MSA_BM_AG_Romanos_AC.Temp_ret_secu | 192.168.4.21 | AI:4208:PRESENT-VALUE | Read | Always
MSA_BM_AG_Romanos_AC.Consigna_temp_imp | 192.168.4.21 | AV:181:PRESENT-VALUE | Read+Write | Always
MSA_BM_AG_Romanos_AC.Mando_valvula | 192.168.4.21 | AO:4403:PRESENT-VALUE | Read | Always
MSA_BM_AG_Romanos_AF.Autorizar | 192.168.4.21 | BV:185:PRESENT-VALUE | Read+Write | Always
MSA_BM_AG_Romanos_AF.Presion_dif_primario | 192.168.4.21 | AI:4404:PRESENT-VALUE | Read | Always
MSA_BM_AG_Romanos_AF.Temp_imp_secu | 192.168.4.21 | AI:4301:PRESENT-VALUE | Read | Always
MSA_BM_AG_Romanos_AF.Temp_ret_secu | 192.168.4.21 | AI:4302:PRESENT-VALUE | Read | Always
MSA_BM_AG_Romanos_AF.Consigna_temp_imp | 192.168.4.21 | AV:182:PRESENT-VALUE | Read+Write | Always
MSA_BM_AG_Romanos_AF.Mando_valvula | 192.168.4.21 | AO:4404:PRESENT-VALUE | Read | Always
MSA_BM_AG_Ent_Vecinal.Horario_estado | 192.168.4.21 | SCH:170:PRESENT-VALUE | Read | Always
MSA_BM_AG_Ent_Vecinal.Horario_B | 192.168.4.21 | SCH:170:WEEKLY-SCHEDULE | Read+Write | Always
MSA_BM_AG_Ent_Vecinal.Manual_horario | 192.168.4.21 | BV:171:PRESENT-VALUE | Read+Write | Always
MSA_BM_AG_Ent_Vecinal.Marcha_paro | 192.168.4.21 | BV:172:PRESENT-VALUE | Read+Write | Always
MSA_BM_AG_Ent_Vecinal_En_Marcha | 192.168.4.21 | BV:173:PRESENT-VALUE | Read | Always
MSA_BM_AG_Ent_Vecinal_AC.Autorizar | 192.168.4.21 | BV:174:PRESENT-VALUE | Read+Write | Always
MSA_BM_AG_Ent_Vecinal_AC.Presion_dif_primario | 192.168.4.21 | AI:4401:PRESENT-VALUE | Read | Always
MSA_BM_AG_Ent_Vecinal_AC.Temp_imp_secu | 192.168.4.21 | AI:4106:PRESENT-VALUE | Read | Always
MSA_BM_AG_Ent_Vecinal_AC.Temp_ret_secu | 192.168.4.21 | AI:4107:PRESENT-VALUE | Read | Always
MSA_BM_AG_Ent_Vecinal_AC.Consigna_temp_imp | 192.168.4.21 | AV:171:PRESENT-VALUE | Read+Write | Always
MSA_BM_AG_Ent_Vecinal_AC.Mando_valvula | 192.168.4.21 | AO:4401:PRESENT-VALUE | Read | Always
MSA_BM_AG_Ent_Vecinal_AF.Autorizar | 192.168.4.21 | BV:175:PRESENT-VALUE | Read+Write | Always
MSA_BM_AG_Ent_Vecinal_AF.Presion_dif_primario | 192.168.4.21 | AI:4402:PRESENT-VALUE | Read | Always
MSA_BM_AG_Ent_Vecinal_AF.Temp_imp_secu | 192.168.4.21 | AI:4108:PRESENT-VALUE | Read | Always
MSA_BM_AG_Ent_Vecinal_AF.Temp_ret_secu | 192.168.4.21 | AI:4201:PRESENT-VALUE | Read | Always
MSA_BM_AG_Ent_Vecinal_AF.Consigna_temp_imp | 192.168.4.21 | AV:172:PRESENT-VALUE | Read+Write | Always
MSA_BM_AG_Ent_Vecinal_AF.Mando_valvula | 192.168.4.21 | AO:4402:PRESENT-VALUE | Read | Always
MSA_UT_AG_Ent_Vecinal.Horario_estado | 192.168.4.41 | SCH:170:PRESENT-VALUE | Read | Always
MSA_UT_AG_Ent_Vecinal.Horario_B | 192.168.4.41 | SCH:170:WEEKLY-SCHEDULE | Read+Write | Always
MSA_UT_AG_Ent_Vecinal.Manual_horario | 192.168.4.41 | BV:171:PRESENT-VALUE | Read+Write | Always
MSA_UT_AG_Ent_Vecinal.Marcha_paro | 192.168.4.41 | BV:172:PRESENT-VALUE | Read+Write | Always
MSA_UT_AG_Ent_Vecinal_En_Marcha | 192.168.4.41 | BV:173:PRESENT-VALUE | Read | Always
MSA_UT_AG_Ent_Vecinal_AC.Autorizar | 192.168.4.41 | BV:174:PRESENT-VALUE | Read+Write | Always
MSA_UT_AG_Ent_Vecinal_AC.Presion_dif_primario | 192.168.4.41 | AI:4201:PRESENT-VALUE | Read | Always
MSA_UT_AG_Ent_Vecinal_AC.Temp_imp_secu | 192.168.4.41 | AI:4106:PRESENT-VALUE | Read | Always
MSA_UT_AG_Ent_Vecinal_AC.Temp_ret_secu | 192.168.4.41 | AI:4107:PRESENT-VALUE | Read | Always
MSA_UT_AG_Ent_Vecinal_AC.Consigna_temp_imp | 192.168.4.41 | AV:171:PRESENT-VALUE | Read+Write | Always
MSA_UT_AG_Ent_Vecinal_AC.Mando_valvula | 192.168.4.41 | AO:4201:PRESENT-VALUE | Read | Always
MSA_UT_AG_Ent_Vecinal_AF.Autorizar | 192.168.4.41 | BV:175:PRESENT-VALUE | Read+Write | Always
MSA_UT_AG_Ent_Vecinal_AF.Presion_dif_primario | 192.168.4.41 | AI:4202:PRESENT-VALUE | Read | Always
MSA_UT_AG_Ent_Vecinal_AF.Temp_imp_secu | 192.168.4.41 | AI:4108:PRESENT-VALUE | Read | Always
MSA_UT_AG_Ent_Vecinal_AF.Temp_ret_secu | 192.168.4.41 | AI:4204:PRESENT-VALUE | Read | Always
MSA_UT_AG_Ent_Vecinal_AF.Consigna_temp_imp | 192.168.4.41 | AV:172:PRESENT-VALUE | Read+Write | Always
MSA_UT_AG_Ent_Vecinal_AF.Mando_valvula | 192.168.4.41 | AO:4202:PRESENT-VALUE | Read | Always
MSA_BM_ACS_Sot_2_Producc.Horario_estado | 192.168.4.21 | SCH:130:PRESENT-VALUE | Read | Always
MSA_BM_ACS_Sot_2_Producc.Horario_B | 192.168.4.21 | SCH:130:WEEKLY-SCHEDULE | Read+Write | Always
MSA_BM_ACS_Sot_2_Producc.Manual_horario | 192.168.4.21 | BV:131:PRESENT-VALUE | Read+Write | Always
MSA_BM_ACS_Sot_2_Producc.Marcha_paro | 192.168.4.21 | BV:132:PRESENT-VALUE | Read+Write | Always
MSA_BM_ACS_Sot_2_Producc.Reset_horas | 192.168.4.21 | BV:133:PRESENT-VALUE | Read | Always
MSA_BM_ACS_Sot_2_Producc_Temp_salida_IC | 192.168.4.21 | AI:4105:PRESENT-VALUE | Read | Always
MSA_BM_ACS_Sot_2_Producc_Temp_entrada_IC | 192.168.4.21 | AI:4104:PRESENT-VALUE | Read | Always
MSA_BM_ACS_Sot_2_Producc_Temp_acumulador | 192.168.4.21 | AI:4102:PRESENT-VALUE | Read | Always
MSA_BM_ACS_Sot_2_Producc_Consigna_deposito | 192.168.4.21 | AV:131:PRESENT-VALUE | Read+Write | Always
MSA_BM_ACS_Sot_2_Producc_Mando_valvula | 192.168.4.21 | BO:4504:PRESENT-VALUE | Read | Always
MSA_BM_ACS_Sot_2_Recirc.Horario_estado | 192.168.4.21 | SCH:140:PRESENT-VALUE | Read | Always
MSA_BM_ACS_Sot_2_Recirc.Horario_B | 192.168.4.21 | SCH:140:WEEKLY-SCHEDULE | Read+Write | Always
MSA_BM_ACS_Sot_2_Recirc.Manual_horario | 192.168.4.21 | BV:141:PRESENT-VALUE | Read+Write | Always
MSA_BM_ACS_Sot_2_Recirc.Marcha_paro | 192.168.4.21 | BV:142:PRESENT-VALUE | Read+Write | Always
MSA_BM_ACS_Sot_2_Recirc.Reset_horas | 192.168.4.21 | BV:143:PRESENT-VALUE | Read | Always
MSA_BM_ACS_Sot_2_Recirc_Temp_retorno | 192.168.4.21 | AI:4101:PRESENT-VALUE | Read | Always
MSA_BM_ACS_Sot_2_Recirc_Temp_recirculacion | 192.168.4.21 | AI:4103:PRESENT-VALUE | Read | Always
MSA_BM_ACS_Sot_2_Bomba_recirc_Estado | 192.168.4.21 | BI:4502:PRESENT-VALUE | Read | Always
MSA_BM_ACS_Sot_2_Bomba_recirc_Orden | 192.168.4.21 | BO:4502:PRESENT-VALUE | Read | Always
MSA_BM_ACS_Sot_2_Bomba_recirc_Fallo | 192.168.4.21 | BV:144:PRESENT-VALUE | Read | Always
MSA_BM_ACS_Sot_2_Bomba_recirc_Horas_funcionamiento | 192.168.4.21 | AV:144:PRESENT-VALUE | Read | Always
MSA_BM_ACS_Sot_2_Producc_Consigna_Antilegionela | 192.168.4.21 | AV:1105:PRESENT-VALUE | Read+Write | Always
MSA_BM_ACS_Sot_2_Producc_Activar_Antilegionela | 192.168.4.21 | BV:1103:PRESENT-VALUE | Read+Write | Always
MSA_BM_ACS_Sot_3_Producc.Horario_estado | 192.168.4.21 | SCH:150:PRESENT-VALUE | Read | Always
MSA_BM_ACS_Sot_3_Producc.Horario_B | 192.168.4.21 | SCH:150:WEEKLY-SCHEDULE | Read+Write | Always
MSA_BM_ACS_Sot_3_Producc.Manual_horario | 192.168.4.21 | BV:151:PRESENT-VALUE | Read+Write | Always
MSA_BM_ACS_Sot_3_Producc.Marcha_paro | 192.168.4.21 | BV:152:PRESENT-VALUE | Read+Write | Always
MSA_BM_ACS_Sot_3_Producc.Reset_horas | 192.168.4.21 | BV:153:PRESENT-VALUE | Read | Always
MSA_BM_ACS_Sot_3_Producc_Temp_salida_IC | 192.168.4.21 | AI:4205:PRESENT-VALUE | Read | Always
MSA_BM_ACS_Sot_3_Producc_Temp_entrada_IC | 192.168.4.21 | AI:4206:PRESENT-VALUE | Read | Always
MSA_BM_ACS_Sot_3_Producc_Temp_acumulador | 192.168.4.21 | AI:4203:PRESENT-VALUE | Read | Always
MSA_BM_ACS_Sot_3_Producc_Consigna_deposito | 192.168.4.21 | AV:151:PRESENT-VALUE | Read+Write | Always
MSA_BM_ACS_Sot_3_Producc_Mando_valvula | 192.168.4.21 | BO:4604:PRESENT-VALUE | Read | Always
MSA_BM_ACS_Sot_3_Recirc.Horario_estado | 192.168.4.21 | SCH:160:PRESENT-VALUE | Read | Always
MSA_BM_ACS_Sot_3_Recirc.Horario_B | 192.168.4.21 | SCH:160:WEEKLY-SCHEDULE | Read+Write | Always
MSA_BM_ACS_Sot_3_Recirc.Manual_horario | 192.168.4.21 | BV:161:PRESENT-VALUE | Read+Write | Always
MSA_BM_ACS_Sot_3_Recirc.Marcha_paro | 192.168.4.21 | BV:162:PRESENT-VALUE | Read+Write | Always
MSA_BM_ACS_Sot_3_Recirc.Reset_horas | 192.168.4.21 | BV:163:PRESENT-VALUE | Read | Always
MSA_BM_ACS_Sot_3_Recirc_Temp_retorno | 192.168.4.21 | AI:4202:PRESENT-VALUE | Read | Always
MSA_BM_ACS_Sot_3_Recirc_Temp_recirculacion | 192.168.4.21 | AI:4204:PRESENT-VALUE | Read | Always
MSA_BM_ACS_Sot_3_Bomba_recirc_Estado | 192.168.4.21 | BI:4602:PRESENT-VALUE | Read | Always
MSA_BM_ACS_Sot_3_Bomba_recirc_Orden | 192.168.4.21 | BO:4602:PRESENT-VALUE | Read | Always
MSA_BM_ACS_Sot_3_Bomba_recirc_Fallo | 192.168.4.21 | BV:164:PRESENT-VALUE | Read | Always
MSA_BM_ACS_Sot_3_Bomba_recirc_Horas_funcionamiento | 192.168.4.21 | AV:164:PRESENT-VALUE | Read | Always
MSA_BM_ACS_Sot_3_Producc_Consigna_Antilegionela | 192.168.4.21 | AV:2007:PRESENT-VALUE | Read+Write | Always
MSA_BM_ACS_Sot_3_Producc_Activar_Antilegionela | 192.168.4.21 | BV:1113:PRESENT-VALUE | Read+Write | Always
MSA_BT_ACS_Sot_3_Borrrell_Producc.Horario_estado | 192.168.4.31 | SCH:150:PRESENT-VALUE | Read | Always
MSA_BT_ACS_Sot_3_Borrrell_Producc.Horario_B | 192.168.4.31 | SCH:150:WEEKLY-SCHEDULE | Read+Write | Always
MSA_BT_ACS_Sot_3_Borrrell_Producc.Manual_horario | 192.168.4.31 | BV:151:PRESENT-VALUE | Read+Write | Always
MSA_BT_ACS_Sot_3_Borrrell_Producc.Marcha_paro | 192.168.4.31 | BV:152:PRESENT-VALUE | Read+Write | Always
MSA_BT_ACS_Sot_3_Borrrell_Producc.Reset_horas | 192.168.4.31 | BV:153:PRESENT-VALUE | Read | Always
MSA_BT_ACS_Sot_3_Borrrell_Producc_Temp_salida_IC | 192.168.4.31 | AI:4206:PRESENT-VALUE | Read | Always
MSA_BT_ACS_Sot_3_Borrrell_Producc_Temp_entrada_IC | 192.168.4.31 | AI:4205:PRESENT-VALUE | Read | Always
MSA_BT_ACS_Sot_3_Borrrell_Producc_Temp_acumulador | 192.168.4.31 | AI:4203:PRESENT-VALUE | Read | Always
MSA_BT_ACS_Sot_3_Borrrell_Producc_Consigna_deposito | 192.168.4.31 | AV:151:PRESENT-VALUE | Read+Write | Always
MSA_BT_ACS_Sot_3_Borrrell_Producc_Mando_valvula | 192.168.4.31 | BO:4504:PRESENT-VALUE | Read | Always
MSA_BT_ACS_Sot_3_Borrrell_Recirc.Horario_estado | 192.168.4.31 | SCH:160:PRESENT-VALUE | Read | Always
MSA_BT_ACS_Sot_3_Borrrell_Recirc.Horario_B | 192.168.4.31 | SCH:160:WEEKLY-SCHEDULE | Read+Write | Always
MSA_BT_ACS_Sot_3_Borrrell_Recirc.Manual_horario | 192.168.4.31 | BV:161:PRESENT-VALUE | Read+Write | Always
MSA_BT_ACS_Sot_3_Borrrell_Recirc.Marcha_paro | 192.168.4.31 | BV:162:PRESENT-VALUE | Read+Write | Always
MSA_BT_ACS_Sot_3_Borrrell_Recirc.Reset_horas | 192.168.4.31 | BV:163:PRESENT-VALUE | Read | Always
MSA_BT_ACS_Sot_3_Borrrell_Recirc_Temp_retorno | 192.168.4.31 | AI:4202:PRESENT-VALUE | Read | Always
MSA_BT_ACS_Sot_3_Borrrell_Recirc_Temp_recirculacion | 192.168.4.31 | AI:4204:PRESENT-VALUE | Read | Always
MSA_BT_ACS_Sot_3_Borrrell_Bomba_recirc_Estado | 192.168.4.31 | BI:4502:PRESENT-VALUE | Read | Always
MSA_BT_ACS_Sot_3_Borrrell_Bomba_recirc_Orden | 192.168.4.31 | BO:4502:PRESENT-VALUE | Read | Always
MSA_BT_ACS_Sot_3_Borrrell_Bomba_recirc_Fallo | 192.168.4.31 | BV:164:PRESENT-VALUE | Read | Always
MSA_BT_ACS_Sot_3_Borrrell_Bomba_recirc_Horas_funcionamiento | 192.168.4.31 | AV:164:PRESENT-VALUE | Read | Always
MSA_BT_ACS_Sot_3_Borrrell_Producc_Consigna_Antilegionela | 192.168.4.31 | AV:1107:PRESENT-VALUE | Read+Write | Always
MSA_BT_ACS_Sot_3_Borrrell_Producc_Activar_Antilegionela | 192.168.4.31 | BV:1114:PRESENT-VALUE | Read+Write | Always
MSA_BT_ACS_Sot_3_Tamarit_Producc.Horario_estado | 192.168.4.31 | SCH:180:PRESENT-VALUE | Read | Always
MSA_BT_ACS_Sot_3_Tamarit_Producc.Horario_B | 192.168.4.31 | SCH:180:WEEKLY-SCHEDULE | Read+Write | Always
MSA_BT_ACS_Sot_3_Tamarit_Producc.Manual_horario | 192.168.4.31 | BV:181:PRESENT-VALUE | Read+Write | Always
MSA_BT_ACS_Sot_3_Tamarit_Producc.Marcha_paro | 192.168.4.31 | BV:182:PRESENT-VALUE | Read+Write | Always
MSA_BT_ACS_Sot_3_Tamarit_Producc.Reset_horas | 192.168.4.31 | BV:183:PRESENT-VALUE | Read | Always
MSA_BT_ACS_Sot_3_Tamarit_Producc_Temp_salida_IC | 192.168.4.31 | AI:4104:PRESENT-VALUE | Read | Always
MSA_BT_ACS_Sot_3_Tamarit_Producc_Temp_entrada_IC | 192.168.4.31 | AI:4105:PRESENT-VALUE | Read | Always
MSA_BT_ACS_Sot_3_Tamarit_Producc_Temp_acumulador | 192.168.4.31 | AI:4102:PRESENT-VALUE | Read | Always
MSA_BT_ACS_Sot_3_Tamarit_Producc_Consigna_deposito | 192.168.4.31 | AV:181:PRESENT-VALUE | Read+Write | Always
MSA_BT_ACS_Sot_3_Tamarit_Producc_Mando_valvula | 192.168.4.31 | BO:4404:PRESENT-VALUE | Read | Always
MSA_BT_ACS_Sot_3_Tamarit_Recirc.Horario_estado | 192.168.4.31 | SCH:140:PRESENT-VALUE | Read | Always
MSA_BT_ACS_Sot_3_Tamarit_Recirc.Horario_B | 192.168.4.31 | SCH:140:WEEKLY-SCHEDULE | Read+Write | Always
MSA_BT_ACS_Sot_3_Tamarit_Recirc.Manual_horario | 192.168.4.31 | BV:141:PRESENT-VALUE | Read+Write | Always
MSA_BT_ACS_Sot_3_Tamarit_Recirc.Marcha_paro | 192.168.4.31 | BV:142:PRESENT-VALUE | Read+Write | Always
MSA_BT_ACS_Sot_3_Tamarit_Recirc.Reset_horas | 192.168.4.31 | BV:143:PRESENT-VALUE | Read | Always
MSA_BT_ACS_Sot_3_Tamarit_Recirc_Temp_retorno | 192.168.4.31 | AI:4101:PRESENT-VALUE | Read | Always
MSA_BT_ACS_Sot_3_Tamarit_Recirc_Temp_recirculacion | 192.168.4.31 | AI:4103:PRESENT-VALUE | Read | Always
MSA_BT_ACS_Sot_3_Tamarit_Bomba_recirc_Estado | 192.168.4.31 | BI:4402:PRESENT-VALUE | Read | Always
MSA_BT_ACS_Sot_3_Tamarit_Bomba_recirc_Orden | 192.168.4.31 | BO:4402:PRESENT-VALUE | Read | Always
MSA_BT_ACS_Sot_3_Tamarit_Bomba_recirc_Fallo | 192.168.4.31 | BV:144:PRESENT-VALUE | Read | Always
MSA_BT_ACS_Sot_3_Tamarit_Bomba_recirc_Horas_funcionamiento | 192.168.4.31 | AV:144:PRESENT-VALUE | Read | Always
MSA_BT_ACS_Sot_3_Tamarit_Producc_Consigna_Antilegionela | 192.168.4.31 | AV:1106:PRESENT-VALUE | Read+Write | Always
MSA_BT_ACS_Sot_3_Tamarit_Producc_Activar_Antilegionela | 192.168.4.31 | BV:1113:PRESENT-VALUE | Read+Write | Always
MSA_UT_ACS_Sot_3_Producc.Horario_estado | 192.168.4.41 | SCH:150:PRESENT-VALUE | Read | Always
MSA_UT_ACS_Sot_3_Producc.Horario_B | 192.168.4.41 | SCH:150:WEEKLY-SCHEDULE | Read+Write | Always
MSA_UT_ACS_Sot_3_Producc.Manual_horario | 192.168.4.41 | BV:151:PRESENT-VALUE | Read+Write | Always
MSA_UT_ACS_Sot_3_Producc.Marcha_paro | 192.168.4.41 | BV:152:PRESENT-VALUE | Read+Write | Always
MSA_UT_ACS_Sot_3_Producc.Reset_horas | 192.168.4.41 | BV:153:PRESENT-VALUE | Read | Always
MSA_UT_ACS_Sot_3_Producc_Temp_salida_IC | 192.168.4.41 | AI:4104:PRESENT-VALUE | Read | Always
MSA_UT_ACS_Sot_3_Producc_Temp_entrada_IC | 192.168.4.41 | AI:4105:PRESENT-VALUE | Read | Always
MSA_UT_ACS_Sot_3_Producc_Temp_acumulador | 192.168.4.41 | AI:4102:PRESENT-VALUE | Read | Always
MSA_UT_ACS_Sot_3_Producc_Consigna_deposito | 192.168.4.41 | AV:151:PRESENT-VALUE | Read+Write | Always
MSA_UT_ACS_Sot_3_Producc_Mando_valvula | 192.168.4.41 | BO:4304:PRESENT-VALUE | Read | Always
MSA_UT_ACS_Sot_3_Recirc.Horario_estado | 192.168.4.41 | SCH:160:PRESENT-VALUE | Read | Always
MSA_UT_ACS_Sot_3_Recirc.Horario_B | 192.168.4.41 | SCH:160:WEEKLY-SCHEDULE | Read+Write | Always
MSA_UT_ACS_Sot_3_Recirc.Manual_horario | 192.168.4.41 | BV:161:PRESENT-VALUE | Read+Write | Always
MSA_UT_ACS_Sot_3_Recirc.Marcha_paro | 192.168.4.41 | BV:162:PRESENT-VALUE | Read+Write | Always
MSA_UT_ACS_Sot_3_Recirc.Reset_horas | 192.168.4.41 | BV:163:PRESENT-VALUE | Read | Always
MSA_UT_ACS_Sot_3_Recirc_Temp_recirculacion | 192.168.4.41 | AI:4103:PRESENT-VALUE | Read | Always
MSA_UT_ACS_Sot_3_Bomba_recirc_Estado | 192.168.4.41 | BI:4302:PRESENT-VALUE | Read | Always
MSA_UT_ACS_Sot_3_Bomba_recirc_Orden | 192.168.4.41 | BO:4302:PRESENT-VALUE | Read | Always
MSA_UT_ACS_Sot_3_Bomba_recirc_Fallo | 192.168.4.41 | BV:164:PRESENT-VALUE | Read | Always
MSA_UT_ACS_Sot_3_Bomba_recirc_Horas_funcionamiento | 192.168.4.41 | AV:164:PRESENT-VALUE | Read | Always
MSA_UT_ACS_Sot_3_Producc_Consigna_Antilegionela | 192.168.4.41 | AV:1106:PRESENT-VALUE | Read+Write | Always
MSA_UT_ACS_Sot_3_Producc_Activar_Antilegionela | 192.168.4.41 | BV:1113:PRESENT-VALUE | Read+Write | Always
MSA_BT_Clima_vestuario_1.Estado_vent_imp | 192.168.4.31:50003:1 | BV:21:PRESENT-VALUE | Read+Write | Always
MSA_BT_Clima_vestuario_1.Temp_impulsion | 192.168.4.31:50003:1 | AI:1:PRESENT-VALUE | Read | Always
MSA_BT_Clima_vestuario_1.Humedad_impulsion | 192.168.4.31:50003:1 | AI:2:PRESENT-VALUE | Read | Always
MSA_BT_Clima_vestuario_1.Temp_retorno | 192.168.4.31:50003:1 | AI:5:PRESENT-VALUE | Read | Always
MSA_BT_Clima_vestuario_1.Humedad_retorno | 192.168.4.31:50003:1 | AI:6:PRESENT-VALUE | Read | Always
MSA_BT_Clima_vestuario_1.CO2_Retorno | 192.168.4.31:50003:1 | AI:9:PRESENT-VALUE | Read | Always
MSA_BT_Clima_vestuario_1.Consigna_temp_retorno | 192.168.4.31:50003:1 | AV:21:PRESENT-VALUE | Read+Write | Always
MSA_BT_Clima_vestuario_1.Temp_impuls_max | 192.168.4.31:50003:1 | AV:22:PRESENT-VALUE | Read+Write | Always
MSA_BT_Clima_vestuario_1.Temp_impuls_min | 192.168.4.31:50003:1 | AV:23:PRESENT-VALUE | Read+Write | Always
MSA_BT_Clima_vestuario_1.Valvula_calor | 192.168.4.31:50003:1 | AO:7:PRESENT-VALUE | Read | Always
MSA_BT_Clima_vestuario_2.Estado_vent_imp | 192.168.4.31:50003:1 | BV:22:PRESENT-VALUE | Read+Write | Always
MSA_BT_Clima_vestuario_2.Temp_impulsion | 192.168.4.31:50003:1 | AI:3:PRESENT-VALUE | Read | Always
MSA_BT_Clima_vestuario_2.Humedad_impulsion | 192.168.4.31:50003:1 | AI:4:PRESENT-VALUE | Read | Always
MSA_BT_Clima_vestuario_2.Temp_retorno | 192.168.4.31:50003:1 | AI:7:PRESENT-VALUE | Read | Always
MSA_BT_Clima_vestuario_2.Humedad_retorno | 192.168.4.31:50003:1 | AI:8:PRESENT-VALUE | Read | Always
MSA_BT_Clima_vestuario_2.CO2_Retorno | 192.168.4.31:50003:1 | AI:10:PRESENT-VALUE | Read | Always
MSA_BT_Clima_vestuario_2.Consigna_temp_retorno | 192.168.4.31:50003:1 | AV:24:PRESENT-VALUE | Read+Write | Always
MSA_BT_Clima_vestuario_2.Temp_impuls_max | 192.168.4.31:50003:1 | AV:25:PRESENT-VALUE | Read+Write | Always
MSA_BT_Clima_vestuario_2.Temp_impuls_min | 192.168.4.31:50003:1 | AV:26:PRESENT-VALUE | Read+Write | Always
MSA_BT_Clima_vestuario_2.Valvula_calor | 192.168.4.31:50003:1 | AO:8:PRESENT-VALUE | Read | Always
MSA_BT_Clima_vestuario_1_Orden_recuperador | 192.168.4.31:50003:1 | BV:23:PRESENT-VALUE | Read | Always
MSA_BT_Clima_vestuario_2_Orden_recuperador | 192.168.4.31:50003:1 | BV:24:PRESENT-VALUE | Read | Always
BM_Temperatura_media_Nucleo | 192.168.4.21 | AV:2101:PRESENT-VALUE | Read | Always
BM_Humedad_media_Nucleo | 192.168.4.21 | AV:2102:PRESENT-VALUE | Read | Always
BT_Temperatura_media_Nucleo | 192.168.4.31 | AV:2101:PRESENT-VALUE | Read | Always
BT_Humedad_media_Nucleo | 192.168.4.31 | AV:2102:PRESENT-VALUE | Read | Always
UT_Temperatura_media_Nucleo | 192.168.4.41 | AV:2101:PRESENT-VALUE | Read | Always
UT_Humedad_media_Nucleo | 192.168.4.41 | AV:2102:PRESENT-VALUE | Read | Always
UM_Temperatura_media_Nucleo | 192.168.4.51 | AV:2101:PRESENT-VALUE | Read | Always
UM_Humedad_media_Nucleo | 192.168.4.51 | AV:2102:PRESENT-VALUE | Read | Always
MSA_BM_Contador_Llenado_Instalaciones_Total | 192.168.4.21 | AV:2201:PRESENT-VALUE | Read | Always | 100000000
MSA_BM_Contador_Llenado_Instalaciones_Inicial | 192.168.4.21 | AV:2202:PRESENT-VALUE | Read+Write | Always | 100000000
MSA_BM_Contador_Llenado_Instalaciones_Reset | 192.168.4.21 | BV:2201:PRESENT-VALUE | Read+Write | Always
MSA_BT_Contador_Llenado_Instalaciones_Total | 192.168.4.31 | AV:2201:PRESENT-VALUE | Read | Always | 100000000
MSA_BT_Contador_Llenado_Instalaciones_Inicial | 192.168.4.31 | AV:2202:PRESENT-VALUE | Read+Write | Always | 100000000
MSA_BT_Contador_Llenado_Instalaciones_Reset | 192.168.4.31 | BV:2201:PRESENT-VALUE | Read+Write | Always
MSA_UT_Contador_Llenado_Instalaciones_Total | 192.168.4.41 | AV:2201:PRESENT-VALUE | Read | Always | 100000000
MSA_UT_Contador_Llenado_Instalaciones_Inicial | 192.168.4.41 | AV:2202:PRESENT-VALUE | Read+Write | Always | 100000000
MSA_UT_Contador_Llenado_Instalaciones_Reset | 192.168.4.41 | BV:2201:PRESENT-VALUE | Read+Write | Always
MSA_BM_Presostato_Agua_Red | 192.168.4.21 | BI:4504:PRESENT-VALUE | Read | Always
MSA_UT_Presostato_Agua_Red | 192.168.4.41 | BI:4203:PRESENT-VALUE | Read | Always
MSA_BM_Extractor_VE01.Horario_estado | 192.168.4.21 | SCH:181:PRESENT-VALUE | Read | Always
MSA_BM_Extractor_VE01.Horario_B | 192.168.4.21 | SCH:181:WEEKLY-SCHEDULE | Read+Write | Always
MSA_BM_Extractor_VE01.Manual_horario | 192.168.4.21 | BV:2202:PRESENT-VALUE | Read+Write | Always
MSA_BM_Extractor_VE01.Marcha_paro | 192.168.4.21 | BV:2203:PRESENT-VALUE | Read+Write | Always
MSA_BM_Extractor_VE01.Reset_horas | 192.168.4.21 | BV:2204:PRESENT-VALUE | Read+Write | Always
MSA_BM_Extractor_VE01.Horas_funcionam | 192.168.4.21 | AV:134:PRESENT-VALUE | Read | Always
MSA_BM_Extractor_VE01.Estado | 192.168.4.21 | BI:4501:PRESENT-VALUE | Read | Always
MSA_BM_Extractor_VE01.Orden | 192.168.4.21 | BO:4501:PRESENT-VALUE | Read | Always
MSA_BM_Extractor_VE01.Fallo | 192.168.4.21 | BV:134:PRESENT-VALUE | Read | Always
MSA_BM_Extractor_VE02.Horario_estado | 192.168.4.21 | SCH:182:PRESENT-VALUE | Read | Always
MSA_BM_Extractor_VE02.Horario_B | 192.168.4.21 | SCH:182:WEEKLY-SCHEDULE | Read+Write | Always
MSA_BM_Extractor_VE02.Manual_horario | 192.168.4.21 | BV:2205:PRESENT-VALUE | Read+Write | Always
MSA_BM_Extractor_VE02.Marcha_paro | 192.168.4.21 | BV:2206:PRESENT-VALUE | Read+Write | Always
MSA_BM_Extractor_VE02.Reset_horas | 192.168.4.21 | BV:2207:PRESENT-VALUE | Read+Write | Always
MSA_BM_Extractor_VE02.Horas_funcionam | 192.168.4.21 | AV:154:PRESENT-VALUE | Read | Always
MSA_BM_Extractor_VE02.Estado | 192.168.4.21 | BI:4601:PRESENT-VALUE | Read | Always
MSA_BM_Extractor_VE02.Orden | 192.168.4.21 | BO:4601:PRESENT-VALUE | Read | Always
MSA_BM_Extractor_VE02.Fallo | 192.168.4.21 | BV:154:PRESENT-VALUE | Read | Always
MSA_BT_Extractor_VE07.Horario_estado | 192.168.4.31 | SCH:181:PRESENT-VALUE | Read | Always
MSA_BT_Extractor_VE07.Horario_B | 192.168.4.31 | SCH:181:WEEKLY-SCHEDULE | Read+Write | Always
MSA_BT_Extractor_VE07.Manual_horario | 192.168.4.31 | BV:2202:PRESENT-VALUE | Read+Write | Always
MSA_BT_Extractor_VE07.Marcha_paro | 192.168.4.31 | BV:2203:PRESENT-VALUE | Read+Write | Always
MSA_BT_Extractor_VE07.Reset_horas | 192.168.4.31 | BV:2204:PRESENT-VALUE | Read+Write | Always
MSA_BT_Extractor_VE07.Horas_funcionam | 192.168.4.31 | AV:184:PRESENT-VALUE | Read | Always
MSA_BT_Extractor_VE07.Estado | 192.168.4.31 | BI:4401:PRESENT-VALUE | Read | Always
MSA_BT_Extractor_VE07.Orden | 192.168.4.31 | BO:4401:PRESENT-VALUE | Read | Always
MSA_BT_Extractor_VE07.Fallo | 192.168.4.31 | BV:184:PRESENT-VALUE | Read | Always
MSA_BT_Extractor_VE08.Horario_estado | 192.168.4.31 | SCH:182:PRESENT-VALUE | Read | Always
MSA_BT_Extractor_VE08.Horario_B | 192.168.4.31 | SCH:182:WEEKLY-SCHEDULE | Read+Write | Always
MSA_BT_Extractor_VE08.Manual_horario | 192.168.4.31 | BV:2205:PRESENT-VALUE | Read+Write | Always
MSA_BT_Extractor_VE08.Marcha_paro | 192.168.4.31 | BV:2206:PRESENT-VALUE | Read+Write | Always
MSA_BT_Extractor_VE08.Reset_horas | 192.168.4.31 | BV:2207:PRESENT-VALUE | Read+Write | Always
MSA_BT_Extractor_VE08.Horas_funcionam | 192.168.4.31 | AV:154:PRESENT-VALUE | Read | Always
MSA_BT_Extractor_VE08.Estado | 192.168.4.31 | BI:4501:PRESENT-VALUE | Read | Always
MSA_BT_Extractor_VE08.Orden | 192.168.4.31 | BO:4501:PRESENT-VALUE | Read | Always
MSA_BT_Extractor_VE08.Fallo | 192.168.4.31 | BV:154:PRESENT-VALUE | Read | Always
MSA_BT_Extractor_VE09B.Horario_estado | 192.168.4.31 | SCH:183:PRESENT-VALUE | Read | Always
MSA_BT_Extractor_VE09B.Horario_B | 192.168.4.31 | SCH:183:WEEKLY-SCHEDULE | Read+Write | Always
MSA_BT_Extractor_VE09B.Manual_horario | 192.168.4.31 | BV:2208:PRESENT-VALUE | Read+Write | Always
MSA_BT_Extractor_VE09B.Marcha_paro | 192.168.4.31 | BV:2209:PRESENT-VALUE | Read+Write | Always
MSA_BT_Extractor_VE09B.Reset_horas | 192.168.4.31 | BV:2210:PRESENT-VALUE | Read+Write | Always
MSA_BT_Extractor_VE09B.Horas_funcionam | 192.168.4.31 | AV:2203:PRESENT-VALUE | Read | Always
MSA_BT_Extractor_VE09B.Estado | 192.168.4.31 | BI:4403:PRESENT-VALUE | Read | Always
MSA_BT_Extractor_VE09B.Orden | 192.168.4.31 | BO:4403:PRESENT-VALUE | Read | Always
MSA_BT_Extractor_VE09B.Fallo | 192.168.4.31 | BV:185:PRESENT-VALUE | Read | Always
MSA_BT_Extractor_VE10B.Horario_estado | 192.168.4.31 | SCH:184:PRESENT-VALUE | Read | Always
MSA_BT_Extractor_VE10B.Horario_B | 192.168.4.31 | SCH:184:WEEKLY-SCHEDULE | Read+Write | Always
MSA_BT_Extractor_VE10B.Manual_horario | 192.168.4.31 | BV:2211:PRESENT-VALUE | Read+Write | Always
MSA_BT_Extractor_VE10B.Marcha_paro | 192.168.4.31 | BV:2212:PRESENT-VALUE | Read+Write | Always
MSA_BT_Extractor_VE10B.Reset_horas | 192.168.4.31 | BV:2213:PRESENT-VALUE | Read+Write | Always
MSA_BT_Extractor_VE10B.Horas_funcionam | 192.168.4.31 | AV:2204:PRESENT-VALUE | Read | Always
MSA_BT_Extractor_VE10B.Estado | 192.168.4.31 | BI:4503:PRESENT-VALUE | Read | Always
MSA_BT_Extractor_VE10B.Orden | 192.168.4.31 | BO:4503:PRESENT-VALUE | Read | Always
MSA_BT_Extractor_VE10B.Fallo | 192.168.4.31 | BV:155:PRESENT-VALUE | Read | Always
MSA_UT_Extractor_VE13.Horario_estado | 192.168.4.41 | SCH:183:PRESENT-VALUE | Read | Always
MSA_UT_Extractor_VE13.Horario_B | 192.168.4.41 | SCH:183:WEEKLY-SCHEDULE | Read+Write | Always
MSA_UT_Extractor_VE13.Manual_horario | 192.168.4.41 | BV:2208:PRESENT-VALUE | Read+Write | Always
MSA_UT_Extractor_VE13.Marcha_paro | 192.168.4.41 | BV:2209:PRESENT-VALUE | Read+Write | Always
MSA_UT_Extractor_VE13.Reset_horas | 192.168.4.41 | BV:2210:PRESENT-VALUE | Read+Write | Always
MSA_UT_Extractor_VE13.Horas_funcionam | 192.168.4.41 | AV:154:PRESENT-VALUE | Read | Always
MSA_UT_Extractor_VE13.Estado | 192.168.4.41 | BI:4301:PRESENT-VALUE | Read | Always
MSA_UT_Extractor_VE13.Orden | 192.168.4.41 | BO:4301:PRESENT-VALUE | Read | Always
MSA_UT_Extractor_VE13.Fallo | 192.168.4.41 | BV:154:PRESENT-VALUE | Read | Always
MSA_UT_Extractor_VE14.Horario_estado | 192.168.4.41 | SCH:184:PRESENT-VALUE | Read | Always
MSA_UT_Extractor_VE14.Horario_B | 192.168.4.41 | SCH:184:WEEKLY-SCHEDULE | Read+Write | Always
MSA_UT_Extractor_VE14.Manual_horario | 192.168.4.41 | BV:2211:PRESENT-VALUE | Read+Write | Always
MSA_UT_Extractor_VE14.Marcha_paro | 192.168.4.41 | BV:2212:PRESENT-VALUE | Read+Write | Always
MSA_UT_Extractor_VE14.Reset_horas | 192.168.4.41 | BV:2213:PRESENT-VALUE | Read+Write | Always
MSA_UT_Extractor_VE14.Horas_funcionam | 192.168.4.41 | AV:2203:PRESENT-VALUE | Read | Always
MSA_UT_Extractor_VE14.Estado | 192.168.4.41 | BI:4303:PRESENT-VALUE | Read | Always
MSA_UT_Extractor_VE14.Orden | 192.168.4.41 | BO:4303:PRESENT-VALUE | Read | Always
MSA_UT_Extractor_VE14.Fallo | 192.168.4.41 | BV:155:PRESENT-VALUE | Read | Always
MSA_UT_Alarma_Variador_Ventilador_ET | 192.168.4.41 | BI:4101:PRESENT-VALUE | Read | Always
BM_Offset_Temp_Media_Display | 192.168.4.21 | AV:2301:PRESENT-VALUE | Read+Write | Always
BM_Offset_Humedad_Media_Display | 192.168.4.21 | AV:2302:PRESENT-VALUE | Read+Write | Always
BT_Offset_Temp_Media_Display | 192.168.4.31 | AV:2301:PRESENT-VALUE | Read+Write | Always
BT_Offset_Humedad_Media_Display | 192.168.4.31 | AV:2302:PRESENT-VALUE | Read+Write | Always
UT_Offset_Temp_Media_Display | 192.168.4.41 | AV:2301:PRESENT-VALUE | Read+Write | Always
UT_Offset_Humedad_Media_Display | 192.168.4.41 | AV:2302:PRESENT-VALUE | Read+Write | Always
UM_Offset_Temp_Media_Display | 192.168.4.51 | AV:2301:PRESENT-VALUE | Read+Write | Always
UM_Offset_Humedad_Media_Display | 192.168.4.51 | AV:2302:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_ESE_AEROTERMIA_GEOTERMIA | 192.168.4.21 | BV:1104:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_ESD_AEROTERMIA_GEOTERMIA | 192.168.4.21 | BV:1105:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_MFZCE_AEROTERMIA_GEOTERMIA | 192.168.4.21 | BV:1106:PRESENT-VALUE | Read+Write | Always
MSA_BM_Cl_MFZCA_AEROTERMIA_GEOTERMIA | 192.168.4.21 | BV:1107:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_ESE_AEROTERMIA_GEOTERMIA | 192.168.4.31 | BV:1104:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_ESD_AEROTERMIA_GEOTERMIA | 192.168.4.31 | BV:1105:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_MFZCE_AEROTERMIA_GEOTERMIA | 192.168.4.31 | BV:1106:PRESENT-VALUE | Read+Write | Always
MSA_BT_Cl_MFZCA_AEROTERMIA_GEOTERMIA | 192.168.4.31 | BV:1107:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_ESE_AEROTERMIA_GEOTERMIA | 192.168.4.41 | BV:1104:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_ESD_AEROTERMIA_GEOTERMIA | 192.168.4.41 | BV:1105:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_MFZCE_AEROTERMIA_GEOTERMIA | 192.168.4.41 | BV:1106:PRESENT-VALUE | Read+Write | Always
MSA_UT_Cl_MFZCA_AEROTERMIA_GEOTERMIA | 192.168.4.41 | BV:1107:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_ESE_AEROTERMIA_GEOTERMIA | 192.168.4.51 | BV:1104:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_ESD_AEROTERMIA_GEOTERMIA | 192.168.4.51 | BV:1105:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_MFZCE_AEROTERMIA_GEOTERMIA | 192.168.4.51 | BV:1106:PRESENT-VALUE | Read+Write | Always
MSA_UM_Cl_MFZCA_AEROTERMIA_GEOTERMIA | 192.168.4.51 | BV:1107:PRESENT-VALUE | Read+Write | Always
MSA_UT_Enfriam_adiabatico.Horario_estado | 192.168.4.41:50004:1 | SCH:10:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico.Horario_B | 192.168.4.41:50004:1 | SCH:10:WEEKLY-SCHEDULE | Read+Write | Always
MSA_UT_Enfriam_adiabatico.Manual_horario | 192.168.4.41:50004:1 | BV:11:PRESENT-VALUE | Read+Write | Always
MSA_UT_Enfriam_adiabatico.Marcha_paro | 192.168.4.41:50004:1 | BV:12:PRESENT-VALUE | Read+Write | Always
MSA_UT_Enfriam_adiabatico.Reset_horas | 192.168.4.41:50004:1 | BV:13:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico_Horas_funcionamiento | 192.168.4.41:50004:1 | AV:11:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico_Consigna_adiabatico | 192.168.4.41:50004:1 | AV:12:PRESENT-VALUE | Read+Write | Always
MSA_UT_Enfriam_adiabatico_Consigna_aerotermia | 192.168.4.41:50004:1 | AV:13:PRESENT-VALUE | Read+Write | Always
MSA_UT_Enfriam_adiabatico_Diferencial_aerotermia | 192.168.4.41:50004:1 | AV:14:PRESENT-VALUE | Read+Write | Always
MSA_UT_Enfriam_adiabatico_Temp_galeria_antes_bat_agua | 192.168.4.41:50004:1 | AI:2:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico_HR_galeria_antes_bat_agua | 192.168.4.41:50004:1 | AI:3:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico_Temp_despues_de_bat_agua | 192.168.4.41:50004:1 | AI:4:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico_HR_despues_de_bat_agua | 192.168.4.41:50004:1 | AI:5:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico_Temp_despues_de_bat_aerotermia | 192.168.4.41:50004:1 | AI:6:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico_HR_despues_de_bat_aerotermia | 192.168.4.41:50004:1 | AI:7:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico_Temp_ambiente_Muelle | 192.168.4.41:50004:1 | AI:1:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico_T_entrada_AF_bat_2_sotano | 192.168.4.41:50004:1 | AI:8:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico_T_salida_AF_bat_2_sotano | 192.168.4.41:50004:1 | AI:9:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico_T_entrada_AF_bat_1_sotano | 192.168.4.41:50004:1 | AI:10:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico_T_salida_AF_bat_1_sotano | 192.168.4.41:50004:1 | AI:11:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico_Mando_valvula_1_sotano | 192.168.4.41:50004:1 | BO:1:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico_Mando_valvula_2_sotano | 192.168.4.41:50004:1 | BO:2:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico_Estado_ventiladores | 192.168.4.41 | BI:2501:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico_Orden_ventiladores | 192.168.4.41 | BO:2203:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico_Fallo_ventiladores | 192.168.4.41 | BV:3001:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico_Orden_aerotermia | 192.168.4.41 | BO:2302:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico_T_entrada_AF_bat_altillo | 192.168.4.41 | AI:2401:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico_T_salida_AF_bat_altillo | 192.168.4.41 | AI:2402:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico_Mando_valvula_1_Altillo | 192.168.4.41 | BO:2201:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico_Mando_valvula_2_Altillo | 192.168.4.41 | BO:2202:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico_Estado_bomba_adiabatico | 192.168.4.41 | BI:2503:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico_Orden_bomba_adiabatico | 192.168.4.41 | BO:2301:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico_Fallo_bomba_adiabatico | 192.168.4.41 | BV:3002:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico_Estado_lanza | 192.168.4.41 | BI:2502:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico_Orden_lanza | 192.168.4.41 | BO:2204:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico_Fallo_lanza | 192.168.4.41 | BV:3003:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico_Temp_despues_de_lanza | 192.168.4.41 | AI:2303:PRESENT-VALUE | Read | Always
MSA_UT_Enfriam_adiabatico_HR_despues_de_lanza | 192.168.4.41 | AI:2304:PRESENT-VALUE | Read | Always
MSA_UT_Contador_Llenado_Adiabatico_Total | 192.168.4.41 | AV:2303:PRESENT-VALUE | Read | Always | 100000000
MSA_UT_Contador_Llenado_Adiabatico_Inicial | 192.168.4.41 | AV:2304:PRESENT-VALUE | Read+Write | Always | 100000000
MSA_UT_Contador_Llenado_Adiabatico_Reset | 192.168.4.41 | BV:3004:PRESENT-VALUE | Read+Write | Always
MSA_BM_AG_BAC_Prim_IC_Ent_Vecinal_Ajuste_variador | 192.168.4.21 | AV:200:PRESENT-VALUE | Read+Write | Always
MSA_BM_AG_BAF_Prim_IC_Ent_Vecinal_Reset_horas | 192.168.4.21 | BV:200:PRESENT-VALUE | Read+Write | Always
MSA_BM_AG_BAF_1_Prim_IC_Ent_Vecinal.Estado | 192.168.4.21 | BI:4701:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAF_1_Prim_IC_Ent_Vecinal.Orden | 192.168.4.21 | BO:4701:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAF_1_Prim_IC_Ent_Vecinal.Fallo | 192.168.4.21 | BV:201:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAF_1_Prim_IC_Ent_Vecinal.Horas_funcionam | 192.168.4.21 | AV:201:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAC_1_Prim_IC_Ent_Vecinal.Alarma_variador | 192.168.4.21 | BI:5101:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAC_1_Prim_IC_Ent_Vecinal.Mando_Variador | 192.168.4.21 | AO:5101:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAF_2_Prim_IC_Ent_Vecinal.Estado | 192.168.4.21 | BI:4702:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAF_2_Prim_IC_Ent_Vecinal.Orden | 192.168.4.21 | BO:4702:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAF_2_Prim_IC_Ent_Vecinal.Fallo | 192.168.4.21 | BV:202:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAF_2_Prim_IC_Ent_Vecinal.Horas_funcionam | 192.168.4.21 | AV:202:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAC_2_Prim_IC_Ent_Vecinal.Alarma_variador | 192.168.4.21 | BI:5102:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAC_2_Prim_IC_Ent_Vecinal.Mando_Variador | 192.168.4.21 | AO:5102:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAC_Prim_IC_Ent_Romanos_Ajuste_variador | 192.168.4.21 | AV:210:PRESENT-VALUE | Read+Write | Always
MSA_BM_AG_BAC_Prim_IC_Ent_Vecinal_Reset_horas | 192.168.4.21 | BV:210:PRESENT-VALUE | Read+Write | Always
MSA_BM_AG_BAC_1_Prim_IC_Ent_Vecinal.Estado | 192.168.4.21 | BI:4703:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAC_1_Prim_IC_Ent_Vecinal.Orden | 192.168.4.21 | BO:4703:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAC_1_Prim_IC_Ent_Vecinal.Fallo | 192.168.4.21 | BV:211:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAC_1_Prim_IC_Ent_Vecinal.Horas_funcionam | 192.168.4.21 | AV:211:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAC_1_Prim_IC_Romanos.Alarma_variador | 192.168.4.21 | BI:5103:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAC_1_Prim_IC_Romanos.Mando_Variador | 192.168.4.21 | AO:5103:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAC_2_Prim_IC_Ent_Vecinal.Estado | 192.168.4.21 | BI:4704:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAC_2_Prim_IC_Ent_Vecinal.Orden | 192.168.4.21 | BO:4704:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAC_2_Prim_IC_Ent_Vecinal.Fallo | 192.168.4.21 | BV:212:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAC_2_Prim_IC_Ent_Vecinal.Horas_funcionam | 192.168.4.21 | AV:212:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAC_2_Prim_IC_Romanos.Alarma_variador | 192.168.4.21 | BI:5104:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAC_2_Prim_IC_Romanos.Mando_Variador | 192.168.4.21 | AO:5104:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAF_Prim_IC_Romanos_Reset_horas | 192.168.4.21 | BV:220:PRESENT-VALUE | Read+Write | Always
MSA_BM_AG_BAF_1_Prim_IC_Romanos.Estado | 192.168.4.21 | BI:4801:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAF_1_Prim_IC_Romanos.Orden | 192.168.4.21 | BO:4801:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAF_1_Prim_IC_Romanos.Fallo | 192.168.4.21 | BV:221:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAF_1_Prim_IC_Romanos.Horas_funcionam | 192.168.4.21 | AV:221:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAF_2_Prim_IC_Romanos.Estado | 192.168.4.21 | BI:4802:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAF_2_Prim_IC_Romanos.Orden | 192.168.4.21 | BO:4802:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAF_2_Prim_IC_Romanos.Fallo | 192.168.4.21 | BV:222:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAF_2_Prim_IC_Romanos.Horas_funcionam | 192.168.4.21 | AV:222:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAC_Prim_IC_Romanos_Reset_horas | 192.168.4.21 | BV:223:PRESENT-VALUE | Read+Write | Always
MSA_BM_AG_BAC_1_Prim_IC_Romanos.Estado | 192.168.4.21 | BI:4803:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAC_1_Prim_IC_Romanos.Orden | 192.168.4.21 | BO:4803:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAC_1_Prim_IC_Romanos.Fallo | 192.168.4.21 | BV:224:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAC_1_Prim_IC_Romanos.Horas_funcionam | 192.168.4.21 | AV:225:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAC_2_Prim_IC_Romanos.Estado | 192.168.4.21 | BI:4804:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAC_2_Prim_IC_Romanos.Orden | 192.168.4.21 | BO:4804:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAC_2_Prim_IC_Romanos.Fallo | 192.168.4.21 | BV:226:PRESENT-VALUE | Read | Always
MSA_BM_AG_BAC_2_Prim_IC_Romanos.Horas_funcionam | 192.168.4.21 | AV:227:PRESENT-VALUE | Read | Always
MSA_BT_AG_BAF_Prim_IC_Local_Com_02_Ajuste_variador | 192.168.4.31 | AV:220:PRESENT-VALUE | Read+Write | Always
MSA_BT_AG_BAF_Prim_IC_Local_Com_02_Reset_horas | 192.168.4.31 | BV:200:PRESENT-VALUE | Read+Write | Always
MSA_BT_AG_BAF_1_Prim_IC_Local_Com_02.Estado | 192.168.4.31 | BI:4601:PRESENT-VALUE | Read | Always
MSA_BT_AG_BAF_1_Prim_IC_Local_Com_02.Orden | 192.168.4.31 | BO:4601:PRESENT-VALUE | Read | Always
MSA_BT_AG_BAF_1_Prim_IC_Local_Com_02.Fallo | 192.168.4.31 | BV:201:PRESENT-VALUE | Read | Always
MSA_BT_AG_BAF_1_Prim_IC_Local_Com_02.Horas_funcionam | 192.168.4.31 | AV:221:PRESENT-VALUE | Read | Always
MSA_BT_AG_BAF_1_Prim_IC_Local_Com_02.Alarma_variador | 192.168.4.31 | BI:4701:PRESENT-VALUE | Read | Always
MSA_BT_AG_BAF_1_Prim_IC_Local_Com_02.Mando_Variador | 192.168.4.31 | AO:4701:PRESENT-VALUE | Read | Always
MSA_BT_AG_BAF_2_Prim_IC_Local_Com_02.Estado | 192.168.4.31 | BI:4602:PRESENT-VALUE | Read | Always
MSA_BT_AG_BAF_2_Prim_IC_Local_Com_02.Orden | 192.168.4.31 | BO:4602:PRESENT-VALUE | Read | Always
MSA_BT_AG_BAF_2_Prim_IC_Local_Com_02.Fallo | 192.168.4.31 | BV:202:PRESENT-VALUE | Read | Always
MSA_BT_AG_BAF_2_Prim_IC_Local_Com_02.Horas_funcionam | 192.168.4.31 | AV:222:PRESENT-VALUE | Read | Always
MSA_BT_AG_BAF_2_Prim_IC_Local_Com_02.Alarma_variador | 192.168.4.31 | BI:4702:PRESENT-VALUE | Read | Always
MSA_BT_AG_BAF_2_Prim_IC_Local_Com_02.Mando_Variador | 192.168.4.31 | AO:4702:PRESENT-VALUE | Read | Always
MSA_BT_AG_BAC_Prim_IC_Local_Com_02_Ajuste_variador | 192.168.4.31 | AV:210:PRESENT-VALUE | Read+Write | Always
MSA_BT_AG_BAC_Prim_IC_Local_Com_02_Reset_horas | 192.168.4.31 | BV:210:PRESENT-VALUE | Read+Write | Always
MSA_BT_AG_BAC_1_Prim_IC_Local_Com_02.Estado | 192.168.4.31 | BI:4603:PRESENT-VALUE | Read | Always
MSA_BT_AG_BAC_1_Prim_IC_Local_Com_02.Orden | 192.168.4.31 | BO:4603:PRESENT-VALUE | Read | Always
MSA_BT_AG_BAC_1_Prim_IC_Local_Com_02.Fallo | 192.168.4.31 | BV:211:PRESENT-VALUE | Read | Always
MSA_BT_AG_BAC_1_Prim_IC_Local_Com_02.Horas_funcionam | 192.168.4.31 | AV:211:PRESENT-VALUE | Read | Always
MSA_BT_AG_BAC_1_Prim_IC_Local_Com_02.Alarma_variador | 192.168.4.31 | BI:4703:PRESENT-VALUE | Read | Always
MSA_BT_AG_BAC_1_Prim_IC_Local_Com_02.Mando_Variador | 192.168.4.31 | AO:4703:PRESENT-VALUE | Read | Always
MSA_BT_AG_BAC_2_Prim_IC_Local_Com_02.Estado | 192.168.4.31 | BI:4604:PRESENT-VALUE | Read | Always
MSA_BT_AG_BAC_2_Prim_IC_Local_Com_02.Orden | 192.168.4.31 | BO:4604:PRESENT-VALUE | Read | Always
MSA_BT_AG_BAC_2_Prim_IC_Local_Com_02.Fallo | 192.168.4.31 | BV:212:PRESENT-VALUE | Read | Always
MSA_BT_AG_BAC_2_Prim_IC_Local_Com_02.Horas_funcionam | 192.168.4.31 | AV:212:PRESENT-VALUE | Read | Always
MSA_BT_AG_BAC_2_Prim_IC_Local_Com_02.Alarma_variador | 192.168.4.31 | BI:4704:PRESENT-VALUE | Read | Always
MSA_BT_AG_BAC_2_Prim_IC_Local_Com_02.Mando_Variador | 192.168.4.31 | AO:4704:PRESENT-VALUE | Read | Always
MSA_UT_AG_BAF_Prim_IC_Ent_Vecinal_Reset_horas | 192.168.4.41 | BV:220:PRESENT-VALUE | Read+Write | Always
MSA_UT_AG_BAF_1_Prim_IC_Ent_Vecinal.Estado | 192.168.4.41 | BI:4401:PRESENT-VALUE | Read | Always
MSA_UT_AG_BAF_1_Prim_IC_Ent_Vecinal.Orden | 192.168.4.41 | BO:4401:PRESENT-VALUE | Read | Always
MSA_UT_AG_BAF_1_Prim_IC_Ent_Vecinal.Fallo | 192.168.4.41 | BV:221:PRESENT-VALUE | Read | Always
MSA_UT_AG_BAF_1_Prim_IC_Ent_Vecinal.Horas_funcionam | 192.168.4.41 | AV:221:PRESENT-VALUE | Read | Always
MSA_UT_AG_BAF_2_Prim_IC_Ent_Vecinal.Estado | 192.168.4.41 | BI:4402:PRESENT-VALUE | Read | Always
MSA_UT_AG_BAF_2_Prim_IC_Ent_Vecinal.Orden | 192.168.4.41 | BO:4402:PRESENT-VALUE | Read | Always
MSA_UT_AG_BAF_2_Prim_IC_Ent_Vecinal.Fallo | 192.168.4.41 | BV:222:PRESENT-VALUE | Read | Always
MSA_UT_AG_BAF_2_Prim_IC_Ent_Vecinal.Horas_funcionam | 192.168.4.41 | AV:222:PRESENT-VALUE | Read | Always
MSA_UT_AG_BAC_Prim_IC_Ent_Vecinal_Reset_horas | 192.168.4.41 | BV:223:PRESENT-VALUE | Read+Write | Always
MSA_UT_AG_BAC_1_Prim_IC_Ent_Vecinal.Estado | 192.168.4.41 | BI:4403:PRESENT-VALUE | Read | Always
MSA_UT_AG_BAC_1_Prim_IC_Ent_Vecinal.Orden | 192.168.4.41 | BO:4403:PRESENT-VALUE | Read | Always
MSA_UT_AG_BAC_1_Prim_IC_Ent_Vecinal.Fallo | 192.168.4.41 | BV:224:PRESENT-VALUE | Read | Always
MSA_UT_AG_BAC_1_Prim_IC_Ent_Vecinal.Horas_funcionam | 192.168.4.41 | AV:225:PRESENT-VALUE | Read | Always
MSA_UT_AG_BAC_2_Prim_IC_Ent_Vecinal.Estado | 192.168.4.41 | BI:4404:PRESENT-VALUE | Read | Always
MSA_UT_AG_BAC_2_Prim_IC_Ent_Vecinal.Orden | 192.168.4.41 | BO:4404:PRESENT-VALUE | Read | Always
MSA_UT_AG_BAC_2_Prim_IC_Ent_Vecinal.Fallo | 192.168.4.41 | BV:226:PRESENT-VALUE | Read | Always
MSA_UT_AG_BAC_2_Prim_IC_Ent_Vecinal.Horas_funcionam | 192.168.4.41 | AV:227:PRESENT-VALUE | Read | Always
MSA_UT_AG_BAC_1_Prim_IC_Ent_Vecinal.Alarma_variador | 192.168.4.41 | BI:4501:PRESENT-VALUE | Read | Always
MSA_UT_AG_BAC_2_Prim_IC_Ent_Vecinal.Alarma_variador | 192.168.4.41 | BI:4502:PRESENT-VALUE | Read | Always
MSA_UT_AG_BAC_1_Prim_IC_Ent_Vecinal.Mando_Variador | 192.168.4.41 | AO:4501:PRESENT-VALUE | Read | Always
MSA_UT_AG_BAC_2_Prim_IC_Ent_Vecinal.Mando_Variador | 192.168.4.41 | AO:4502:PRESENT-VALUE | Read | Always
MSA_UT_AG_BAC_Prim_IC_Ent_Vecinal_Ajuste_variador | 192.168.4.41 | AV:200:PRESENT-VALUE | Read+Write | Always
MSA_BM_Pozo_Pluviales_Alarma_Bomba | 192.168.4.21 | BI:4303:PRESENT-VALUE | Read | Always
MSA_BM_Pozo_Pluviales_Alarma_Nivel | 192.168.4.21 | BI:4304:PRESENT-VALUE | Read | Always

## BACNET2
|  |  | (All) | (All)
MSA_BT_CL_ESE_Aerotermia.Temp_Aspiracion_Refrigerante_Circ_1 | 192.168.4.35:6:0:000000000015 | AI:1:PRESENT-VALUE | Read | Always
MSA_BT_CL_ESE_Aerotermia.Temp_Liquida_Refrigerante_Circ_1 | 192.168.4.35:6:0:000000000015 | AI:2:PRESENT-VALUE | Read | Always
MSA_BT_CL_ESE_Aerotermia.Temp_Exterior | 192.168.4.35:6:0:000000000015 | AI:3:PRESENT-VALUE | Read | Always
MSA_BT_CL_ESE_Aerotermia.Temp_Aspiracion_Refrigerante_Circ_2 | 192.168.4.35:6:0:000000000015 | AI:4:PRESENT-VALUE | Read | Always
MSA_BT_CL_ESE_Aerotermia.Temp_Liquida_Refrigerante_Circ_2 | 192.168.4.35:6:0:000000000015 | AI:5:PRESENT-VALUE | Read | Always
MSA_BT_CL_ESE_Aerotermia.Temp_Descarga_Refrigerante_Circ_1 | 192.168.4.35:6:0:000000000015 | AI:6:PRESENT-VALUE | Read | Always
MSA_BT_CL_ESE_Aerotermia.Temp_Descarga_Refrigerante_Circ_2 | 192.168.4.35:6:0:000000000015 | AI:7:PRESENT-VALUE | Read | Always
MSA_BT_CL_ESE_Aerotermia.Temp_Retorno | 192.168.4.35:6:0:000000000015 | AI:16:PRESENT-VALUE | Read | Always
MSA_BT_CL_ESE_Aerotermia.Codigo_Alarma | 192.168.4.35:6:0:000000000015 | AI:31:PRESENT-VALUE | Read | Always
MSA_BT_CL_ESE_Aerotermia.Horas_Funcionamiento_Compresor_1 | 192.168.4.35:6:0:000000000015 | AI:19:PRESENT-VALUE | Read | Always
MSA_BT_CL_ESE_Aerotermia.Horas_Funcionamiento_Compresor_2 | 192.168.4.35:6:0:000000000015 | AI:20:PRESENT-VALUE | Read | Always
MSA_BT_CL_ESE_Aerotermia.Consigna_Temperatura_Frio | 192.168.4.35:6:0:000000000015 | AV:2:PRESENT-VALUE | Read+Write | Always
MSA_BT_CL_ESE_Aerotermia.Consigna_Temperatura_Calor | 192.168.4.35:6:0:000000000015 | AV:3:PRESENT-VALUE | Read+Write | Always
MSA_BT_CL_ESE_Aerotermia.Modo_Funcionamiento | 192.168.4.35:6:0:000000000015 | AV:8:PRESENT-VALUE | Read+Write | Always
MSA_BT_CL_ESE_Aerotermia.Reset_Alarma | 192.168.4.35:6:0:000000000015 | BV:2:PRESENT-VALUE | Read+Write | Always
MSA_BT_CL_MFZCA_Aerotermia.Temp_Aspiracion_Refrigerante_Circ_1 | 192.168.4.35:6:0:000000000017 | AI:1:PRESENT-VALUE | Read | Always
MSA_BT_CL_MFZCA_Aerotermia.Temp_Liquida_Refrigerante_Circ_1 | 192.168.4.35:6:0:000000000017 | AI:2:PRESENT-VALUE | Read | Always
MSA_BT_CL_MFZCA_Aerotermia.Temp_Exterior | 192.168.4.35:6:0:000000000017 | AI:3:PRESENT-VALUE | Read | Always
MSA_BT_CL_MFZCA_Aerotermia.Temp_Aspiracion_Refrigerante_Circ_2 | 192.168.4.35:6:0:000000000017 | AI:4:PRESENT-VALUE | Read | Always
MSA_BT_CL_MFZCA_Aerotermia.Temp_Liquida_Refrigerante_Circ_2 | 192.168.4.35:6:0:000000000017 | AI:5:PRESENT-VALUE | Read | Always
MSA_BT_CL_MFZCA_Aerotermia.Temp_Descarga_Refrigerante_Circ_1 | 192.168.4.35:6:0:000000000017 | AI:6:PRESENT-VALUE | Read | Always
MSA_BT_CL_MFZCA_Aerotermia.Temp_Descarga_Refrigerante_Circ_2 | 192.168.4.35:6:0:000000000017 | AI:7:PRESENT-VALUE | Read | Always
MSA_BT_CL_MFZCA_Aerotermia.Temp_Retorno | 192.168.4.35:6:0:000000000017 | AI:16:PRESENT-VALUE | Read | Always
MSA_BT_CL_MFZCA_Aerotermia.Codigo_Alarma | 192.168.4.35:6:0:000000000017 | AI:31:PRESENT-VALUE | Read | Always
MSA_BT_CL_MFZCA_Aerotermia.Horas_Funcionamiento_Compresor_1 | 192.168.4.35:6:0:000000000017 | AI:19:PRESENT-VALUE | Read | Always
MSA_BT_CL_MFZCA_Aerotermia.Horas_Funcionamiento_Compresor_2 | 192.168.4.35:6:0:000000000017 | AI:20:PRESENT-VALUE | Read | Always
MSA_BT_CL_MFZCA_Aerotermia.Consigna_Temperatura_Frio | 192.168.4.35:6:0:000000000017 | AV:2:PRESENT-VALUE | Read+Write | Always
MSA_BT_CL_MFZCA_Aerotermia.Consigna_Temperatura_Calor | 192.168.4.35:6:0:000000000017 | AV:3:PRESENT-VALUE | Read+Write | Always
MSA_BT_CL_MFZCA_Aerotermia.Modo_Funcionamiento | 192.168.4.35:6:0:000000000017 | AV:8:PRESENT-VALUE | Read+Write | Always
MSA_BT_CL_MFZCA_Aerotermia.Reset_Alarma | 192.168.4.35:6:0:000000000017 | BV:2:PRESENT-VALUE | Read+Write | Always
MSA_BT_CL_ESD_Aerotermia.Temp_Aspiracion_Refrigerante_Circ_1 | 192.168.4.35:6:0:000000000018 | AI:1:PRESENT-VALUE | Read | Always
MSA_BT_CL_ESD_Aerotermia.Temp_Liquida_Refrigerante_Circ_1 | 192.168.4.35:6:0:000000000018 | AI:2:PRESENT-VALUE | Read | Always
MSA_BT_CL_ESD_Aerotermia.Temp_Exterior | 192.168.4.35:6:0:000000000018 | AI:3:PRESENT-VALUE | Read | Always
MSA_BT_CL_ESD_Aerotermia.Temp_Aspiracion_Refrigerante_Circ_2 | 192.168.4.35:6:0:000000000018 | AI:4:PRESENT-VALUE | Read | Always
MSA_BT_CL_ESD_Aerotermia.Temp_Liquida_Refrigerante_Circ_2 | 192.168.4.35:6:0:000000000018 | AI:5:PRESENT-VALUE | Read | Always
MSA_BT_CL_ESD_Aerotermia.Temp_Descarga_Refrigerante_Circ_1 | 192.168.4.35:6:0:000000000018 | AI:6:PRESENT-VALUE | Read | Always
MSA_BT_CL_ESD_Aerotermia.Temp_Descarga_Refrigerante_Circ_2 | 192.168.4.35:6:0:000000000018 | AI:7:PRESENT-VALUE | Read | Always
MSA_BT_CL_ESD_Aerotermia.Temp_Retorno | 192.168.4.35:6:0:000000000018 | AI:16:PRESENT-VALUE | Read | Always
MSA_BT_CL_ESD_Aerotermia.Codigo_Alarma | 192.168.4.35:6:0:000000000018 | AI:31:PRESENT-VALUE | Read | Always
MSA_BT_CL_ESD_Aerotermia.Horas_Funcionamiento_Compresor_1 | 192.168.4.35:6:0:000000000018 | AI:19:PRESENT-VALUE | Read | Always
MSA_BT_CL_ESD_Aerotermia.Horas_Funcionamiento_Compresor_2 | 192.168.4.35:6:0:000000000018 | AI:20:PRESENT-VALUE | Read | Always
MSA_BT_CL_ESD_Aerotermia.Consigna_Temperatura_Frio | 192.168.4.35:6:0:000000000018 | AV:2:PRESENT-VALUE | Read+Write | Always
MSA_BT_CL_ESD_Aerotermia.Consigna_Temperatura_Calor | 192.168.4.35:6:0:000000000018 | AV:3:PRESENT-VALUE | Read+Write | Always
MSA_BT_CL_ESD_Aerotermia.Modo_Funcionamiento | 192.168.4.35:6:0:000000000018 | AV:8:PRESENT-VALUE | Read+Write | Always
MSA_BT_CL_ESD_Aerotermia.Reset_Alarma | 192.168.4.35:6:0:000000000018 | BV:2:PRESENT-VALUE | Read+Write | Always
MSA_BM_CL_ESE_Aerotermia.Temp_Aspiracion_Refrigerante_Circ_1 | 192.168.4.25:5:0:00000000000B | AI:1:PRESENT-VALUE | Read | Always
MSA_BM_CL_ESE_Aerotermia.Temp_Liquida_Refrigerante_Circ_1 | 192.168.4.25:5:0:00000000000B | AI:2:PRESENT-VALUE | Read | Always
MSA_BM_CL_ESE_Aerotermia.Temp_Exterior | 192.168.4.25:5:0:00000000000B | AI:3:PRESENT-VALUE | Read | Always
MSA_BM_CL_ESE_Aerotermia.Temp_Aspiracion_Refrigerante_Circ_2 | 192.168.4.25:5:0:00000000000B | AI:4:PRESENT-VALUE | Read | Always
MSA_BM_CL_ESE_Aerotermia.Temp_Liquida_Refrigerante_Circ_2 | 192.168.4.25:5:0:00000000000B | AI:5:PRESENT-VALUE | Read | Always
MSA_BM_CL_ESE_Aerotermia.Temp_Descarga_Refrigerante_Circ_1 | 192.168.4.25:5:0:00000000000B | AI:6:PRESENT-VALUE | Read | Always
MSA_BM_CL_ESE_Aerotermia.Temp_Descarga_Refrigerante_Circ_2 | 192.168.4.25:5:0:00000000000B | AI:7:PRESENT-VALUE | Read | Always
MSA_BM_CL_ESE_Aerotermia.Temp_Retorno | 192.168.4.25:5:0:00000000000B | AI:16:PRESENT-VALUE | Read | Always
MSA_BM_CL_ESE_Aerotermia.Codigo_Alarma | 192.168.4.25:5:0:00000000000B | AI:31:PRESENT-VALUE | Read | Always
MSA_BM_CL_ESE_Aerotermia.Horas_Funcionamiento_Compresor_1 | 192.168.4.25:5:0:00000000000B | AI:19:PRESENT-VALUE | Read | Always
MSA_BM_CL_ESE_Aerotermia.Horas_Funcionamiento_Compresor_2 | 192.168.4.25:5:0:00000000000B | AI:20:PRESENT-VALUE | Read | Always
MSA_BM_CL_ESE_Aerotermia.Consigna_Temperatura_Frio | 192.168.4.25:5:0:00000000000B | AV:2:PRESENT-VALUE | Read+Write | Always
MSA_BM_CL_ESE_Aerotermia.Consigna_Temperatura_Calor | 192.168.4.25:5:0:00000000000B | AV:3:PRESENT-VALUE | Read+Write | Always
MSA_BM_CL_ESE_Aerotermia.Modo_Funcionamiento | 192.168.4.25:5:0:00000000000B | AV:8:PRESENT-VALUE | Read+Write | Always
MSA_BM_CL_ESE_Aerotermia.Reset_Alarma | 192.168.4.25:5:0:00000000000B | BV:2:PRESENT-VALUE | Read+Write | Always
MSA_BM_CL_MFZCA_Aerotermia.Temp_Aspiracion_Refrigerante_Circ_1 | 192.168.4.25:5:0:00000000000D | AI:1:PRESENT-VALUE | Read | Always
MSA_BM_CL_MFZCA_Aerotermia.Temp_Liquida_Refrigerante_Circ_1 | 192.168.4.25:5:0:00000000000D | AI:2:PRESENT-VALUE | Read | Always
MSA_BM_CL_MFZCA_Aerotermia.Temp_Exterior | 192.168.4.25:5:0:00000000000D | AI:3:PRESENT-VALUE | Read | Always
MSA_BM_CL_MFZCA_Aerotermia.Temp_Aspiracion_Refrigerante_Circ_2 | 192.168.4.25:5:0:00000000000D | AI:4:PRESENT-VALUE | Read | Always
MSA_BM_CL_MFZCA_Aerotermia.Temp_Liquida_Refrigerante_Circ_2 | 192.168.4.25:5:0:00000000000D | AI:5:PRESENT-VALUE | Read | Always
MSA_BM_CL_MFZCA_Aerotermia.Temp_Descarga_Refrigerante_Circ_1 | 192.168.4.25:5:0:00000000000D | AI:6:PRESENT-VALUE | Read | Always
MSA_BM_CL_MFZCA_Aerotermia.Temp_Descarga_Refrigerante_Circ_2 | 192.168.4.25:5:0:00000000000D | AI:7:PRESENT-VALUE | Read | Always
MSA_BM_CL_MFZCA_Aerotermia.Temp_Retorno | 192.168.4.25:5:0:00000000000D | AI:16:PRESENT-VALUE | Read | Always
MSA_BM_CL_MFZCA_Aerotermia.Codigo_Alarma | 192.168.4.25:5:0:00000000000D | AI:31:PRESENT-VALUE | Read | Always
MSA_BM_CL_MFZCA_Aerotermia.Horas_Funcionamiento_Compresor_1 | 192.168.4.25:5:0:00000000000D | AI:19:PRESENT-VALUE | Read | Always
MSA_BM_CL_MFZCA_Aerotermia.Horas_Funcionamiento_Compresor_2 | 192.168.4.25:5:0:00000000000D | AI:20:PRESENT-VALUE | Read | Always
MSA_BM_CL_MFZCA_Aerotermia.Consigna_Temperatura_Frio | 192.168.4.25:5:0:00000000000D | AV:2:PRESENT-VALUE | Read+Write | Always
MSA_BM_CL_MFZCA_Aerotermia.Consigna_Temperatura_Calor | 192.168.4.25:5:0:00000000000D | AV:3:PRESENT-VALUE | Read+Write | Always
MSA_BM_CL_MFZCA_Aerotermia.Modo_Funcionamiento | 192.168.4.25:5:0:00000000000D | AV:8:PRESENT-VALUE | Read+Write | Always
MSA_BM_CL_MFZCA_Aerotermia.Reset_Alarma | 192.168.4.25:5:0:00000000000D | BV:2:PRESENT-VALUE | Read+Write | Always
MSA_BM_CL_ESD_Aerotermia.Temp_Aspiracion_Refrigerante_Circ_1 | 192.168.4.25:5:0:00000000000E | AI:1:PRESENT-VALUE | Read | Always
MSA_BM_CL_ESD_Aerotermia.Temp_Liquida_Refrigerante_Circ_1 | 192.168.4.25:5:0:00000000000E | AI:2:PRESENT-VALUE | Read | Always
MSA_BM_CL_ESD_Aerotermia.Temp_Exterior | 192.168.4.25:5:0:00000000000E | AI:3:PRESENT-VALUE | Read | Always
MSA_BM_CL_ESD_Aerotermia.Temp_Aspiracion_Refrigerante_Circ_2 | 192.168.4.25:5:0:00000000000E | AI:4:PRESENT-VALUE | Read | Always
MSA_BM_CL_ESD_Aerotermia.Temp_Liquida_Refrigerante_Circ_2 | 192.168.4.25:5:0:00000000000E | AI:5:PRESENT-VALUE | Read | Always
MSA_BM_CL_ESD_Aerotermia.Temp_Descarga_Refrigerante_Circ_1 | 192.168.4.25:5:0:00000000000E | AI:6:PRESENT-VALUE | Read | Always
MSA_BM_CL_ESD_Aerotermia.Temp_Descarga_Refrigerante_Circ_2 | 192.168.4.25:5:0:00000000000E | AI:7:PRESENT-VALUE | Read | Always
MSA_BM_CL_ESD_Aerotermia.Temp_Retorno | 192.168.4.25:5:0:00000000000E | AI:16:PRESENT-VALUE | Read | Always
MSA_BM_CL_ESD_Aerotermia.Codigo_Alarma | 192.168.4.25:5:0:00000000000E | AI:31:PRESENT-VALUE | Read | Always
MSA_BM_CL_ESD_Aerotermia.Horas_Funcionamiento_Compresor_1 | 192.168.4.25:5:0:00000000000E | AI:19:PRESENT-VALUE | Read | Always
MSA_BM_CL_ESD_Aerotermia.Horas_Funcionamiento_Compresor_2 | 192.168.4.25:5:0:00000000000E | AI:20:PRESENT-VALUE | Read | Always
MSA_BM_CL_ESD_Aerotermia.Consigna_Temperatura_Frio | 192.168.4.25:5:0:00000000000E | AV:2:PRESENT-VALUE | Read+Write | Always
MSA_BM_CL_ESD_Aerotermia.Consigna_Temperatura_Calor | 192.168.4.25:5:0:00000000000E | AV:3:PRESENT-VALUE | Read+Write | Always
MSA_BM_CL_ESD_Aerotermia.Modo_Funcionamiento | 192.168.4.25:5:0:00000000000E | AV:8:PRESENT-VALUE | Read+Write | Always
MSA_BM_CL_ESD_Aerotermia.Reset_Alarma | 192.168.4.25:5:0:00000000000E | BV:2:PRESENT-VALUE | Read+Write | Always
MSA_UT_CL_ESE_Aerotermia.Temp_Aspiracion_Refrigerante_Circ_1 | 192.168.4.45:7:0:00000000001F | AI:1:PRESENT-VALUE | Read | Always
MSA_UT_CL_ESE_Aerotermia.Temp_Liquida_Refrigerante_Circ_1 | 192.168.4.45:7:0:00000000001F | AI:2:PRESENT-VALUE | Read | Always
MSA_UT_CL_ESE_Aerotermia.Temp_Exterior | 192.168.4.45:7:0:00000000001F | AI:3:PRESENT-VALUE | Read | Always
MSA_UT_CL_ESE_Aerotermia.Temp_Aspiracion_Refrigerante_Circ_2 | 192.168.4.45:7:0:00000000001F | AI:4:PRESENT-VALUE | Read | Always
MSA_UT_CL_ESE_Aerotermia.Temp_Liquida_Refrigerante_Circ_2 | 192.168.4.45:7:0:00000000001F | AI:5:PRESENT-VALUE | Read | Always
MSA_UT_CL_ESE_Aerotermia.Temp_Descarga_Refrigerante_Circ_1 | 192.168.4.45:7:0:00000000001F | AI:6:PRESENT-VALUE | Read | Always
MSA_UT_CL_ESE_Aerotermia.Temp_Descarga_Refrigerante_Circ_2 | 192.168.4.45:7:0:00000000001F | AI:7:PRESENT-VALUE | Read | Always
MSA_UT_CL_ESE_Aerotermia.Temp_Retorno | 192.168.4.45:7:0:00000000001F | AI:16:PRESENT-VALUE | Read | Always
MSA_UT_CL_ESE_Aerotermia.Codigo_Alarma | 192.168.4.45:7:0:00000000001F | AI:31:PRESENT-VALUE | Read | Always
MSA_UT_CL_ESE_Aerotermia.Horas_Funcionamiento_Compresor_1 | 192.168.4.45:7:0:00000000001F | AI:19:PRESENT-VALUE | Read | Always
MSA_UT_CL_ESE_Aerotermia.Horas_Funcionamiento_Compresor_2 | 192.168.4.45:7:0:00000000001F | AI:20:PRESENT-VALUE | Read | Always
MSA_UT_CL_ESE_Aerotermia.Consigna_Temperatura_Frio | 192.168.4.45:7:0:00000000001F | AV:2:PRESENT-VALUE | Read+Write | Always
MSA_UT_CL_ESE_Aerotermia.Consigna_Temperatura_Calor | 192.168.4.45:7:0:00000000001F | AV:3:PRESENT-VALUE | Read+Write | Always
MSA_UT_CL_ESE_Aerotermia.Modo_Funcionamiento | 192.168.4.45:7:0:00000000001F | AV:8:PRESENT-VALUE | Read+Write | Always
MSA_UT_CL_ESE_Aerotermia.Reset_Alarma | 192.168.4.45:7:0:00000000001F | BV:2:PRESENT-VALUE | Read+Write | Always
MSA_UT_CL_MFZCA_Aerotermia.Temp_Aspiracion_Refrigerante_Circ_1 | 192.168.4.45:7:0:000000000021 | AI:1:PRESENT-VALUE | Read | Always
MSA_UT_CL_MFZCA_Aerotermia.Temp_Liquida_Refrigerante_Circ_1 | 192.168.4.45:7:0:000000000021 | AI:2:PRESENT-VALUE | Read | Always
MSA_UT_CL_MFZCA_Aerotermia.Temp_Exterior | 192.168.4.45:7:0:000000000021 | AI:3:PRESENT-VALUE | Read | Always
MSA_UT_CL_MFZCA_Aerotermia.Temp_Aspiracion_Refrigerante_Circ_2 | 192.168.4.45:7:0:000000000021 | AI:4:PRESENT-VALUE | Read | Always
MSA_UT_CL_MFZCA_Aerotermia.Temp_Liquida_Refrigerante_Circ_2 | 192.168.4.45:7:0:000000000021 | AI:5:PRESENT-VALUE | Read | Always
MSA_UT_CL_MFZCA_Aerotermia.Temp_Descarga_Refrigerante_Circ_1 | 192.168.4.45:7:0:000000000021 | AI:6:PRESENT-VALUE | Read | Always
MSA_UT_CL_MFZCA_Aerotermia.Temp_Descarga_Refrigerante_Circ_2 | 192.168.4.45:7:0:000000000021 | AI:7:PRESENT-VALUE | Read | Always
MSA_UT_CL_MFZCA_Aerotermia.Temp_Retorno | 192.168.4.45:7:0:000000000021 | AI:16:PRESENT-VALUE | Read | Always
MSA_UT_CL_MFZCA_Aerotermia.Codigo_Alarma | 192.168.4.45:7:0:000000000021 | AI:31:PRESENT-VALUE | Read | Always
MSA_UT_CL_MFZCA_Aerotermia.Horas_Funcionamiento_Compresor_1 | 192.168.4.45:7:0:000000000021 | AI:19:PRESENT-VALUE | Read | Always
MSA_UT_CL_MFZCA_Aerotermia.Horas_Funcionamiento_Compresor_2 | 192.168.4.45:7:0:000000000021 | AI:20:PRESENT-VALUE | Read | Always
MSA_UT_CL_MFZCA_Aerotermia.Consigna_Temperatura_Frio | 192.168.4.45:7:0:000000000021 | AV:2:PRESENT-VALUE | Read+Write | Always
MSA_UT_CL_MFZCA_Aerotermia.Consigna_Temperatura_Calor | 192.168.4.45:7:0:000000000021 | AV:3:PRESENT-VALUE | Read+Write | Always
MSA_UT_CL_MFZCA_Aerotermia.Modo_Funcionamiento | 192.168.4.45:7:0:000000000021 | AV:8:PRESENT-VALUE | Read+Write | Always
MSA_UT_CL_MFZCA_Aerotermia.Reset_Alarma | 192.168.4.45:7:0:000000000021 | BV:2:PRESENT-VALUE | Read+Write | Always
MSA_UT_CL_ESD_Aerotermia.Temp_Aspiracion_Refrigerante_Circ_1 | 192.168.4.45:7:0:000000000022 | AI:1:PRESENT-VALUE | Read | Always
MSA_UT_CL_ESD_Aerotermia.Temp_Liquida_Refrigerante_Circ_1 | 192.168.4.45:7:0:000000000022 | AI:2:PRESENT-VALUE | Read | Always
MSA_UT_CL_ESD_Aerotermia.Temp_Exterior | 192.168.4.45:7:0:000000000022 | AI:3:PRESENT-VALUE | Read | Always
MSA_UT_CL_ESD_Aerotermia.Temp_Aspiracion_Refrigerante_Circ_2 | 192.168.4.45:7:0:000000000022 | AI:4:PRESENT-VALUE | Read | Always
MSA_UT_CL_ESD_Aerotermia.Temp_Liquida_Refrigerante_Circ_2 | 192.168.4.45:7:0:000000000022 | AI:5:PRESENT-VALUE | Read | Always
MSA_UT_CL_ESD_Aerotermia.Temp_Descarga_Refrigerante_Circ_1 | 192.168.4.45:7:0:000000000022 | AI:6:PRESENT-VALUE | Read | Always
MSA_UT_CL_ESD_Aerotermia.Temp_Descarga_Refrigerante_Circ_2 | 192.168.4.45:7:0:000000000022 | AI:7:PRESENT-VALUE | Read | Always
MSA_UT_CL_ESD_Aerotermia.Temp_Retorno | 192.168.4.45:7:0:000000000022 | AI:16:PRESENT-VALUE | Read | Always
MSA_UT_CL_ESD_Aerotermia.Codigo_Alarma | 192.168.4.45:7:0:000000000022 | AI:31:PRESENT-VALUE | Read | Always
MSA_UT_CL_ESD_Aerotermia.Horas_Funcionamiento_Compresor_1 | 192.168.4.45:7:0:000000000022 | AI:19:PRESENT-VALUE | Read | Always
MSA_UT_CL_ESD_Aerotermia.Horas_Funcionamiento_Compresor_2 | 192.168.4.45:7:0:000000000022 | AI:20:PRESENT-VALUE | Read | Always
MSA_UT_CL_ESD_Aerotermia.Consigna_Temperatura_Frio | 192.168.4.45:7:0:000000000022 | AV:2:PRESENT-VALUE | Read+Write | Always
MSA_UT_CL_ESD_Aerotermia.Consigna_Temperatura_Calor | 192.168.4.45:7:0:000000000022 | AV:3:PRESENT-VALUE | Read+Write | Always
MSA_UT_CL_ESD_Aerotermia.Modo_Funcionamiento | 192.168.4.45:7:0:000000000022 | AV:8:PRESENT-VALUE | Read+Write | Always
MSA_UT_CL_ESD_Aerotermia.Reset_Alarma | 192.168.4.45:7:0:000000000022 | BV:2:PRESENT-VALUE | Read+Write | Always
MSA_UM_CL_ESE_Aerotermia.Temp_Aspiracion_Refrigerante_Circ_1 | 192.168.4.55:8:0:000000000029 | AI:1:PRESENT-VALUE | Read | Always
MSA_UM_CL_ESE_Aerotermia.Temp_Liquida_Refrigerante_Circ_1 | 192.168.4.55:8:0:000000000029 | AI:2:PRESENT-VALUE | Read | Always
MSA_UM_CL_ESE_Aerotermia.Temp_Exterior | 192.168.4.55:8:0:000000000029 | AI:3:PRESENT-VALUE | Read | Always
MSA_UM_CL_ESE_Aerotermia.Temp_Aspiracion_Refrigerante_Circ_2 | 192.168.4.55:8:0:000000000029 | AI:4:PRESENT-VALUE | Read | Always
MSA_UM_CL_ESE_Aerotermia.Temp_Liquida_Refrigerante_Circ_2 | 192.168.4.55:8:0:000000000029 | AI:5:PRESENT-VALUE | Read | Always
MSA_UM_CL_ESE_Aerotermia.Temp_Descarga_Refrigerante_Circ_1 | 192.168.4.55:8:0:000000000029 | AI:6:PRESENT-VALUE | Read | Always
MSA_UM_CL_ESE_Aerotermia.Temp_Descarga_Refrigerante_Circ_2 | 192.168.4.55:8:0:000000000029 | AI:7:PRESENT-VALUE | Read | Always
MSA_UM_CL_ESE_Aerotermia.Temp_Retorno | 192.168.4.55:8:0:000000000029 | AI:16:PRESENT-VALUE | Read | Always
MSA_UM_CL_ESE_Aerotermia.Codigo_Alarma | 192.168.4.55:8:0:000000000029 | AI:31:PRESENT-VALUE | Read | Always
MSA_UM_CL_ESE_Aerotermia.Horas_Funcionamiento_Compresor_1 | 192.168.4.55:8:0:000000000029 | AI:19:PRESENT-VALUE | Read | Always
MSA_UM_CL_ESE_Aerotermia.Horas_Funcionamiento_Compresor_2 | 192.168.4.55:8:0:000000000029 | AI:20:PRESENT-VALUE | Read | Always
MSA_UM_CL_ESE_Aerotermia.Consigna_Temperatura_Frio | 192.168.4.55:8:0:000000000029 | AV:2:PRESENT-VALUE | Read+Write | Always
MSA_UM_CL_ESE_Aerotermia.Consigna_Temperatura_Calor | 192.168.4.55:8:0:000000000029 | AV:3:PRESENT-VALUE | Read+Write | Always
MSA_UM_CL_ESE_Aerotermia.Modo_Funcionamiento | 192.168.4.55:8:0:000000000029 | AV:8:PRESENT-VALUE | Read+Write | Always
MSA_UM_CL_ESE_Aerotermia.Reset_Alarma | 192.168.4.55:8:0:000000000029 | BV:2:PRESENT-VALUE | Read+Write | Always
MSA_UM_CL_MFZCA_Aerotermia.Temp_Aspiracion_Refrigerante_Circ_1 | 192.168.4.55:8:0:00000000002B | AI:1:PRESENT-VALUE | Read | Always
MSA_UM_CL_MFZCA_Aerotermia.Temp_Liquida_Refrigerante_Circ_1 | 192.168.4.55:8:0:00000000002B | AI:2:PRESENT-VALUE | Read | Always
MSA_UM_CL_MFZCA_Aerotermia.Temp_Exterior | 192.168.4.55:8:0:00000000002B | AI:3:PRESENT-VALUE | Read | Always
MSA_UM_CL_MFZCA_Aerotermia.Temp_Aspiracion_Refrigerante_Circ_2 | 192.168.4.55:8:0:00000000002B | AI:4:PRESENT-VALUE | Read | Always
MSA_UM_CL_MFZCA_Aerotermia.Temp_Liquida_Refrigerante_Circ_2 | 192.168.4.55:8:0:00000000002B | AI:5:PRESENT-VALUE | Read | Always
MSA_UM_CL_MFZCA_Aerotermia.Temp_Descarga_Refrigerante_Circ_1 | 192.168.4.55:8:0:00000000002B | AI:6:PRESENT-VALUE | Read | Always
MSA_UM_CL_MFZCA_Aerotermia.Temp_Descarga_Refrigerante_Circ_2 | 192.168.4.55:8:0:00000000002B | AI:7:PRESENT-VALUE | Read | Always
MSA_UM_CL_MFZCA_Aerotermia.Temp_Retorno | 192.168.4.55:8:0:00000000002B | AI:16:PRESENT-VALUE | Read | Always
MSA_UM_CL_MFZCA_Aerotermia.Codigo_Alarma | 192.168.4.55:8:0:00000000002B | AI:31:PRESENT-VALUE | Read | Always
MSA_UM_CL_MFZCA_Aerotermia.Horas_Funcionamiento_Compresor_1 | 192.168.4.55:8:0:00000000002B | AI:19:PRESENT-VALUE | Read | Always
MSA_UM_CL_MFZCA_Aerotermia.Horas_Funcionamiento_Compresor_2 | 192.168.4.55:8:0:00000000002B | AI:20:PRESENT-VALUE | Read | Always
MSA_UM_CL_MFZCA_Aerotermia.Consigna_Temperatura_Frio | 192.168.4.55:8:0:00000000002B | AV:2:PRESENT-VALUE | Read+Write | Always
MSA_UM_CL_MFZCA_Aerotermia.Consigna_Temperatura_Calor | 192.168.4.55:8:0:00000000002B | AV:3:PRESENT-VALUE | Read+Write | Always
MSA_UM_CL_MFZCA_Aerotermia.Modo_Funcionamiento | 192.168.4.55:8:0:00000000002B | AV:8:PRESENT-VALUE | Read+Write | Always
MSA_UM_CL_MFZCA_Aerotermia.Reset_Alarma | 192.168.4.55:8:0:00000000002B | BV:2:PRESENT-VALUE | Read+Write | Always
MSA_UM_CL_ESD_Aerotermia.Temp_Aspiracion_Refrigerante_Circ_1 | 192.168.4.55:8:0:00000000002C | AI:1:PRESENT-VALUE | Read | Always
MSA_UM_CL_ESD_Aerotermia.Temp_Liquida_Refrigerante_Circ_1 | 192.168.4.55:8:0:00000000002C | AI:2:PRESENT-VALUE | Read | Always
MSA_UM_CL_ESD_Aerotermia.Temp_Exterior | 192.168.4.55:8:0:00000000002C | AI:3:PRESENT-VALUE | Read | Always
MSA_UM_CL_ESD_Aerotermia.Temp_Aspiracion_Refrigerante_Circ_2 | 192.168.4.55:8:0:00000000002C | AI:4:PRESENT-VALUE | Read | Always
MSA_UM_CL_ESD_Aerotermia.Temp_Liquida_Refrigerante_Circ_2 | 192.168.4.55:8:0:00000000002C | AI:5:PRESENT-VALUE | Read | Always
MSA_UM_CL_ESD_Aerotermia.Temp_Descarga_Refrigerante_Circ_1 | 192.168.4.55:8:0:00000000002C | AI:6:PRESENT-VALUE | Read | Always
MSA_UM_CL_ESD_Aerotermia.Temp_Descarga_Refrigerante_Circ_2 | 192.168.4.55:8:0:00000000002C | AI:7:PRESENT-VALUE | Read | Always
MSA_UM_CL_ESD_Aerotermia.Temp_Retorno | 192.168.4.55:8:0:00000000002C | AI:16:PRESENT-VALUE | Read | Always
MSA_UM_CL_ESD_Aerotermia.Codigo_Alarma | 192.168.4.55:8:0:00000000002C | AI:31:PRESENT-VALUE | Read | Always
MSA_UM_CL_ESD_Aerotermia.Horas_Funcionamiento_Compresor_1 | 192.168.4.55:8:0:00000000002C | AI:19:PRESENT-VALUE | Read | Always
MSA_UM_CL_ESD_Aerotermia.Horas_Funcionamiento_Compresor_2 | 192.168.4.55:8:0:00000000002C | AI:20:PRESENT-VALUE | Read | Always
MSA_UM_CL_ESD_Aerotermia.Consigna_Temperatura_Frio | 192.168.4.55:8:0:00000000002C | AV:2:PRESENT-VALUE | Read+Write | Always
MSA_UM_CL_ESD_Aerotermia.Consigna_Temperatura_Calor | 192.168.4.55:8:0:00000000002C | AV:3:PRESENT-VALUE | Read+Write | Always
MSA_UM_CL_ESD_Aerotermia.Modo_Funcionamiento | 192.168.4.55:8:0:00000000002C | AV:8:PRESENT-VALUE | Read+Write | Always
MSA_UM_CL_ESD_Aerotermia.Reset_Alarma | 192.168.4.55:8:0:00000000002C | BV:2:PRESENT-VALUE | Read+Write | Always
MSA_UT_Adiabatico_Aerotermia.Temp_Aspiracion_Refrigerante_Circ_1 | 192.168.4.45:7:0:000000000023 | AI:1:PRESENT-VALUE | Read | Always
MSA_UT_Adiabatico_Aerotermia.Temp_Liquida_Refrigerante_Circ_1 | 192.168.4.45:7:0:000000000023 | AI:2:PRESENT-VALUE | Read | Always
MSA_UT_Adiabatico_Aerotermia.Temp_Exterior | 192.168.4.45:7:0:000000000023 | AI:3:PRESENT-VALUE | Read | Always
MSA_UT_Adiabatico_Aerotermia.Temp_Aspiracion_Refrigerante_Circ_2 | 192.168.4.45:7:0:000000000023 | AI:4:PRESENT-VALUE | Read | Always
MSA_UT_Adiabatico_Aerotermia.Temp_Liquida_Refrigerante_Circ_2 | 192.168.4.45:7:0:000000000023 | AI:5:PRESENT-VALUE | Read | Always
MSA_UT_Adiabatico_Aerotermia.Temp_Descarga_Refrigerante_Circ_1 | 192.168.4.45:7:0:000000000023 | AI:6:PRESENT-VALUE | Read | Always
MSA_UT_Adiabatico_Aerotermia.Temp_Descarga_Refrigerante_Circ_2 | 192.168.4.45:7:0:000000000023 | AI:7:PRESENT-VALUE | Read | Always
MSA_UT_Adiabatico_Aerotermia.Temp_Retorno | 192.168.4.45:7:0:000000000023 | AI:16:PRESENT-VALUE | Read | Always
MSA_UT_Adiabatico_Aerotermia.Codigo_Alarma | 192.168.4.45:7:0:000000000023 | AI:31:PRESENT-VALUE | Read | Always
MSA_UT_Adiabatico_Aerotermia.Horas_Funcionamiento_Compresor_1 | 192.168.4.45:7:0:000000000023 | AI:19:PRESENT-VALUE | Read | Always
MSA_UT_Adiabatico_Aerotermia.Horas_Funcionamiento_Compresor_2 | 192.168.4.45:7:0:000000000023 | AI:20:PRESENT-VALUE | Read | Always
MSA_UT_Adiabatico_Aerotermia.Consigna_Temperatura_Frio | 192.168.4.45:7:0:000000000023 | AV:2:PRESENT-VALUE | Read+Write | Always
MSA_UT_Adiabatico_Aerotermia.Consigna_Temperatura_Calor | 192.168.4.45:7:0:000000000023 | AV:3:PRESENT-VALUE | Read+Write | Always
MSA_UT_Adiabatico_Aerotermia.Modo_Funcionamiento | 192.168.4.45:7:0:000000000023 | AV:8:PRESENT-VALUE | Read+Write | Always
MSA_UT_Adiabatico_Aerotermia.Reset_Alarma | 192.168.4.45:7:0:000000000023 | BV:2:PRESENT-VALUE | Read+Write | Always
MSA_BM_CL_ESE_Aerotermia.Status | 192.168.4.25:5:0:00000000000B | BV:3:PRESENT-VALUE | Read | Always
MSA_BM_CL_MFZCA_Aerotermia.Status | 192.168.4.25:5:0:00000000000D | BV:3:PRESENT-VALUE | Read | Always
MSA_BM_CL_ESD_Aerotermia.Status | 192.168.4.25:5:0:00000000000E | BV:3:PRESENT-VALUE | Read | Always
MSA_BT_CL_ESE_Aerotermia.Status | 192.168.4.35:6:0:000000000015 | BV:3:PRESENT-VALUE | Read | Always
MSA_BT_CL_MFZCA_Aerotermia.Status | 192.168.4.35:6:0:000000000017 | BV:3:PRESENT-VALUE | Read | Always
MSA_BT_CL_ESD_Aerotermia.Status | 192.168.4.35:6:0:000000000018 | BV:3:PRESENT-VALUE | Read | Always
MSA_UT_CL_ESE_Aerotermia.Status | 192.168.4.45:7:0:00000000001F | BV:3:PRESENT-VALUE | Read | Always
MSA_UT_CL_MFZCA_Aerotermia.Status | 192.168.4.45:7:0:000000000021 | BV:3:PRESENT-VALUE | Read | Always
MSA_UT_CL_ESD_Aerotermia.Status | 192.168.4.45:7:0:000000000022 | BV:3:PRESENT-VALUE | Read | Always
MSA_UM_CL_ESE_Aerotermia.Status | 192.168.4.55:8:0:000000000029 | BV:3:PRESENT-VALUE | Read | Always
MSA_UM_CL_MFZCA_Aerotermia.Status | 192.168.4.55:8:0:00000000002B | BV:3:PRESENT-VALUE | Read | Always
MSA_UM_CL_ESD_Aerotermia.Status | 192.168.4.55:8:0:00000000002C | BV:3:PRESENT-VALUE | Read | Always
MSA_UT_Adiabatico_Aerotermia.Status | 192.168.4.45:7:0:000000000023 | BV:3:PRESENT-VALUE | Read | Always

## MODBUS
|  |  | (All) | (All)
MSA_BM_01_Pila_Mal | 192.168.4.23:4660 | 1:0X:200 | Read+Write | Always
MSA_BM_01_Alarma_incendio | 192.168.4.23:4660 | 1:0X:199 | Read+Write | Always
MSA_BM_01_leer_seg | 192.168.4.23:4660 | 1:4X:7 | Read+Write | Always
MSA_BM_01_leer_min | 192.168.4.23:4660 | 1:4X:8 | Read+Write | Always
MSA_BM_01_leer_hora | 192.168.4.23:4660 | 1:4X:9 | Read+Write | Always
MSA_BM_01_leer_dia | 192.168.4.23:4660 | 1:4X:10 | Read+Write | Always
MSA_BM_01_leer_mes | 192.168.4.23:4660 | 1:4X:11 | Read+Write | Always
MSA_BM_01_leer_anno | 192.168.4.23:4660 | 1:4X:12 | Read+Write | Always
MSA_BM_02_Pila_Mal | 192.168.4.23:4660 | 2:0X:200 | Read+Write | Always
MSA_BM_02_Alarma_incendio | 192.168.4.23:4660 | 2:0X:199 | Read+Write | Always
MSA_BM_02_leer_seg | 192.168.4.23:4660 | 2:4X:7 | Read+Write | Always
MSA_BM_02_leer_min | 192.168.4.23:4660 | 2:4X:8 | Read+Write | Always
MSA_BM_02_leer_hora | 192.168.4.23:4660 | 2:4X:9 | Read+Write | Always
MSA_BM_02_leer_dia | 192.168.4.23:4660 | 2:4X:10 | Read+Write | Always
MSA_BM_02_leer_mes | 192.168.4.23:4660 | 2:4X:11 | Read+Write | Always
MSA_BM_02_leer_anno | 192.168.4.23:4660 | 2:4X:12 | Read+Write | Always
MSA_BM_03_Pila_Mal | 192.168.4.23:4660 | 3:0X:200 | Read+Write | Always
MSA_BM_03_Alarma_incendio | 192.168.4.23:4660 | 3:0X:199 | Read+Write | Always
MSA_BM_03_leer_seg | 192.168.4.23:4660 | 3:4X:7 | Read+Write | Always
MSA_BM_03_leer_min | 192.168.4.23:4660 | 3:4X:8 | Read+Write | Always
MSA_BM_03_leer_hora | 192.168.4.23:4660 | 3:4X:9 | Read+Write | Always
MSA_BM_03_leer_dia | 192.168.4.23:4660 | 3:4X:10 | Read+Write | Always
MSA_BM_03_leer_mes | 192.168.4.23:4660 | 3:4X:11 | Read+Write | Always
MSA_BM_03_leer_anno | 192.168.4.23:4660 | 3:4X:12 | Read+Write | Always
MSA_BM_04_Pila_Mal | 192.168.4.23:4660 | 4:0X:200 | Read+Write | Always
MSA_BM_04_Alarma_incendio | 192.168.4.23:4660 | 4:0X:199 | Read+Write | Always
MSA_BM_04_leer_seg | 192.168.4.23:4660 | 4:4X:7 | Read+Write | Always
MSA_BM_04_leer_min | 192.168.4.23:4660 | 4:4X:8 | Read+Write | Always
MSA_BM_04_leer_hora | 192.168.4.23:4660 | 4:4X:9 | Read+Write | Always
MSA_BM_04_leer_dia | 192.168.4.23:4660 | 4:4X:10 | Read+Write | Always
MSA_BM_04_leer_mes | 192.168.4.23:4660 | 4:4X:11 | Read+Write | Always
MSA_BM_04_leer_anno | 192.168.4.23:4660 | 4:4X:12 | Read+Write | Always
MSA_BM_05_Pila_Mal | 192.168.4.23:4660 | 5:0X:200 | Read+Write | Always
MSA_BM_05_Alarma_incendio | 192.168.4.23:4660 | 5:0X:199 | Read+Write | Always
MSA_BM_05_leer_seg | 192.168.4.23:4660 | 5:4X:7 | Read+Write | Always
MSA_BM_05_leer_min | 192.168.4.23:4660 | 5:4X:8 | Read+Write | Always
MSA_BM_05_leer_hora | 192.168.4.23:4660 | 5:4X:9 | Read+Write | Always
MSA_BM_05_leer_dia | 192.168.4.23:4660 | 5:4X:10 | Read+Write | Always
MSA_BM_05_leer_mes | 192.168.4.23:4660 | 5:4X:11 | Read+Write | Always
MSA_BM_05_leer_anno | 192.168.4.23:4660 | 5:4X:12 | Read+Write | Always
MSA_BM_06_Pila_Mal | 192.168.4.23:4660 | 6:0X:200 | Read+Write | Always
MSA_BM_06_Alarma_incendio | 192.168.4.23:4660 | 6:0X:199 | Read+Write | Always
MSA_BM_06_leer_seg | 192.168.4.23:4660 | 6:4X:7 | Read+Write | Always
MSA_BM_06_leer_min | 192.168.4.23:4660 | 6:4X:8 | Read+Write | Always
MSA_BM_06_leer_hora | 192.168.4.23:4660 | 6:4X:9 | Read+Write | Always
MSA_BM_06_leer_dia | 192.168.4.23:4660 | 6:4X:10 | Read+Write | Always
MSA_BM_06_leer_mes | 192.168.4.23:4660 | 6:4X:11 | Read+Write | Always
MSA_BM_06_leer_anno | 192.168.4.23:4660 | 6:4X:12 | Read+Write | Always
MSA_BT_Ventil_desenfumaje_VPS_1_03.Manual_horario | 192.168.4.33:4660 | 7:0X:386 | Read+Write | Screen
MSA_BT_Ventil_desenfumaje_VPS_1_02.Marcha_paro | 192.168.4.33:4660 | 7:0X:354 | Read+Write | Screen
MSA_BT_Ventil_desenfumaje_VPS_1_02.Estado | 192.168.4.33:4660 | 7:0X:217 | Read | Screen
MSA_BT_Ventil_desenfumaje_VPS_1_02.Orden | 192.168.4.33:4660 | 7:0X:273 | Read | Screen
MSA_BT_Ventil_desenfumaje_VPS_1_02.Fallo | 192.168.4.33:4660 | 7:0X:355 | Read | Screen
MSA_BT_Ventil_desenfumaje_VPS_1_03.Marcha_paro | 192.168.4.33:4660 | 7:0X:356 | Read+Write | Screen
MSA_BT_Ventil_desenfumaje_VPS_1_03.Estado | 192.168.4.33:4660 | 7:0X:218 | Read | Screen
MSA_BT_Ventil_desenfumaje_VPS_1_03.Orden | 192.168.4.33:4660 | 7:0X:274 | Read | Screen
MSA_BT_Ventil_desenfumaje_VPS_1_03.Fallo | 192.168.4.33:4660 | 7:0X:357 | Read | Screen
MSA_BM_08_Alarma_incendio | 192.168.4.23:4660 | 8:0X:199 | Read+Write | Always
MSA_BM_08_leer_seg | 192.168.4.23:4660 | 8:4X:7 | Read+Write | Always
MSA_BM_08_leer_min | 192.168.4.23:4660 | 8:4X:8 | Read+Write | Always
MSA_BM_08_leer_hora | 192.168.4.23:4660 | 8:4X:9 | Read+Write | Always
MSA_BM_08_leer_dia | 192.168.4.23:4660 | 8:4X:10 | Read+Write | Always
MSA_BM_08_leer_mes | 192.168.4.23:4660 | 8:4X:11 | Read+Write | Always
MSA_BM_08_leer_anno | 192.168.4.23:4660 | 8:4X:12 | Read+Write | Always
MSA_BM_09_Pila_Mal | 192.168.4.23:4660 | 9:0X:200 | Read+Write | Always
MSA_BM_09_Alarma_incendio | 192.168.4.23:4660 | 9:0X:199 | Read+Write | Always
MSA_BM_09_leer_seg | 192.168.4.23:4660 | 9:4X:7 | Read+Write | Always
MSA_BM_09_leer_min | 192.168.4.23:4660 | 9:4X:8 | Read+Write | Always
MSA_BM_09_leer_hora | 192.168.4.23:4660 | 9:4X:9 | Read+Write | Always
MSA_BM_09_leer_dia | 192.168.4.23:4660 | 9:4X:10 | Read+Write | Always
MSA_BM_09_leer_mes | 192.168.4.23:4660 | 9:4X:11 | Read+Write | Always
MSA_BM_09_leer_anno | 192.168.4.23:4660 | 9:4X:12 | Read+Write | Always
MSA_BM_10_Pila_Mal | 192.168.4.23:4660 | 10:0X:200 | Read+Write | Always
MSA_BM_10_Alarma_incendio | 192.168.4.23:4660 | 10:0X:199 | Read+Write | Always
MSA_BM_10_leer_seg | 192.168.4.23:4660 | 10:4X:7 | Read+Write | Always
MSA_BM_10_leer_min | 192.168.4.23:4660 | 10:4X:8 | Read+Write | Always
MSA_BM_10_leer_hora | 192.168.4.23:4660 | 10:4X:9 | Read+Write | Always
MSA_BM_10_leer_dia | 192.168.4.23:4660 | 10:4X:10 | Read+Write | Always
MSA_BM_10_leer_mes | 192.168.4.23:4660 | 10:4X:11 | Read+Write | Always
MSA_BM_10_leer_anno | 192.168.4.23:4660 | 10:4X:12 | Read+Write | Always
MSA_BT_01_Pila_Mal | 192.168.4.33:4660 | 1:0X:200 | Read+Write | Always
MSA_BT_01_Alarma_incendio | 192.168.4.33:4660 | 1:0X:199 | Read+Write | Always
MSA_BT_01_leer_seg | 192.168.4.33:4660 | 1:4X:7 | Read+Write | Always
MSA_BT_01_leer_min | 192.168.4.33:4660 | 1:4X:8 | Read+Write | Always
MSA_BT_01_leer_hora | 192.168.4.33:4660 | 1:4X:9 | Read+Write | Always
MSA_BT_01_leer_dia | 192.168.4.33:4660 | 1:4X:10 | Read+Write | Always
MSA_BT_01_leer_mes | 192.168.4.33:4660 | 1:4X:11 | Read+Write | Always
MSA_BT_01_leer_anno | 192.168.4.33:4660 | 1:4X:12 | Read+Write | Always
MSA_BT_02_Pila_Mal | 192.168.4.33:4660 | 2:0X:200 | Read+Write | Always
MSA_BT_02_Alarma_incendio | 192.168.4.33:4660 | 2:0X:199 | Read+Write | Always
MSA_BT_02_leer_seg | 192.168.4.33:4660 | 2:4X:7 | Read+Write | Always
MSA_BT_02_leer_min | 192.168.4.33:4660 | 2:4X:8 | Read+Write | Always
MSA_BT_02_leer_hora | 192.168.4.33:4660 | 2:4X:9 | Read+Write | Always
MSA_BT_02_leer_dia | 192.168.4.33:4660 | 2:4X:10 | Read+Write | Always
MSA_BT_02_leer_mes | 192.168.4.33:4660 | 2:4X:11 | Read+Write | Always
MSA_BT_02_leer_anno | 192.168.4.33:4660 | 2:4X:12 | Read+Write | Always
MSA_BT_03_Pila_Mal | 192.168.4.33:4660 | 3:0X:200 | Read+Write | Always
MSA_BT_03_Alarma_incendio | 192.168.4.33:4660 | 3:0X:199 | Read+Write | Always
MSA_BT_03_leer_seg | 192.168.4.33:4660 | 3:4X:7 | Read+Write | Always
MSA_BT_03_leer_min | 192.168.4.33:4660 | 3:4X:8 | Read+Write | Always
MSA_BT_03_leer_hora | 192.168.4.33:4660 | 3:4X:9 | Read+Write | Always
MSA_BT_03_leer_dia | 192.168.4.33:4660 | 3:4X:10 | Read+Write | Always
MSA_BT_03_leer_mes | 192.168.4.33:4660 | 3:4X:11 | Read+Write | Always
MSA_BT_03_leer_anno | 192.168.4.33:4660 | 3:4X:12 | Read+Write | Always
MSA_BT_04_Pila_Mal | 192.168.4.33:4660 | 4:0X:200 | Read+Write | Always
MSA_BT_04_Alarma_incendio | 192.168.4.33:4660 | 4:0X:199 | Read+Write | Always
MSA_BT_04_leer_seg | 192.168.4.33:4660 | 4:4X:7 | Read+Write | Always
MSA_BT_04_leer_min | 192.168.4.33:4660 | 4:4X:8 | Read+Write | Always
MSA_BT_04_leer_hora | 192.168.4.33:4660 | 4:4X:9 | Read+Write | Always
MSA_BT_04_leer_dia | 192.168.4.33:4660 | 4:4X:10 | Read+Write | Always
MSA_BT_04_leer_mes | 192.168.4.33:4660 | 4:4X:11 | Read+Write | Always
MSA_BT_04_leer_anno | 192.168.4.33:4660 | 4:4X:12 | Read+Write | Always
MSA_BT_05_Pila_Mal | 192.168.4.33:4660 | 5:0X:200 | Read+Write | Always
MSA_BT_05_Alarma_incendio | 192.168.4.33:4660 | 5:0X:199 | Read+Write | Always
MSA_BT_05_leer_seg | 192.168.4.33:4660 | 5:4X:7 | Read+Write | Always
MSA_BT_05_leer_min | 192.168.4.33:4660 | 5:4X:8 | Read+Write | Always
MSA_BT_05_leer_hora | 192.168.4.33:4660 | 5:4X:9 | Read+Write | Always
MSA_BT_05_leer_dia | 192.168.4.33:4660 | 5:4X:10 | Read+Write | Always
MSA_BT_05_leer_mes | 192.168.4.33:4660 | 5:4X:11 | Read+Write | Always
MSA_BT_05_leer_anno | 192.168.4.33:4660 | 5:4X:12 | Read+Write | Always
MSA_BT_06_Pila_Mal | 192.168.4.33:4660 | 6:0X:200 | Read+Write | Always
MSA_BT_06_Alarma_incendio | 192.168.4.33:4660 | 6:0X:199 | Read+Write | Always
MSA_BT_06_leer_seg | 192.168.4.33:4660 | 6:4X:7 | Read+Write | Always
MSA_BT_06_leer_min | 192.168.4.33:4660 | 6:4X:8 | Read+Write | Always
MSA_BT_06_leer_hora | 192.168.4.33:4660 | 6:4X:9 | Read+Write | Always
MSA_BT_06_leer_dia | 192.168.4.33:4660 | 6:4X:10 | Read+Write | Always
MSA_BT_06_leer_mes | 192.168.4.33:4660 | 6:4X:11 | Read+Write | Always
MSA_BT_06_leer_anno | 192.168.4.33:4660 | 6:4X:12 | Read+Write | Always
MSA_BT_07_Pila_Mal | 192.168.4.33:4660 | 7:0X:200 | Read+Write | Always
MSA_BT_07_Alarma_incendio | 192.168.4.33:4660 | 7:0X:199 | Read+Write | Always
MSA_BT_07_leer_seg | 192.168.4.33:4660 | 7:4X:7 | Read+Write | Always
MSA_BT_07_leer_min | 192.168.4.33:4660 | 7:4X:8 | Read+Write | Always
MSA_BT_07_leer_hora | 192.168.4.33:4660 | 7:4X:9 | Read+Write | Always
MSA_BT_07_leer_dia | 192.168.4.33:4660 | 7:4X:10 | Read+Write | Always
MSA_BT_07_leer_mes | 192.168.4.33:4660 | 7:4X:11 | Read+Write | Always
MSA_BT_07_leer_anno | 192.168.4.33:4660 | 7:4X:12 | Read+Write | Always
MSA_BT_08_Pila_Mal | 192.168.4.33:4660 | 8:0X:200 | Read+Write | Always
MSA_BT_08_Alarma_incendio | 192.168.4.33:4660 | 8:0X:199 | Read+Write | Always
MSA_BT_08_leer_seg | 192.168.4.33:4660 | 8:4X:7 | Read+Write | Always
MSA_BT_08_leer_min | 192.168.4.33:4660 | 8:4X:8 | Read+Write | Always
MSA_BT_08_leer_hora | 192.168.4.33:4660 | 8:4X:9 | Read+Write | Always
MSA_BT_08_leer_dia | 192.168.4.33:4660 | 8:4X:10 | Read+Write | Always
MSA_BT_08_leer_mes | 192.168.4.33:4660 | 8:4X:11 | Read+Write | Always
MSA_BT_08_leer_anno | 192.168.4.33:4660 | 8:4X:12 | Read+Write | Always
MSA_BT_09_Pila_Mal | 192.168.4.33:4660 | 9:0X:200 | Read+Write | Always
MSA_BT_09_Alarma_incendio | 192.168.4.33:4660 | 9:0X:199 | Read+Write | Always
MSA_BT_09_leer_seg | 192.168.4.33:4660 | 9:4X:7 | Read+Write | Always
MSA_BT_09_leer_min | 192.168.4.33:4660 | 9:4X:8 | Read+Write | Always
MSA_BT_09_leer_hora | 192.168.4.33:4660 | 9:4X:9 | Read+Write | Always
MSA_BT_09_leer_dia | 192.168.4.33:4660 | 9:4X:10 | Read+Write | Always
MSA_BT_09_leer_mes | 192.168.4.33:4660 | 9:4X:11 | Read+Write | Always
MSA_BT_09_leer_anno | 192.168.4.33:4660 | 9:4X:12 | Read+Write | Always
MSA_BT_10_Pila_Mal | 192.168.4.33:4660 | 10:0X:200 | Read+Write | Always
MSA_BT_10_Alarma_incendio | 192.168.4.33:4660 | 10:0X:199 | Read+Write | Always
MSA_BT_10_leer_seg | 192.168.4.33:4660 | 10:4X:7 | Read+Write | Always
MSA_BT_10_leer_min | 192.168.4.33:4660 | 10:4X:8 | Read+Write | Always
MSA_BT_10_leer_hora | 192.168.4.33:4660 | 10:4X:9 | Read+Write | Always
MSA_BT_10_leer_dia | 192.168.4.33:4660 | 10:4X:10 | Read+Write | Always
MSA_BT_10_leer_mes | 192.168.4.33:4660 | 10:4X:11 | Read+Write | Always
MSA_BT_10_leer_anno | 192.168.4.33:4660 | 10:4X:12 | Read+Write | Always
MSA_UT_01_Pila_Mal | 192.168.4.43:4660 | 1:0X:200 | Read+Write | Always
MSA_UT_01_Alarma_incendio | 192.168.4.43:4660 | 1:0X:199 | Read+Write | Always
MSA_UT_01_leer_seg | 192.168.4.43:4660 | 1:4X:7 | Read+Write | Always
MSA_UT_01_leer_min | 192.168.4.43:4660 | 1:4X:8 | Read+Write | Always
MSA_UT_01_leer_hora | 192.168.4.43:4660 | 1:4X:9 | Read+Write | Always
MSA_UT_01_leer_dia | 192.168.4.43:4660 | 1:4X:10 | Read+Write | Always
MSA_UT_01_leer_mes | 192.168.4.43:4660 | 1:4X:11 | Read+Write | Always
MSA_UT_01_leer_anno | 192.168.4.43:4660 | 1:4X:12 | Read+Write | Always
MSA_UT_02_Pila_Mal | 192.168.4.43:4660 | 2:0X:200 | Read+Write | Always
MSA_UT_02_Alarma_incendio | 192.168.4.43:4660 | 2:0X:199 | Read+Write | Always
MSA_UT_02_leer_seg | 192.168.4.43:4660 | 2:4X:7 | Read+Write | Always
MSA_UT_02_leer_min | 192.168.4.43:4660 | 2:4X:8 | Read+Write | Always
MSA_UT_02_leer_hora | 192.168.4.43:4660 | 2:4X:9 | Read+Write | Always
MSA_UT_02_leer_dia | 192.168.4.43:4660 | 2:4X:10 | Read+Write | Always
MSA_UT_02_leer_mes | 192.168.4.43:4660 | 2:4X:11 | Read+Write | Always
MSA_UT_02_leer_anno | 192.168.4.43:4660 | 2:4X:12 | Read+Write | Always
MSA_UT_03_Pila_Mal | 192.168.4.43:4660 | 3:0X:200 | Read+Write | Always
MSA_UT_03_Alarma_incendio | 192.168.4.43:4660 | 3:0X:199 | Read+Write | Always
MSA_UT_03_leer_seg | 192.168.4.43:4660 | 3:4X:7 | Read+Write | Always
MSA_UT_03_leer_min | 192.168.4.43:4660 | 3:4X:8 | Read+Write | Always
MSA_UT_03_leer_hora | 192.168.4.43:4660 | 3:4X:9 | Read+Write | Always
MSA_UT_03_leer_dia | 192.168.4.43:4660 | 3:4X:10 | Read+Write | Always
MSA_UT_03_leer_mes | 192.168.4.43:4660 | 3:4X:11 | Read+Write | Always
MSA_UT_03_leer_anno | 192.168.4.43:4660 | 3:4X:12 | Read+Write | Always
MSA_UT_04_Pila_Mal | 192.168.4.43:4660 | 4:0X:200 | Read+Write | Always
MSA_UT_04_Alarma_incendio | 192.168.4.43:4660 | 4:0X:199 | Read+Write | Always
MSA_UT_04_leer_seg | 192.168.4.43:4660 | 4:4X:7 | Read+Write | Always
MSA_UT_04_leer_min | 192.168.4.43:4660 | 4:4X:8 | Read+Write | Always
MSA_UT_04_leer_hora | 192.168.4.43:4660 | 4:4X:9 | Read+Write | Always
MSA_UT_04_leer_dia | 192.168.4.43:4660 | 4:4X:10 | Read+Write | Always
MSA_UT_04_leer_mes | 192.168.4.43:4660 | 4:4X:11 | Read+Write | Always
MSA_UT_04_leer_anno | 192.168.4.43:4660 | 4:4X:12 | Read+Write | Always
MSA_UT_05_Pila_Mal | 192.168.4.43:4660 | 5:0X:200 | Read+Write | Always
MSA_UT_05_Alarma_incendio | 192.168.4.43:4660 | 5:0X:199 | Read+Write | Always
MSA_UT_05_leer_seg | 192.168.4.43:4660 | 5:4X:7 | Read+Write | Always
MSA_UT_05_leer_min | 192.168.4.43:4660 | 5:4X:8 | Read+Write | Always
MSA_UT_05_leer_hora | 192.168.4.43:4660 | 5:4X:9 | Read+Write | Always
MSA_UT_05_leer_dia | 192.168.4.43:4660 | 5:4X:10 | Read+Write | Always
MSA_UT_05_leer_mes | 192.168.4.43:4660 | 5:4X:11 | Read+Write | Always
MSA_UT_05_leer_anno | 192.168.4.43:4660 | 5:4X:12 | Read+Write | Always
MSA_UT_06_Pila_Mal | 192.168.4.43:4660 | 6:0X:200 | Read+Write | Always
MSA_UT_06_Alarma_incendio | 192.168.4.43:4660 | 6:0X:199 | Read+Write | Always
MSA_UT_06_leer_seg | 192.168.4.43:4660 | 6:4X:7 | Read+Write | Always
MSA_UT_06_leer_min | 192.168.4.43:4660 | 6:4X:8 | Read+Write | Always
MSA_UT_06_leer_hora | 192.168.4.43:4660 | 6:4X:9 | Read+Write | Always
MSA_UT_06_leer_dia | 192.168.4.43:4660 | 6:4X:10 | Read+Write | Always
MSA_UT_06_leer_mes | 192.168.4.43:4660 | 6:4X:11 | Read+Write | Always
MSA_UT_06_leer_anno | 192.168.4.43:4660 | 6:4X:12 | Read+Write | Always
MSA_UT_07_Pila_Mal | 192.168.4.43:4660 | 7:0X:200 | Read+Write | Always
MSA_UT_07_Alarma_incendio | 192.168.4.43:4660 | 7:0X:199 | Read+Write | Always
MSA_UT_07_leer_seg | 192.168.4.43:4660 | 7:4X:7 | Read+Write | Always
MSA_UT_07_leer_min | 192.168.4.43:4660 | 7:4X:8 | Read+Write | Always
MSA_UT_07_leer_hora | 192.168.4.43:4660 | 7:4X:9 | Read+Write | Always
MSA_UT_07_leer_dia | 192.168.4.43:4660 | 7:4X:10 | Read+Write | Always
MSA_UT_07_leer_mes | 192.168.4.43:4660 | 7:4X:11 | Read+Write | Always
MSA_UT_07_leer_anno | 192.168.4.43:4660 | 7:4X:12 | Read+Write | Always
MSA_UT_08_Pila_Mal | 192.168.4.43:4660 | 8:0X:200 | Read+Write | Always
MSA_UT_08_Alarma_incendio | 192.168.4.43:4660 | 8:0X:199 | Read+Write | Always
MSA_UT_08_leer_seg | 192.168.4.43:4660 | 8:4X:7 | Read+Write | Always
MSA_UT_08_leer_min | 192.168.4.43:4660 | 8:4X:8 | Read+Write | Always
MSA_UT_08_leer_hora | 192.168.4.43:4660 | 8:4X:9 | Read+Write | Always
MSA_UT_08_leer_dia | 192.168.4.43:4660 | 8:4X:10 | Read+Write | Always
MSA_UT_08_leer_mes | 192.168.4.43:4660 | 8:4X:11 | Read+Write | Always
MSA_UT_08_leer_anno | 192.168.4.43:4660 | 8:4X:12 | Read+Write | Always
MSA_UT_09_Pila_Mal | 192.168.4.43:4660 | 9:0X:200 | Read+Write | Always
MSA_UT_09_Alarma_incendio | 192.168.4.43:4660 | 9:0X:199 | Read+Write | Always
MSA_UT_09_leer_seg | 192.168.4.43:4660 | 9:4X:7 | Read+Write | Always
MSA_UT_09_leer_min | 192.168.4.43:4660 | 9:4X:8 | Read+Write | Always
MSA_UT_09_leer_hora | 192.168.4.43:4660 | 9:4X:9 | Read+Write | Always
MSA_UT_09_leer_dia | 192.168.4.43:4660 | 9:4X:10 | Read+Write | Always
MSA_UT_09_leer_mes | 192.168.4.43:4660 | 9:4X:11 | Read+Write | Always
MSA_UT_09_leer_anno | 192.168.4.43:4660 | 9:4X:12 | Read+Write | Always
MSA_UT_10_Pila_Mal | 192.168.4.43:4660 | 10:0X:200 | Read+Write | Always
MSA_UT_10_Alarma_incendio | 192.168.4.43:4660 | 10:0X:199 | Read+Write | Always
MSA_UT_10_leer_seg | 192.168.4.43:4660 | 10:4X:7 | Read+Write | Always
MSA_UT_10_leer_min | 192.168.4.43:4660 | 10:4X:8 | Read+Write | Always
MSA_UT_10_leer_hora | 192.168.4.43:4660 | 10:4X:9 | Read+Write | Always
MSA_UT_10_leer_dia | 192.168.4.43:4660 | 10:4X:10 | Read+Write | Always
MSA_UT_10_leer_mes | 192.168.4.43:4660 | 10:4X:11 | Read+Write | Always
MSA_UT_10_leer_anno | 192.168.4.43:4660 | 10:4X:12 | Read+Write | Always
MSA_UT_11_Pila_Mal | 192.168.4.43:4660 | 11:0X:200 | Read+Write | Always
MSA_UT_11_Alarma_incendio | 192.168.4.43:4660 | 11:0X:199 | Read+Write | Always
MSA_UT_11_leer_seg | 192.168.4.43:4660 | 11:4X:7 | Read+Write | Always
MSA_UT_11_leer_min | 192.168.4.43:4660 | 11:4X:8 | Read+Write | Always
MSA_UT_11_leer_hora | 192.168.4.43:4660 | 11:4X:9 | Read+Write | Always
MSA_UT_11_leer_dia | 192.168.4.43:4660 | 11:4X:10 | Read+Write | Always
MSA_UT_11_leer_mes | 192.168.4.43:4660 | 11:4X:11 | Read+Write | Always
MSA_UT_11_leer_anno | 192.168.4.43:4660 | 11:4X:12 | Read+Write | Always
MSA_UM_01_Pila_Mal | 192.168.4.53:4660 | 1:0X:200 | Read+Write | Always
MSA_UM_01_Alarma_incendio | 192.168.4.53:4660 | 1:0X:199 | Read+Write | Always
MSA_UM_01_leer_seg | 192.168.4.53:4660 | 1:4X:7 | Read+Write | Always
MSA_UM_01_leer_min | 192.168.4.53:4660 | 1:4X:8 | Read+Write | Always
MSA_UM_01_leer_hora | 192.168.4.53:4660 | 1:4X:9 | Read+Write | Always
MSA_UM_01_leer_dia | 192.168.4.53:4660 | 1:4X:10 | Read+Write | Always
MSA_UM_01_leer_mes | 192.168.4.53:4660 | 1:4X:11 | Read+Write | Always
MSA_UM_01_leer_anno | 192.168.4.53:4660 | 1:4X:12 | Read+Write | Always
MSA_UM_02_Pila_Mal | 192.168.4.53:4660 | 2:0X:200 | Read+Write | Always
MSA_UM_02_Alarma_incendio | 192.168.4.53:4660 | 2:0X:199 | Read+Write | Always
MSA_UM_02_leer_seg | 192.168.4.53:4660 | 2:4X:7 | Read+Write | Always
MSA_UM_02_leer_min | 192.168.4.53:4660 | 2:4X:8 | Read+Write | Always
MSA_UM_02_leer_hora | 192.168.4.53:4660 | 2:4X:9 | Read+Write | Always
MSA_UM_02_leer_dia | 192.168.4.53:4660 | 2:4X:10 | Read+Write | Always
MSA_UM_02_leer_mes | 192.168.4.53:4660 | 2:4X:11 | Read+Write | Always
MSA_UM_02_leer_anno | 192.168.4.53:4660 | 2:4X:12 | Read+Write | Always
MSA_UM_03_Pila_Mal | 192.168.4.53:4660 | 3:0X:200 | Read+Write | Always
MSA_UM_03_Alarma_incendio | 192.168.4.53:4660 | 3:0X:199 | Read+Write | Always
MSA_UM_03_leer_seg | 192.168.4.53:4660 | 3:4X:7 | Read+Write | Always
MSA_UM_03_leer_min | 192.168.4.53:4660 | 3:4X:8 | Read+Write | Always
MSA_UM_03_leer_hora | 192.168.4.53:4660 | 3:4X:9 | Read+Write | Always
MSA_UM_03_leer_dia | 192.168.4.53:4660 | 3:4X:10 | Read+Write | Always
MSA_UM_03_leer_mes | 192.168.4.53:4660 | 3:4X:11 | Read+Write | Always
MSA_UM_03_leer_anno | 192.168.4.53:4660 | 3:4X:12 | Read+Write | Always
MSA_UM_04_Pila_Mal | 192.168.4.53:4660 | 4:0X:200 | Read+Write | Always
MSA_UM_04_Alarma_incendio | 192.168.4.53:4660 | 4:0X:199 | Read+Write | Always
MSA_UM_04_leer_seg | 192.168.4.53:4660 | 4:4X:7 | Read+Write | Always
MSA_UM_04_leer_min | 192.168.4.53:4660 | 4:4X:8 | Read+Write | Always
MSA_UM_04_leer_hora | 192.168.4.53:4660 | 4:4X:9 | Read+Write | Always
MSA_UM_04_leer_dia | 192.168.4.53:4660 | 4:4X:10 | Read+Write | Always
MSA_UM_04_leer_mes | 192.168.4.53:4660 | 4:4X:11 | Read+Write | Always
MSA_UM_04_leer_anno | 192.168.4.53:4660 | 4:4X:12 | Read+Write | Always
MSA_UM_05_Pila_Mal | 192.168.4.53:4660 | 5:0X:200 | Read+Write | Always
MSA_UM_05_Alarma_incendio | 192.168.4.53:4660 | 5:0X:199 | Read+Write | Always
MSA_UM_05_leer_seg | 192.168.4.53:4660 | 5:4X:7 | Read+Write | Always
MSA_UM_05_leer_min | 192.168.4.53:4660 | 5:4X:8 | Read+Write | Always
MSA_UM_05_leer_hora | 192.168.4.53:4660 | 5:4X:9 | Read+Write | Always
MSA_UM_05_leer_dia | 192.168.4.53:4660 | 5:4X:10 | Read+Write | Always
MSA_UM_05_leer_mes | 192.168.4.53:4660 | 5:4X:11 | Read+Write | Always
MSA_UM_05_leer_anno | 192.168.4.53:4660 | 5:4X:12 | Read+Write | Always
MSA_UM_06_Pila_Mal | 192.168.4.53:4660 | 6:0X:200 | Read+Write | Always
MSA_UM_06_Alarma_incendio | 192.168.4.53:4660 | 6:0X:199 | Read+Write | Always
MSA_UM_06_leer_seg | 192.168.4.53:4660 | 6:4X:7 | Read+Write | Always
MSA_UM_06_leer_min | 192.168.4.53:4660 | 6:4X:8 | Read+Write | Always
MSA_UM_06_leer_hora | 192.168.4.53:4660 | 6:4X:9 | Read+Write | Always
MSA_UM_06_leer_dia | 192.168.4.53:4660 | 6:4X:10 | Read+Write | Always
MSA_UM_06_leer_mes | 192.168.4.53:4660 | 6:4X:11 | Read+Write | Always
MSA_UM_06_leer_anno | 192.168.4.53:4660 | 6:4X:12 | Read+Write | Always
MSA_UM_07_Pila_Mal | 192.168.4.53:4660 | 7:0X:200 | Read+Write | Always
MSA_UM_07_Alarma_incendio | 192.168.4.53:4660 | 7:0X:199 | Read+Write | Always
MSA_UM_07_leer_seg | 192.168.4.53:4660 | 7:4X:7 | Read+Write | Always
MSA_UM_07_leer_min | 192.168.4.53:4660 | 7:4X:8 | Read+Write | Always
MSA_UM_07_leer_hora | 192.168.4.53:4660 | 7:4X:9 | Read+Write | Always
MSA_UM_07_leer_dia | 192.168.4.53:4660 | 7:4X:10 | Read+Write | Always
MSA_UM_07_leer_mes | 192.168.4.53:4660 | 7:4X:11 | Read+Write | Always
MSA_UM_07_leer_anno | 192.168.4.53:4660 | 7:4X:12 | Read+Write | Always
MSA_UM_08_Pila_Mal | 192.168.4.53:4660 | 8:0X:200 | Read+Write | Always
MSA_UM_08_Alarma_incendio | 192.168.4.53:4660 | 8:0X:199 | Read+Write | Always
MSA_UM_08_leer_seg | 192.168.4.53:4660 | 8:4X:7 | Read+Write | Always
MSA_UM_08_leer_min | 192.168.4.53:4660 | 8:4X:8 | Read+Write | Always
MSA_UM_08_leer_hora | 192.168.4.53:4660 | 8:4X:9 | Read+Write | Always
MSA_UM_08_leer_dia | 192.168.4.53:4660 | 8:4X:10 | Read+Write | Always
MSA_UM_08_leer_mes | 192.168.4.53:4660 | 8:4X:11 | Read+Write | Always
MSA_UM_08_leer_anno | 192.168.4.53:4660 | 8:4X:12 | Read+Write | Always
MSA_UM_09_Pila_Mal | 192.168.4.53:4660 | 9:0X:200 | Read+Write | Always
MSA_UM_09_Alarma_incendio | 192.168.4.53:4660 | 9:0X:199 | Read+Write | Always
MSA_UM_09_leer_seg | 192.168.4.53:4660 | 9:4X:7 | Read+Write | Always
MSA_UM_09_leer_min | 192.168.4.53:4660 | 9:4X:8 | Read+Write | Always
MSA_UM_09_leer_hora | 192.168.4.53:4660 | 9:4X:9 | Read+Write | Always
MSA_UM_09_leer_dia | 192.168.4.53:4660 | 9:4X:10 | Read+Write | Always
MSA_UM_09_leer_mes | 192.168.4.53:4660 | 9:4X:11 | Read+Write | Always
MSA_UM_09_leer_anno | 192.168.4.53:4660 | 9:4X:12 | Read+Write | Always
MSA_UM_10_Pila_Mal | 192.168.4.53:4660 | 10:0X:200 | Read+Write | Always
MSA_UM_10_Alarma_incendio | 192.168.4.53:4660 | 10:0X:199 | Read+Write | Always
MSA_UM_10_leer_seg | 192.168.4.53:4660 | 10:4X:7 | Read+Write | Always
MSA_UM_10_leer_min | 192.168.4.53:4660 | 10:4X:8 | Read+Write | Always
MSA_UM_10_leer_hora | 192.168.4.53:4660 | 10:4X:9 | Read+Write | Always
MSA_UM_10_leer_dia | 192.168.4.53:4660 | 10:4X:10 | Read+Write | Always
MSA_UM_10_leer_mes | 192.168.4.53:4660 | 10:4X:11 | Read+Write | Always
MSA_UM_10_leer_anno | 192.168.4.53:4660 | 10:4X:12 | Read+Write | Always
MSA_UM_11_Pila_Mal | 192.168.4.53:4660 | 11:0X:200 | Read+Write | Always
MSA_UM_11_Alarma_incendio | 192.168.4.53:4660 | 11:0X:199 | Read+Write | Always
MSA_UM_11_leer_seg | 192.168.4.53:4660 | 11:4X:7 | Read+Write | Always
MSA_UM_11_leer_min | 192.168.4.53:4660 | 11:4X:8 | Read+Write | Always
MSA_UM_11_leer_hora | 192.168.4.53:4660 | 11:4X:9 | Read+Write | Always
MSA_UM_11_leer_dia | 192.168.4.53:4660 | 11:4X:10 | Read+Write | Always
MSA_UM_11_leer_mes | 192.168.4.53:4660 | 11:4X:11 | Read+Write | Always
MSA_UM_11_leer_anno | 192.168.4.53:4660 | 11:4X:12 | Read+Write | Always
MSA_BM_Alumb_Accesos.Estado | 192.168.4.23:4660 | 8:0X:206 | Read+Write | Always
MSA_BM_Alumb_Accesos.Fallo | 192.168.4.23:4660 | 8:0X:333 | Read+Write | Always
MSA_BM_Alumb_Accesos.Horario_A | 192.168.4.23:4660 | 8:3X:893T80 | Read+Write | Always
MSA_BM_Alumb_Accesos.Horario_estado | 192.168.4.23:4660 | 8:0X:329 | Read+Write | Always
MSA_BM_Alumb_Accesos.Manual_horario | 192.168.4.23:4660 | 8:0X:330 | Read+Write | Always
MSA_BM_Alumb_Accesos.Marcha_paro | 192.168.4.23:4660 | 8:0X:331 | Read+Write | Always
MSA_BM_Alumb_Accesos.Orden | 192.168.4.23:4660 | 8:0X:267 | Read+Write | Always
MSA_BM_Alumb_accesos_der.Estado | 192.168.4.23:4660 | 2:0X:217 | Read+Write | Always
MSA_BM_Alumb_accesos_der.Fallo | 192.168.4.23:4660 | 2:0X:381 | Read+Write | Always
MSA_BM_Alumb_accesos_der.Horario_A | 192.168.4.23:4660 | 2:3X:629T80 | Read+Write | Always
MSA_BM_Alumb_accesos_der.Horario_estado | 192.168.4.23:4660 | 2:0X:377 | Read+Write | Always
MSA_BM_Alumb_accesos_der.Manual_horario | 192.168.4.23:4660 | 2:0X:378 | Read+Write | Always
MSA_BM_Alumb_accesos_der.Marcha_paro | 192.168.4.23:4660 | 2:0X:379 | Read+Write | Always
MSA_BM_Alumb_accesos_der.Orden | 192.168.4.23:4660 | 2:0X:275 | Read+Write | Always
MSA_BM_Alumb_accesos_izq.Estado | 192.168.4.23:4660 | 2:0X:208 | Read+Write | Always
MSA_BM_Alumb_accesos_izq.Fallo | 192.168.4.23:4660 | 2:0X:373 | Read+Write | Always
MSA_BM_Alumb_accesos_izq.Horario_A | 192.168.4.23:4660 | 2:3X:673T80 | Read+Write | Always
MSA_BM_Alumb_accesos_izq.Horario_estado | 192.168.4.23:4660 | 2:0X:369 | Read+Write | Always
MSA_BM_Alumb_accesos_izq.Manual_horario | 192.168.4.23:4660 | 2:0X:370 | Read+Write | Always
MSA_BM_Alumb_accesos_izq.Marcha_paro | 192.168.4.23:4660 | 2:0X:371 | Read+Write | Always
MSA_BM_Alumb_accesos_izq.Orden | 192.168.4.23:4660 | 2:0X:274 | Read+Write | Always
MSA_BM_Alumb_accesos_testa.Estado | 192.168.4.23:4660 | 2:0X:218 | Read+Write | Always
MSA_BM_Alumb_accesos_testa.Fallo | 192.168.4.23:4660 | 2:0X:389 | Read+Write | Always
MSA_BM_Alumb_accesos_testa.Horario_A | 192.168.4.23:4660 | 2:3X:585T80 | Read+Write | Always
MSA_BM_Alumb_accesos_testa.Horario_estado | 192.168.4.23:4660 | 2:0X:385 | Read+Write | Always
MSA_BM_Alumb_accesos_testa.Manual_horario | 192.168.4.23:4660 | 2:0X:386 | Read+Write | Always
MSA_BM_Alumb_accesos_testa.Marcha_paro | 192.168.4.23:4660 | 2:0X:387 | Read+Write | Always
MSA_BM_Alumb_accesos_testa.Orden | 192.168.4.23:4660 | 2:0X:276 | Read+Write | Always
MSA_BM_Alumb_Baluarte.Estado | 192.168.4.23:4660 | 6:0X:222 | Read+Write | Always
MSA_BM_Alumb_Baluarte.Fallo | 192.168.4.23:4660 | 6:0X:413 | Read+Write | Always
MSA_BM_Alumb_Baluarte.Horario_A | 192.168.4.23:4660 | 6:3X:453T80 | Read+Write | Always
MSA_BM_Alumb_Baluarte.Horario_estado | 192.168.4.23:4660 | 6:0X:409 | Read+Write | Always
MSA_BM_Alumb_Baluarte.Manual_horario | 192.168.4.23:4660 | 6:0X:410 | Read+Write | Always
MSA_BM_Alumb_Baluarte.Marcha_paro | 192.168.4.23:4660 | 6:0X:411 | Read+Write | Always
MSA_BM_Alumb_Baluarte.Orden | 192.168.4.23:4660 | 6:0X:280 | Read+Write | Always
MSA_BM_Alumb_Contraescarpa.Estado | 192.168.4.23:4660 | 6:0X:223 | Read+Write | Always
MSA_BM_Alumb_Contraescarpa.Fallo | 192.168.4.23:4660 | 6:0X:349 | Read+Write | Always
MSA_BM_Alumb_Contraescarpa.Horario_A | 192.168.4.23:4660 | 6:3X:805T80 | Read+Write | Always
MSA_BM_Alumb_Contraescarpa.Horario_estado | 192.168.4.23:4660 | 6:0X:345 | Read+Write | Always
MSA_BM_Alumb_Contraescarpa.Manual_horario | 192.168.4.23:4660 | 6:0X:346 | Read+Write | Always
MSA_BM_Alumb_Contraescarpa.Marcha_paro | 192.168.4.23:4660 | 6:0X:347 | Read+Write | Always
MSA_BM_Alumb_Contraescarpa.Orden | 192.168.4.23:4660 | 6:0X:269 | Read+Write | Always
MSA_BM_Alumb_emergencia_gral.Estado | 192.168.4.23:4660 | 8:0X:207 | Read+Write | Always
MSA_BM_Alumb_emergencia_gral.Fallo | 192.168.4.23:4660 | 8:0X:349 | Read+Write | Always
MSA_BM_Alumb_emergencia_gral.Horario_A | 192.168.4.23:4660 | 8:3X:805T80 | Read+Write | Always
MSA_BM_Alumb_emergencia_gral.Horario_estado | 192.168.4.23:4660 | 8:0X:345 | Read+Write | Always
MSA_BM_Alumb_emergencia_gral.Manual_horario | 192.168.4.23:4660 | 8:0X:346 | Read+Write | Always
MSA_BM_Alumb_emergencia_gral.Marcha_paro | 192.168.4.23:4660 | 8:0X:347 | Read+Write | Always
MSA_BM_Alumb_emergencia_gral.Orden | 192.168.4.23:4660 | 8:0X:269 | Read+Write | Always
MSA_BM_Alumb_encants_der.Estado | 192.168.4.23:4660 | 2:0X:206 | Read+Write | Always
MSA_BM_Alumb_encants_der.Fallo | 192.168.4.23:4660 | 2:0X:357 | Read+Write | Always
MSA_BM_Alumb_encants_der.Horario_A | 192.168.4.23:4660 | 2:3X:761T80 | Read+Write | Always
MSA_BM_Alumb_encants_der.Horario_estado | 192.168.4.23:4660 | 2:0X:353 | Read+Write | Always
MSA_BM_Alumb_encants_der.Manual_horario | 192.168.4.23:4660 | 2:0X:354 | Read+Write | Always
MSA_BM_Alumb_encants_der.Marcha_paro | 192.168.4.23:4660 | 2:0X:355 | Read+Write | Always
MSA_BM_Alumb_encants_der.Orden | 192.168.4.23:4660 | 2:0X:270 | Read+Write | Always
MSA_BM_Alumb_encants_der_vigi.Estado | 192.168.4.23:4660 | 2:0X:207 | Read+Write | Always
MSA_BM_Alumb_encants_der_vigi.Fallo | 192.168.4.23:4660 | 2:0X:365 | Read+Write | Always
MSA_BM_Alumb_encants_der_vigi.Horario_A | 192.168.4.23:4660 | 2:3X:717T80 | Read+Write | Always
MSA_BM_Alumb_encants_der_vigi.Horario_estado | 192.168.4.23:4660 | 2:0X:361 | Read+Write | Always
MSA_BM_Alumb_encants_der_vigi.Manual_horario | 192.168.4.23:4660 | 2:0X:362 | Read+Write | Always
MSA_BM_Alumb_encants_der_vigi.Marcha_paro | 192.168.4.23:4660 | 2:0X:363 | Read+Write | Always
MSA_BM_Alumb_encants_der_vigi.Orden | 192.168.4.23:4660 | 2:0X:273 | Read+Write | Always
MSA_BM_Alumb_encants_izq.Estado | 192.168.4.23:4660 | 2:0X:201 | Read+Write | Always
MSA_BM_Alumb_encants_izq.Fallo | 192.168.4.23:4660 | 2:0X:317 | Read+Write | Always
MSA_BM_Alumb_encants_izq.Horario_A | 192.168.4.23:4660 | 2:3X:981T80 | Read+Write | Always
MSA_BM_Alumb_encants_izq.Horario_estado | 192.168.4.23:4660 | 2:0X:313 | Read+Write | Always
MSA_BM_Alumb_encants_izq.Manual_horario | 192.168.4.23:4660 | 2:0X:314 | Read+Write | Always
MSA_BM_Alumb_encants_izq.Marcha_paro | 192.168.4.23:4660 | 2:0X:315 | Read+Write | Always
MSA_BM_Alumb_encants_izq.Orden | 192.168.4.23:4660 | 2:0X:265 | Read+Write | Always
MSA_BM_Alumb_encants_izq_vigi.Estado | 192.168.4.23:4660 | 2:0X:202 | Read+Write | Always
MSA_BM_Alumb_encants_izq_vigi.Fallo | 192.168.4.23:4660 | 2:0X:325 | Read+Write | Always
MSA_BM_Alumb_encants_izq_vigi.Horario_A | 192.168.4.23:4660 | 2:3X:937T80 | Read+Write | Always
MSA_BM_Alumb_encants_izq_vigi.Horario_estado | 192.168.4.23:4660 | 2:0X:321 | Read+Write | Always
MSA_BM_Alumb_encants_izq_vigi.Manual_horario | 192.168.4.23:4660 | 2:0X:322 | Read+Write | Always
MSA_BM_Alumb_encants_izq_vigi.Marcha_paro | 192.168.4.23:4660 | 2:0X:323 | Read+Write | Always
MSA_BM_Alumb_encants_izq_vigi.Orden | 192.168.4.23:4660 | 2:0X:266 | Read+Write | Always
MSA_BM_Alumb_escalera_BM01.Estado | 192.168.4.23:4660 | 2:0X:219 | Read+Write | Always
MSA_BM_Alumb_escalera_BM01.Fallo | 192.168.4.23:4660 | 2:0X:397 | Read+Write | Always
MSA_BM_Alumb_escalera_BM01.Horario_A | 192.168.4.23:4660 | 2:3X:541T80 | Read+Write | Always
MSA_BM_Alumb_escalera_BM01.Horario_estado | 192.168.4.23:4660 | 2:0X:393 | Read+Write | Always
MSA_BM_Alumb_escalera_BM01.Manual_horario | 192.168.4.23:4660 | 2:0X:394 | Read+Write | Always
MSA_BM_Alumb_escalera_BM01.Marcha_paro | 192.168.4.23:4660 | 2:0X:395 | Read+Write | Always
MSA_BM_Alumb_escalera_BM01.Orden | 192.168.4.23:4660 | 2:0X:277 | Read+Write | Always
MSA_BM_Alumb_escalera_BM02.Estado | 192.168.4.23:4660 | 2:0X:220 | Read+Write | Always
MSA_BM_Alumb_escalera_BM02.Fallo | 192.168.4.23:4660 | 2:0X:405 | Read+Write | Always
MSA_BM_Alumb_escalera_BM02.Horario_A | 192.168.4.23:4660 | 2:3X:497T80 | Read+Write | Always
MSA_BM_Alumb_escalera_BM02.Horario_estado | 192.168.4.23:4660 | 2:0X:401 | Read+Write | Always
MSA_BM_Alumb_escalera_BM02.Manual_horario | 192.168.4.23:4660 | 2:0X:402 | Read+Write | Always
MSA_BM_Alumb_escalera_BM02.Marcha_paro | 192.168.4.23:4660 | 2:0X:403 | Read+Write | Always
MSA_BM_Alumb_escalera_BM02.Orden | 192.168.4.23:4660 | 2:0X:278 | Read+Write | Always
MSA_BM_Alumb_escalera_BM03.Estado | 192.168.4.23:4660 | 2:0X:221 | Read+Write | Always
MSA_BM_Alumb_escalera_BM03.Fallo | 192.168.4.23:4660 | 2:0X:413 | Read+Write | Always
MSA_BM_Alumb_escalera_BM03.Horario_A | 192.168.4.23:4660 | 2:3X:453T80 | Read+Write | Always
MSA_BM_Alumb_escalera_BM03.Horario_estado | 192.168.4.23:4660 | 2:0X:409 | Read+Write | Always
MSA_BM_Alumb_escalera_BM03.Manual_horario | 192.168.4.23:4660 | 2:0X:410 | Read+Write | Always
MSA_BM_Alumb_escalera_BM03.Marcha_paro | 192.168.4.23:4660 | 2:0X:411 | Read+Write | Always
MSA_BM_Alumb_escalera_BM03.Orden | 192.168.4.23:4660 | 2:0X:279 | Read+Write | Always
MSA_BM_Alumb_Exte_1_Marques.Estado | 192.168.4.23:4660 | 3:0X:201 | Read+Write | Always
MSA_BM_Alumb_Exte_1_Marques.Fallo | 192.168.4.23:4660 | 3:0X:317 | Read+Write | Always
MSA_BM_Alumb_Exte_1_Marques.Horario_A | 192.168.4.23:4660 | 3:3X:981T80 | Read+Write | Always
MSA_BM_Alumb_Exte_1_Marques.Horario_estado | 192.168.4.23:4660 | 3:0X:313 | Read+Write | Always
MSA_BM_Alumb_Exte_1_Marques.Manual_horario | 192.168.4.23:4660 | 3:0X:314 | Read+Write | Always
MSA_BM_Alumb_Exte_1_Marques.Marcha_paro | 192.168.4.23:4660 | 3:0X:315 | Read+Write | Always
MSA_BM_Alumb_Exte_1_Marques.Orden | 192.168.4.23:4660 | 3:0X:265 | Read+Write | Always
MSA_BM_Alumb_Exte_2_Marques.Estado | 192.168.4.23:4660 | 3:0X:202 | Read+Write | Always
MSA_BM_Alumb_Exte_2_Marques.Fallo | 192.168.4.23:4660 | 3:0X:325 | Read+Write | Always
MSA_BM_Alumb_Exte_2_Marques.Horario_A | 192.168.4.23:4660 | 3:3X:937T80 | Read+Write | Always
MSA_BM_Alumb_Exte_2_Marques.Horario_estado | 192.168.4.23:4660 | 3:0X:321 | Read+Write | Always
MSA_BM_Alumb_Exte_2_Marques.Manual_horario | 192.168.4.23:4660 | 3:0X:322 | Read+Write | Always
MSA_BM_Alumb_Exte_2_Marques.Marcha_paro | 192.168.4.23:4660 | 3:0X:323 | Read+Write | Always
MSA_BM_Alumb_Exte_2_Marques.Orden | 192.168.4.23:4660 | 3:0X:266 | Read+Write | Always
MSA_BM_Alumb_Exte_3_fachada.Estado | 192.168.4.23:4660 | 3:0X:203 | Read+Write | Always
MSA_BM_Alumb_Exte_3_fachada.Fallo | 192.168.4.23:4660 | 3:0X:333 | Read+Write | Always
MSA_BM_Alumb_Exte_3_fachada.Horario_A | 192.168.4.23:4660 | 3:3X:893T80 | Read+Write | Always
MSA_BM_Alumb_Exte_3_fachada.Horario_estado | 192.168.4.23:4660 | 3:0X:329 | Read+Write | Always
MSA_BM_Alumb_Exte_3_fachada.Manual_horario | 192.168.4.23:4660 | 3:0X:330 | Read+Write | Always
MSA_BM_Alumb_Exte_3_fachada.Marcha_paro | 192.168.4.23:4660 | 3:0X:331 | Read+Write | Always
MSA_BM_Alumb_Exte_3_fachada.Orden | 192.168.4.23:4660 | 3:0X:267 | Read+Write | Always
MSA_BM_Alumb_Exte_4_fachada.Estado | 192.168.4.23:4660 | 3:0X:204 | Read+Write | Always
MSA_BM_Alumb_Exte_4_fachada.Fallo | 192.168.4.23:4660 | 3:0X:341 | Read+Write | Always
MSA_BM_Alumb_Exte_4_fachada.Horario_A | 192.168.4.23:4660 | 3:3X:849T80 | Read+Write | Always
MSA_BM_Alumb_Exte_4_fachada.Horario_estado | 192.168.4.23:4660 | 3:0X:337 | Read+Write | Always
MSA_BM_Alumb_Exte_4_fachada.Manual_horario | 192.168.4.23:4660 | 3:0X:338 | Read+Write | Always
MSA_BM_Alumb_Exte_4_fachada.Marcha_paro | 192.168.4.23:4660 | 3:0X:339 | Read+Write | Always
MSA_BM_Alumb_Exte_4_fachada.Orden | 192.168.4.23:4660 | 3:0X:268 | Read+Write | Always
MSA_BM_Alumb_Exte_5_PlazaM.Estado | 192.168.4.23:4660 | 3:0X:205 | Read+Write | Always
MSA_BM_Alumb_Exte_5_PlazaM.Fallo | 192.168.4.23:4660 | 3:0X:349 | Read+Write | Always
MSA_BM_Alumb_Exte_5_PlazaM.Horario_A | 192.168.4.23:4660 | 3:3X:805T80 | Read+Write | Always
MSA_BM_Alumb_Exte_5_PlazaM.Horario_estado | 192.168.4.23:4660 | 3:0X:345 | Read+Write | Always
MSA_BM_Alumb_Exte_5_PlazaM.Manual_horario | 192.168.4.23:4660 | 3:0X:346 | Read+Write | Always
MSA_BM_Alumb_Exte_5_PlazaM.Marcha_paro | 192.168.4.23:4660 | 3:0X:347 | Read+Write | Always
MSA_BM_Alumb_Exte_5_PlazaM.Orden | 192.168.4.23:4660 | 3:0X:269 | Read+Write | Always
MSA_BM_Alumb_Exte_6_PlazaB.Estado | 192.168.4.23:4660 | 3:0X:206 | Read+Write | Always
MSA_BM_Alumb_Exte_6_PlazaB.Fallo | 192.168.4.23:4660 | 3:0X:357 | Read+Write | Always
MSA_BM_Alumb_Exte_6_PlazaB.Horario_A | 192.168.4.23:4660 | 3:3X:761T80 | Read+Write | Always
MSA_BM_Alumb_Exte_6_PlazaB.Horario_estado | 192.168.4.23:4660 | 3:0X:353 | Read+Write | Always
MSA_BM_Alumb_Exte_6_PlazaB.Manual_horario | 192.168.4.23:4660 | 3:0X:354 | Read+Write | Always
MSA_BM_Alumb_Exte_6_PlazaB.Marcha_paro | 192.168.4.23:4660 | 3:0X:355 | Read+Write | Always
MSA_BM_Alumb_Exte_6_PlazaB.Orden | 192.168.4.23:4660 | 3:0X:270 | Read+Write | Always
MSA_BM_Alumb_fresc_1.Estado | 192.168.4.23:4660 | 2:0X:203 | Read+Write | Always
MSA_BM_Alumb_fresc_1.Fallo | 192.168.4.23:4660 | 2:0X:333 | Read+Write | Always
MSA_BM_Alumb_fresc_1.Horario_A | 192.168.4.23:4660 | 2:3X:893T80 | Read+Write | Always
MSA_BM_Alumb_fresc_1.Horario_estado | 192.168.4.23:4660 | 2:0X:329 | Read+Write | Always
MSA_BM_Alumb_fresc_1.Manual_horario | 192.168.4.23:4660 | 2:0X:330 | Read+Write | Always
MSA_BM_Alumb_fresc_1.Marcha_paro | 192.168.4.23:4660 | 2:0X:331 | Read+Write | Always
MSA_BM_Alumb_fresc_1.Orden | 192.168.4.23:4660 | 2:0X:267 | Read+Write | Always
MSA_BM_Alumb_fresc_2.Estado | 192.168.4.23:4660 | 2:0X:204 | Read+Write | Always
MSA_BM_Alumb_fresc_2.Fallo | 192.168.4.23:4660 | 2:0X:341 | Read+Write | Always
MSA_BM_Alumb_fresc_2.Horario_A | 192.168.4.23:4660 | 2:3X:849T80 | Read+Write | Always
MSA_BM_Alumb_fresc_2.Horario_estado | 192.168.4.23:4660 | 2:0X:337 | Read+Write | Always
MSA_BM_Alumb_fresc_2.Manual_horario | 192.168.4.23:4660 | 2:0X:338 | Read+Write | Always
MSA_BM_Alumb_fresc_2.Marcha_paro | 192.168.4.23:4660 | 2:0X:339 | Read+Write | Always
MSA_BM_Alumb_fresc_2.Orden | 192.168.4.23:4660 | 2:0X:268 | Read+Write | Always
MSA_BM_Alumb_fresc_3.Estado | 192.168.4.23:4660 | 2:0X:205 | Read+Write | Always
MSA_BM_Alumb_fresc_3.Fallo | 192.168.4.23:4660 | 2:0X:349 | Read+Write | Always
MSA_BM_Alumb_fresc_3.Horario_A | 192.168.4.23:4660 | 2:3X:805T80 | Read+Write | Always
MSA_BM_Alumb_fresc_3.Horario_estado | 192.168.4.23:4660 | 2:0X:345 | Read+Write | Always
MSA_BM_Alumb_fresc_3.Manual_horario | 192.168.4.23:4660 | 2:0X:346 | Read+Write | Always
MSA_BM_Alumb_fresc_3.Marcha_paro | 192.168.4.23:4660 | 2:0X:347 | Read+Write | Always
MSA_BM_Alumb_fresc_3.Orden | 192.168.4.23:4660 | 2:0X:269 | Read+Write | Always
MSA_BM_Alumb_Gral_1.Estado | 192.168.4.23:4660 | 8:0X:205 | Read+Write | Always
MSA_BM_Alumb_Gral_1.Fallo | 192.168.4.23:4660 | 8:0X:325 | Read+Write | Always
MSA_BM_Alumb_Gral_1.Horario_A | 192.168.4.23:4660 | 8:3X:937T80 | Read+Write | Always
MSA_BM_Alumb_Gral_1.Horario_estado | 192.168.4.23:4660 | 8:0X:321 | Read+Write | Always
MSA_BM_Alumb_Gral_1.Manual_horario | 192.168.4.23:4660 | 8:0X:322 | Read+Write | Always
MSA_BM_Alumb_Gral_1.Marcha_paro | 192.168.4.23:4660 | 8:0X:323 | Read+Write | Always
MSA_BM_Alumb_Gral_1.Orden | 192.168.4.23:4660 | 8:0X:266 | Read+Write | Always
MSA_BM_Alumb_Gral_Estado_int | 192.168.4.23:4660 | 6:0X:228 | Read+Write | Always
MSA_BM_Alumb_Gral_techo_1.Estado | 192.168.4.23:4660 | 6:0X:219 | Read+Write | Always
MSA_BM_Alumb_Gral_techo_1.Fallo | 192.168.4.23:4660 | 6:0X:389 | Read+Write | Always
MSA_BM_Alumb_Gral_techo_1.Horario_A | 192.168.4.23:4660 | 6:3X:585T80 | Read+Write | Always
MSA_BM_Alumb_Gral_techo_1.Horario_estado | 192.168.4.23:4660 | 6:0X:385 | Read+Write | Always
MSA_BM_Alumb_Gral_techo_1.Manual_horario | 192.168.4.23:4660 | 6:0X:386 | Read+Write | Always
MSA_BM_Alumb_Gral_techo_1.Marcha_paro | 192.168.4.23:4660 | 6:0X:387 | Read+Write | Always
MSA_BM_Alumb_Gral_techo_1.Orden | 192.168.4.23:4660 | 6:0X:277 | Read+Write | Always
MSA_BM_Alumb_Gral_techo_2.Estado | 192.168.4.23:4660 | 6:0X:220 | Read+Write | Always
MSA_BM_Alumb_Gral_techo_2.Fallo | 192.168.4.23:4660 | 6:0X:397 | Read+Write | Always
MSA_BM_Alumb_Gral_techo_2.Horario_A | 192.168.4.23:4660 | 6:3X:541T80 | Read+Write | Always
MSA_BM_Alumb_Gral_techo_2.Horario_estado | 192.168.4.23:4660 | 6:0X:393 | Read+Write | Always
MSA_BM_Alumb_Gral_techo_2.Manual_horario | 192.168.4.23:4660 | 6:0X:394 | Read+Write | Always
MSA_BM_Alumb_Gral_techo_2.Marcha_paro | 192.168.4.23:4660 | 6:0X:395 | Read+Write | Always
MSA_BM_Alumb_Gral_techo_2.Orden | 192.168.4.23:4660 | 6:0X:278 | Read+Write | Always
MSA_BM_Alumb_Gral_techo_3.Estado | 192.168.4.23:4660 | 6:0X:221 | Read+Write | Always
MSA_BM_Alumb_Gral_techo_3.Fallo | 192.168.4.23:4660 | 6:0X:405 | Read+Write | Always
MSA_BM_Alumb_Gral_techo_3.Horario_A | 192.168.4.23:4660 | 6:3X:497T80 | Read+Write | Always
MSA_BM_Alumb_Gral_techo_3.Horario_estado | 192.168.4.23:4660 | 6:0X:401 | Read+Write | Always
MSA_BM_Alumb_Gral_techo_3.Manual_horario | 192.168.4.23:4660 | 6:0X:402 | Read+Write | Always
MSA_BM_Alumb_Gral_techo_3.Marcha_paro | 192.168.4.23:4660 | 6:0X:403 | Read+Write | Always
MSA_BM_Alumb_Gral_techo_3.Orden | 192.168.4.23:4660 | 6:0X:279 | Read+Write | Always
MSA_BM_Alumb_Pergolas_Borrell_1.Estado | 192.168.4.23:4660 | 1:0X:259 | Read+Write | Always
MSA_BM_Alumb_Pergolas_Borrell_1.Fallo | 192.168.4.23:4660 | 1:0X:413 | Read+Write | Always
MSA_BM_Alumb_Pergolas_Borrell_1.Horario_A | 192.168.4.23:4660 | 1:3X:453T80 | Read+Write | Always
MSA_BM_Alumb_Pergolas_Borrell_1.Horario_estado | 192.168.4.23:4660 | 1:0X:409 | Read+Write | Always
MSA_BM_Alumb_Pergolas_Borrell_1.Manual_horario | 192.168.4.23:4660 | 1:0X:410 | Read+Write | Always
MSA_BM_Alumb_Pergolas_Borrell_1.Marcha_paro | 192.168.4.23:4660 | 1:0X:411 | Read+Write | Always
MSA_BM_Alumb_Pergolas_Borrell_1.Orden | 192.168.4.23:4660 | 1:0X:295 | Read+Write | Always
MSA_BM_Alumb_Pergolas_Borrell_2.Estado | 192.168.4.23:4660 | 1:0X:260 | Read+Write | Always
MSA_BM_Alumb_Pergolas_Borrell_2.Fallo | 192.168.4.23:4660 | 1:0X:421 | Read+Write | Always
MSA_BM_Alumb_Pergolas_Borrell_2.Horario_A | 192.168.4.23:4660 | 1:3X:409T80 | Read+Write | Always
MSA_BM_Alumb_Pergolas_Borrell_2.Horario_estado | 192.168.4.23:4660 | 1:0X:417 | Read+Write | Always
MSA_BM_Alumb_Pergolas_Borrell_2.Manual_horario | 192.168.4.23:4660 | 1:0X:418 | Read+Write | Always
MSA_BM_Alumb_Pergolas_Borrell_2.Marcha_paro | 192.168.4.23:4660 | 1:0X:419 | Read+Write | Always
MSA_BM_Alumb_Pergolas_Borrell_2.Orden | 192.168.4.23:4660 | 1:0X:296 | Read+Write | Always
MSA_BM_Alumb_Pergolas_Manso_1.Estado | 192.168.4.23:4660 | 1:0X:257 | Read+Write | Always
MSA_BM_Alumb_Pergolas_Manso_1.Fallo | 192.168.4.23:4660 | 1:0X:397 | Read+Write | Always
MSA_BM_Alumb_Pergolas_Manso_1.Horario_A | 192.168.4.23:4660 | 1:3X:541T80 | Read+Write | Always
MSA_BM_Alumb_Pergolas_Manso_1.Horario_estado | 192.168.4.23:4660 | 1:0X:393 | Read+Write | Always
MSA_BM_Alumb_Pergolas_Manso_1.Manual_horario | 192.168.4.23:4660 | 1:0X:394 | Read+Write | Always
MSA_BM_Alumb_Pergolas_Manso_1.Marcha_paro | 192.168.4.23:4660 | 1:0X:395 | Read+Write | Always
MSA_BM_Alumb_Pergolas_Manso_1.Orden | 192.168.4.23:4660 | 1:0X:293 | Read+Write | Always
MSA_BM_Alumb_Pergolas_Manso_2.Estado | 192.168.4.23:4660 | 1:0X:258 | Read+Write | Always
MSA_BM_Alumb_Pergolas_Manso_2.Fallo | 192.168.4.23:4660 | 1:0X:405 | Read+Write | Always
MSA_BM_Alumb_Pergolas_Manso_2.Horario_A | 192.168.4.23:4660 | 1:3X:497T80 | Read+Write | Always
MSA_BM_Alumb_Pergolas_Manso_2.Horario_estado | 192.168.4.23:4660 | 1:0X:401 | Read+Write | Always
MSA_BM_Alumb_Pergolas_Manso_2.Manual_horario | 192.168.4.23:4660 | 1:0X:402 | Read+Write | Always
MSA_BM_Alumb_Pergolas_Manso_2.Marcha_paro | 192.168.4.23:4660 | 1:0X:403 | Read+Write | Always
MSA_BM_Alumb_Pergolas_Manso_2.Orden | 192.168.4.23:4660 | 1:0X:294 | Read+Write | Always
MSA_BM_Alumb_Plaza_Manso_balizas.Estado | 192.168.4.23:4660 | 6:0X:225 | Read+Write | Always
MSA_BM_Alumb_Plaza_Manso_balizas.Fallo | 192.168.4.23:4660 | 6:0X:365 | Read+Write | Always
MSA_BM_Alumb_Plaza_Manso_balizas.Horario_A | 192.168.4.23:4660 | 6:3X:717T80 | Read+Write | Always
MSA_BM_Alumb_Plaza_Manso_balizas.Horario_estado | 192.168.4.23:4660 | 6:0X:361 | Read+Write | Always
MSA_BM_Alumb_Plaza_Manso_balizas.Manual_horario | 192.168.4.23:4660 | 6:0X:362 | Read+Write | Always
MSA_BM_Alumb_Plaza_Manso_balizas.Marcha_paro | 192.168.4.23:4660 | 6:0X:363 | Read+Write | Always
MSA_BM_Alumb_Plaza_Manso_balizas.Orden | 192.168.4.23:4660 | 6:0X:274 | Read+Write | Always
MSA_BM_Alumb_Plaza_Manso_preim.Estado | 192.168.4.23:4660 | 6:0X:224 | Read+Write | Always
MSA_BM_Alumb_Plaza_Manso_preim.Fallo | 192.168.4.23:4660 | 6:0X:357 | Read+Write | Always
MSA_BM_Alumb_Plaza_Manso_preim.Horario_A | 192.168.4.23:4660 | 6:3X:761T80 | Read+Write | Always
MSA_BM_Alumb_Plaza_Manso_preim.Horario_estado | 192.168.4.23:4660 | 6:0X:353 | Read+Write | Always
MSA_BM_Alumb_Plaza_Manso_preim.Manual_horario | 192.168.4.23:4660 | 6:0X:354 | Read+Write | Always
MSA_BM_Alumb_Plaza_Manso_preim.Marcha_paro | 192.168.4.23:4660 | 6:0X:355 | Read+Write | Always
MSA_BM_Alumb_Plaza_Manso_preim.Orden | 192.168.4.23:4660 | 6:0X:273 | Read+Write | Always
MSA_BM_Alumb_QM17_Baluarte.Estado | 192.168.4.23:4660 | 7:0X:207 | Read+Write | Always
MSA_BM_Alumb_QM17_Baluarte.Fallo | 192.168.4.23:4660 | 7:0X:317 | Read+Write | Always
MSA_BM_Alumb_QM17_Baluarte.Horario_A | 192.168.4.23:4660 | 7:3X:981T80 | Read+Write | Always
MSA_BM_Alumb_QM17_Baluarte.Horario_estado | 192.168.4.23:4660 | 7:0X:313 | Read+Write | Always
MSA_BM_Alumb_QM17_Baluarte.Manual_horario | 192.168.4.23:4660 | 7:0X:314 | Read+Write | Always
MSA_BM_Alumb_QM17_Baluarte.Marcha_paro | 192.168.4.23:4660 | 7:0X:315 | Read+Write | Always
MSA_BM_Alumb_QM17_Baluarte.Orden | 192.168.4.23:4660 | 7:0X:265 | Read+Write | Always
MSA_BM_Alumb_QM21_Cocina_BM.Estado | 192.168.4.23:4660 | 6:0X:203 | Read+Write | Always
MSA_BM_Alumb_QM21_Cocina_BM.Fallo | 192.168.4.23:4660 | 6:0X:325 | Read+Write | Always
MSA_BM_Alumb_QM21_Cocina_BM.Horario_A | 192.168.4.23:4660 | 6:3X:937T80 | Read+Write | Always
MSA_BM_Alumb_QM21_Cocina_BM.Horario_estado | 192.168.4.23:4660 | 6:0X:321 | Read+Write | Always
MSA_BM_Alumb_QM21_Cocina_BM.Manual_horario | 192.168.4.23:4660 | 6:0X:322 | Read+Write | Always
MSA_BM_Alumb_QM21_Cocina_BM.Marcha_paro | 192.168.4.23:4660 | 6:0X:323 | Read+Write | Always
MSA_BM_Alumb_QM21_Cocina_BM.Orden | 192.168.4.23:4660 | 6:0X:266 | Read+Write | Always
MSA_BM_Alumb_QM21_Patio_testa_BM.Estado | 192.168.4.23:4660 | 6:0X:202 | Read+Write | Always
MSA_BM_Alumb_QM21_Patio_testa_BM.Fallo | 192.168.4.23:4660 | 6:0X:317 | Read+Write | Always
MSA_BM_Alumb_QM21_Patio_testa_BM.Horario_A | 192.168.4.23:4660 | 6:3X:981T80 | Read+Write | Always
MSA_BM_Alumb_QM21_Patio_testa_BM.Horario_estado | 192.168.4.23:4660 | 6:0X:313 | Read+Write | Always
MSA_BM_Alumb_QM21_Patio_testa_BM.Manual_horario | 192.168.4.23:4660 | 6:0X:314 | Read+Write | Always
MSA_BM_Alumb_QM21_Patio_testa_BM.Marcha_paro | 192.168.4.23:4660 | 6:0X:315 | Read+Write | Always
MSA_BM_Alumb_QM21_Patio_testa_BM.Orden | 192.168.4.23:4660 | 6:0X:265 | Read+Write | Always
MSA_BM_Alumb_Reserva_1.Estado | 192.168.4.23:4660 | 6:0X:226 | Read+Write | Always
MSA_BM_Alumb_Reserva_1.Fallo | 192.168.4.23:4660 | 6:0X:373 | Read+Write | Always
MSA_BM_Alumb_Reserva_1.Horario_A | 192.168.4.23:4660 | 6:3X:673T80 | Read+Write | Always
MSA_BM_Alumb_Reserva_1.Horario_estado | 192.168.4.23:4660 | 6:0X:369 | Read+Write | Always
MSA_BM_Alumb_Reserva_1.Manual_horario | 192.168.4.23:4660 | 6:0X:370 | Read+Write | Always
MSA_BM_Alumb_Reserva_1.Marcha_paro | 192.168.4.23:4660 | 6:0X:371 | Read+Write | Always
MSA_BM_Alumb_Reserva_1.Orden | 192.168.4.23:4660 | 6:0X:275 | Read+Write | Always
MSA_BM_Alumb_Reserva_2.Estado | 192.168.4.23:4660 | 6:0X:227 | Read+Write | Always
MSA_BM_Alumb_Reserva_2.Fallo | 192.168.4.23:4660 | 6:0X:381 | Read+Write | Always
MSA_BM_Alumb_Reserva_2.Horario_A | 192.168.4.23:4660 | 6:3X:629T80 | Read+Write | Always
MSA_BM_Alumb_Reserva_2.Horario_estado | 192.168.4.23:4660 | 6:0X:377 | Read+Write | Always
MSA_BM_Alumb_Reserva_2.Manual_horario | 192.168.4.23:4660 | 6:0X:378 | Read+Write | Always
MSA_BM_Alumb_Reserva_2.Marcha_paro | 192.168.4.23:4660 | 6:0X:379 | Read+Write | Always
MSA_BM_Alumb_Reserva_2.Orden | 192.168.4.23:4660 | 6:0X:276 | Read+Write | Always
MSA_BM_Alumb_residuos.Estado | 192.168.4.23:4660 | 8:0X:208 | Read+Write | Always
MSA_BM_Alumb_residuos.Fallo | 192.168.4.23:4660 | 8:0X:341 | Read+Write | Always
MSA_BM_Alumb_residuos.Horario_A | 192.168.4.23:4660 | 8:3X:849T80 | Read+Write | Always
MSA_BM_Alumb_residuos.Horario_estado | 192.168.4.23:4660 | 8:0X:337 | Read+Write | Always
MSA_BM_Alumb_residuos.Manual_horario | 192.168.4.23:4660 | 8:0X:338 | Read+Write | Always
MSA_BM_Alumb_residuos.Marcha_paro | 192.168.4.23:4660 | 8:0X:339 | Read+Write | Always
MSA_BM_Alumb_residuos.Orden | 192.168.4.23:4660 | 8:0X:268 | Read+Write | Always
MSA_BM_Alumb_Vigi_locales_serv.Estado | 192.168.4.23:4660 | 8:0X:204 | Read+Write | Always
MSA_BM_Alumb_Vigi_locales_serv.Fallo | 192.168.4.23:4660 | 8:0X:317 | Read+Write | Always
MSA_BM_Alumb_Vigi_locales_serv.Horario_A | 192.168.4.23:4660 | 8:3X:981T80 | Read+Write | Always
MSA_BM_Alumb_Vigi_locales_serv.Horario_estado | 192.168.4.23:4660 | 8:0X:313 | Read+Write | Always
MSA_BM_Alumb_Vigi_locales_serv.Manual_horario | 192.168.4.23:4660 | 8:0X:314 | Read+Write | Always
MSA_BM_Alumb_Vigi_locales_serv.Marcha_paro | 192.168.4.23:4660 | 8:0X:315 | Read+Write | Always
MSA_BM_Alumb_Vigi_locales_serv.Orden | 192.168.4.23:4660 | 8:0X:265 | Read+Write | Always
MSA_BM_Bomba_AC_A_Geoterm_1.Alarma_variador | 192.168.4.23:4660 | 5:0X:247 | Read+Write | Always
MSA_BM_Bomba_AC_A_Geoterm_1.Estado | 192.168.4.23:4660 | 5:0X:223 | Read+Write | Always
MSA_BM_Bomba_AC_A_Geoterm_1.Fallo | 192.168.4.23:4660 | 5:0X:334 | Read+Write | Always
MSA_BM_Bomba_AC_A_Geoterm_1.Horas_funcionam | 192.168.4.23:4660 | 5:3X:848 | Read+Write | Always
MSA_BM_Bomba_AC_A_Geoterm_1.Orden | 192.168.4.23:4660 | 5:0X:283 | Read+Write | Always
MSA_BM_Bomba_AC_A_Geoterm_2.Alarma_variador | 192.168.4.23:4660 | 5:0X:248 | Read+Write | Always
MSA_BM_Bomba_AC_A_Geoterm_2.Estado | 192.168.4.23:4660 | 5:0X:224 | Read+Write | Always
MSA_BM_Bomba_AC_A_Geoterm_2.Fallo | 192.168.4.23:4660 | 5:0X:335 | Read+Write | Always
MSA_BM_Bomba_AC_A_Geoterm_2.Horas_funcionam | 192.168.4.23:4660 | 5:3X:804 | Read+Write | Always
MSA_BM_Bomba_AC_A_Geoterm_2.Orden | 192.168.4.23:4660 | 5:0X:284 | Read+Write | Always
MSA_BM_Bomba_AF_A_Geoterm_1.Alarma_variador | 192.168.4.23:4660 | 5:0X:245 | Read+Write | Always
MSA_BM_Bomba_AF_A_Geoterm_1.Estado | 192.168.4.23:4660 | 5:0X:204 | Read+Write | Always
MSA_BM_Bomba_AF_A_Geoterm_1.Fallo | 192.168.4.23:4660 | 5:0X:357 | Read+Write | Always
MSA_BM_Bomba_AF_A_Geoterm_1.Horas_funcionam | 192.168.4.23:4660 | 5:3X:584 | Read+Write | Always
MSA_BM_Bomba_AF_A_Geoterm_1.Orden | 192.168.4.23:4660 | 5:0X:275 | Read+Write | Always
MSA_BM_Bomba_AF_A_Geoterm_2.Alarma_variador | 192.168.4.23:4660 | 5:0X:246 | Read+Write | Always
MSA_BM_Bomba_AF_A_Geoterm_2.Estado | 192.168.4.23:4660 | 5:0X:205 | Read+Write | Always
MSA_BM_Bomba_AF_A_Geoterm_2.Fallo | 192.168.4.23:4660 | 5:0X:358 | Read+Write | Always
MSA_BM_Bomba_AF_A_Geoterm_2.Horas_funcionam | 192.168.4.23:4660 | 5:3X:540 | Read+Write | Always
MSA_BM_Bomba_AF_A_Geoterm_2.Orden | 192.168.4.23:4660 | 5:0X:276 | Read+Write | Always
MSA_BM_Bomba_calor_1.Estado | 192.168.4.23:4660 | 4:0X:221 | Read+Write | Always
MSA_BM_Bomba_calor_1.Horas_funcionam | 192.168.4.23:4660 | 4:3X:848 | Read+Write | Always
MSA_BM_Bomba_calor_2.Estado | 192.168.4.23:4660 | 4:0X:222 | Read+Write | Always
MSA_BM_Bomba_calor_2.Horas_funcionam | 192.168.4.23:4660 | 4:3X:804 | Read+Write | Always
MSA_BM_Bomba_Condens_1.Estado | 192.168.4.23:4660 | 4:0X:217 | Read+Write | Always
MSA_BM_Bomba_Condens_1.Horas_funcionam | 192.168.4.23:4660 | 4:3X:1024 | Read+Write | Always
MSA_BM_Bomba_Condens_2.Estado | 192.168.4.23:4660 | 4:0X:218 | Read+Write | Always
MSA_BM_Bomba_Condens_2.Horas_funcionam | 192.168.4.23:4660 | 4:3X:980 | Read+Write | Always
MSA_BM_Bomba_frio_1.Estado | 192.168.4.23:4660 | 4:0X:219 | Read+Write | Always
MSA_BM_Bomba_frio_1.Horas_funcionam | 192.168.4.23:4660 | 4:3X:936 | Read+Write | Always
MSA_BM_Bomba_frio_2.Estado | 192.168.4.23:4660 | 4:0X:220 | Read+Write | Always
MSA_BM_Bomba_frio_2.Horas_funcionam | 192.168.4.23:4660 | 4:3X:892 | Read+Write | Always
MSA_BM_Bombas_AC_A_Geoterm.Horario_A | 192.168.4.23:4660 | 5:3X:893T80 | Read+Write | Always
MSA_BM_Bombas_AC_A_Geoterm.Horario_estado | 192.168.4.23:4660 | 5:0X:329 | Read+Write | Always
MSA_BM_Bombas_AC_A_Geoterm.Manual_horario | 192.168.4.23:4660 | 5:0X:330 | Read+Write | Always
MSA_BM_Bombas_AC_A_Geoterm.Marcha_paro | 192.168.4.23:4660 | 5:0X:331 | Read+Write | Always
MSA_BM_Bombas_AC_A_Geoterm.Reset_horas | 192.168.4.23:4660 | 5:0X:332 | Read+Write | Always
MSA_BM_Bombas_ACS_P_Inf.Horario_A | 192.168.4.23:4660 | 5:3X:849T80 | Read+Write | Always
MSA_BM_Bombas_ACS_P_Inf.Horario_estado | 192.168.4.23:4660 | 5:0X:337 | Read+Write | Always
MSA_BM_Bombas_ACS_P_Inf.Manual_horario | 192.168.4.23:4660 | 5:0X:338 | Read+Write | Always
MSA_BM_Bombas_ACS_P_Inf.Marcha_paro | 192.168.4.23:4660 | 5:0X:339 | Read+Write | Always
MSA_BM_Bombas_ACS_P_Inf.Reset_horas | 192.168.4.23:4660 | 5:0X:340 | Read+Write | Always
MSA_BM_Bombas_ACS_P_Inf_1.Alarma_variador | 192.168.4.23:4660 | 5:0X:229 | Read+Write | Always
MSA_BM_Bombas_ACS_P_Inf_1.Estado | 192.168.4.23:4660 | 5:0X:219 | Read+Write | Always
MSA_BM_Bombas_ACS_P_Inf_1.Fallo | 192.168.4.23:4660 | 5:0X:341 | Read+Write | Always
MSA_BM_Bombas_ACS_P_Inf_1.Horas_funcionam | 192.168.4.23:4660 | 5:3X:760 | Read+Write | Always
MSA_BM_Bombas_ACS_P_Inf_1.Orden | 192.168.4.23:4660 | 5:0X:279 | Read+Write | Always
MSA_BM_Bombas_ACS_P_Inf_2.Alarma_variador | 192.168.4.23:4660 | 5:0X:231 | Read+Write | Always
MSA_BM_Bombas_ACS_P_Inf_2.Estado | 192.168.4.23:4660 | 5:0X:220 | Read+Write | Always
MSA_BM_Bombas_ACS_P_Inf_2.Fallo | 192.168.4.23:4660 | 5:0X:342 | Read+Write | Always
MSA_BM_Bombas_ACS_P_Inf_2.Horas_funcionam | 192.168.4.23:4660 | 5:3X:716 | Read+Write | Always
MSA_BM_Bombas_ACS_P_Inf_2.Orden | 192.168.4.23:4660 | 5:0X:280 | Read+Write | Always
MSA_BM_Bombas_ACS_PB.Horario_A | 192.168.4.23:4660 | 5:3X:805T80 | Read+Write | Always
MSA_BM_Bombas_ACS_PB.Horario_estado | 192.168.4.23:4660 | 5:0X:345 | Read+Write | Always
MSA_BM_Bombas_ACS_PB.Manual_horario | 192.168.4.23:4660 | 5:0X:346 | Read+Write | Always
MSA_BM_Bombas_ACS_PB.Marcha_paro | 192.168.4.23:4660 | 5:0X:347 | Read+Write | Always
MSA_BM_Bombas_ACS_PB.Reset_horas | 192.168.4.23:4660 | 5:0X:348 | Read+Write | Always
MSA_BM_Bombas_ACS_PB_1.Alarma_variador | 192.168.4.23:4660 | 5:0X:206 | Read+Write | Always
MSA_BM_Bombas_ACS_PB_1.Estado | 192.168.4.23:4660 | 5:0X:217 | Read+Write | Always
MSA_BM_Bombas_ACS_PB_1.Fallo | 192.168.4.23:4660 | 5:0X:349 | Read+Write | Always
MSA_BM_Bombas_ACS_PB_1.Horas_funcionam | 192.168.4.23:4660 | 5:3X:672 | Read+Write | Always
MSA_BM_Bombas_ACS_PB_1.Orden | 192.168.4.23:4660 | 5:0X:277 | Read+Write | Always
MSA_BM_Bombas_ACS_PB_2.Alarma_variador | 192.168.4.23:4660 | 5:0X:207 | Read+Write | Always
MSA_BM_Bombas_ACS_PB_2.Estado | 192.168.4.23:4660 | 5:0X:218 | Read+Write | Always
MSA_BM_Bombas_ACS_PB_2.Fallo | 192.168.4.23:4660 | 5:0X:350 | Read+Write | Always
MSA_BM_Bombas_ACS_PB_2.Horas_funcionam | 192.168.4.23:4660 | 5:3X:628 | Read+Write | Always
MSA_BM_Bombas_ACS_PB_2.Orden | 192.168.4.23:4660 | 5:0X:278 | Read+Write | Always
MSA_BM_Bombas_AF_A_Geoterm.Horario_A | 192.168.4.23:4660 | 5:3X:761T80 | Read+Write | Always
MSA_BM_Bombas_AF_A_Geoterm.Horario_estado | 192.168.4.23:4660 | 5:0X:353 | Read+Write | Always
MSA_BM_Bombas_AF_A_Geoterm.Manual_horario | 192.168.4.23:4660 | 5:0X:354 | Read+Write | Always
MSA_BM_Bombas_AF_A_Geoterm.Marcha_paro | 192.168.4.23:4660 | 5:0X:355 | Read+Write | Always
MSA_BM_Bombas_AF_A_Geoterm.Reset_horas | 192.168.4.23:4660 | 5:0X:356 | Read+Write | Always
MSA_BM_Bombas_calor_Fallo | 192.168.4.23:4660 | 4:0X:381 | Read+Write | Always
MSA_BM_Bombas_calor_Interruptor_flujo | 192.168.4.23:4660 | 5:0X:232 | Read+Write | Always
MSA_BM_Bombas_calor_Orden | 192.168.4.23:4660 | 4:0X:275 | Read+Write | Always
MSA_BM_Bombas_calor_Presostato_maxima | 192.168.4.23:4660 | 5:0X:238 | Read+Write | Always
MSA_BM_Bombas_calor_Presostato_minima | 192.168.4.23:4660 | 5:0X:239 | Read+Write | Always
MSA_BM_Bombas_Condens_Fallo | 192.168.4.23:4660 | 4:0X:377 | Read+Write | Always
MSA_BM_Bombas_Condens_Interruptor_flujo | 192.168.4.23:4660 | 5:0X:208 | Read+Write | Always
MSA_BM_Bombas_Condens_Orden | 192.168.4.23:4660 | 4:0X:269 | Read+Write | Always
MSA_BM_Bombas_Condens_Presostato_maxima | 192.168.4.23:4660 | 5:0X:234 | Read+Write | Always
MSA_BM_Bombas_Condens_Presostato_minima | 192.168.4.23:4660 | 5:0X:235 | Read+Write | Always
MSA_BM_Bombas_frio_Fallo | 192.168.4.23:4660 | 4:0X:379 | Read+Write | Always
MSA_BM_Bombas_frio_Interruptor_flujo | 192.168.4.23:4660 | 5:0X:230 | Read+Write | Always
MSA_BM_Bombas_frio_Orden | 192.168.4.23:4660 | 4:0X:273 | Read+Write | Always
MSA_BM_Bombas_frio_Presostato_maxima | 192.168.4.23:4660 | 5:0X:236 | Read+Write | Always
MSA_BM_Bombas_frio_Presostato_minima | 192.168.4.23:4660 | 5:0X:233 | Read+Write | Always
MSA_BM_Bombas_UTAS.Horario_A | 192.168.4.23:4660 | 5:3X:937T80 | Read+Write | Always
MSA_BM_Bombas_UTAS.Horario_estado | 192.168.4.23:4660 | 5:0X:313 | Read+Write | Always
MSA_BM_Bombas_UTAS.Manual_horario | 192.168.4.23:4660 | 5:0X:314 | Read+Write | Always
MSA_BM_Bombas_UTAS.Marcha_paro | 192.168.4.23:4660 | 5:0X:315 | Read+Write | Always
MSA_BM_Bombas_UTAS.Reset_horas | 192.168.4.23:4660 | 5:0X:316 | Read+Write | Always
MSA_BM_Bombas_UTAS_AC_1.Alarma_variador | 192.168.4.23:4660 | 5:0X:225 | Read+Write | Always
MSA_BM_Bombas_UTAS_AC_1.Estado | 192.168.4.23:4660 | 5:0X:221 | Read+Write | Always
MSA_BM_Bombas_UTAS_AC_1.Fallo | 192.168.4.23:4660 | 5:0X:318 | Read+Write | Always
MSA_BM_Bombas_UTAS_AC_1.Horas_funcionam | 192.168.4.23:4660 | 5:3X:1024 | Read+Write | Always
MSA_BM_Bombas_UTAS_AC_1.Orden | 192.168.4.23:4660 | 5:0X:281 | Read+Write | Always
MSA_BM_Bombas_UTAS_AC_2.Alarma_variador | 192.168.4.23:4660 | 5:0X:226 | Read+Write | Always
MSA_BM_Bombas_UTAS_AC_2.Estado | 192.168.4.23:4660 | 5:0X:222 | Read+Write | Always
MSA_BM_Bombas_UTAS_AC_2.Fallo | 192.168.4.23:4660 | 5:0X:319 | Read+Write | Always
MSA_BM_Bombas_UTAS_AC_2.Horas_funcionam | 192.168.4.23:4660 | 5:3X:980 | Read+Write | Always
MSA_BM_Bombas_UTAS_AC_2.Orden | 192.168.4.23:4660 | 5:0X:282 | Read+Write | Always
MSA_BM_Bombas_UTAS_AF_1.Alarma_variador | 192.168.4.23:4660 | 5:0X:227 | Read+Write | Always
MSA_BM_Bombas_UTAS_AF_1.Estado | 192.168.4.23:4660 | 5:0X:202 | Read+Write | Always
MSA_BM_Bombas_UTAS_AF_1.Fallo | 192.168.4.23:4660 | 5:0X:326 | Read+Write | Always
MSA_BM_Bombas_UTAS_AF_1.Horas_funcionam | 192.168.4.23:4660 | 5:3X:936 | Read+Write | Always
MSA_BM_Bombas_UTAS_AF_1.Orden | 192.168.4.23:4660 | 5:0X:273 | Read+Write | Always
MSA_BM_Bombas_UTAS_AF_2.Alarma_variador | 192.168.4.23:4660 | 5:0X:228 | Read+Write | Always
MSA_BM_Bombas_UTAS_AF_2.Estado | 192.168.4.23:4660 | 5:0X:203 | Read+Write | Always
MSA_BM_Bombas_UTAS_AF_2.Fallo | 192.168.4.23:4660 | 5:0X:327 | Read+Write | Always
MSA_BM_Bombas_UTAS_AF_2.Horas_funcionam | 192.168.4.23:4660 | 5:3X:892 | Read+Write | Always
MSA_BM_Bombas_UTAS_AF_2.Orden | 192.168.4.23:4660 | 5:0X:274 | Read+Write | Always
MSA_BM_Cl_ESD.Estado_maquina | 192.168.4.23:4660 | 1:0X:236 | Read+Write | Always
MSA_BM_Cl_ESD.Estado_recuperador | 192.168.4.23:4660 | 1:0X:252 | Read+Write | Always
MSA_BM_Cl_ESD.Estado_vent_imp | 192.168.4.23:4660 | 1:0X:231 | Read+Write | Always
MSA_BM_Cl_ESD.Estado_vent_ret | 192.168.4.23:4660 | 1:0X:232 | Read+Write | Always
MSA_BM_Cl_ESD.Fallo_maquina | 192.168.4.23:4660 | 1:0X:344 | Read+Write | Always
MSA_BM_Cl_ESD.Fallo_recuperador | 192.168.4.23:4660 | 1:0X:343 | Read+Write | Always
MSA_BM_Cl_ESD.Fallo_vent_imp | 192.168.4.23:4660 | 1:0X:341 | Read+Write | Always
MSA_BM_Cl_ESD.Fallo_vent_ret | 192.168.4.23:4660 | 1:0X:342 | Read+Write | Always
MSA_BM_Cl_ESD.Filtro_imp | 192.168.4.23:4660 | 1:0X:207 | Read+Write | Always
MSA_BM_Cl_ESD.Filtro_recuperador | 192.168.4.23:4660 | 1:0X:244 | Read+Write | Always
MSA_BM_Cl_ESD.Filtro_ret | 192.168.4.23:4660 | 1:0X:208 | Read+Write | Always
MSA_BM_Cl_ESD.Horario_A | 192.168.4.23:4660 | 1:3X:849T80 | Read+Write | Always
MSA_BM_Cl_ESD.Horario_estado | 192.168.4.23:4660 | 1:0X:337 | Read+Write | Always
MSA_BM_Cl_ESD.Horas_funcionam | 192.168.4.23:4660 | 1:3X:892 | Read+Write | Always
MSA_BM_Cl_ESD.Manual_horario | 192.168.4.23:4660 | 1:0X:338 | Read+Write | Always
MSA_BM_Cl_ESD.Marcha_paro | 192.168.4.23:4660 | 1:0X:339 | Read+Write | Always
MSA_BM_Cl_ESD.Orden_humectador | 192.168.4.23:4660 | 1:0X:286 | Read+Write | Always
MSA_BM_Cl_ESD.Orden_maquina | 192.168.4.23:4660 | 1:0X:278 | Read+Write | Always
MSA_BM_Cl_ESD.Orden_recuperador | 192.168.4.23:4660 | 1:0X:282 | Read+Write | Always
MSA_BM_Cl_ESD.Orden_vent_imp | 192.168.4.23:4660 | 1:0X:273 | Read+Write | Always
MSA_BM_Cl_ESD.Orden_vent_ret | 192.168.4.23:4660 | 1:0X:274 | Read+Write | Always
MSA_BM_Cl_ESD.Presostato_vent_imp | 192.168.4.23:4660 | 1:0X:223 | Read+Write | Always
MSA_BM_Cl_ESD.Presostato_vent_ret | 192.168.4.23:4660 | 1:0X:224 | Read+Write | Always
MSA_BM_Cl_ESD.Reset_horas | 192.168.4.23:4660 | 1:0X:340 | Read+Write | Always
MSA_BM_Cl_ESE.Estado_maquina | 192.168.4.23:4660 | 1:0X:233 | Read+Write | Always
MSA_BM_Cl_ESE.Estado_recuperador | 192.168.4.23:4660 | 1:0X:249 | Read+Write | Always
MSA_BM_Cl_ESE.Estado_vent_imp | 192.168.4.23:4660 | 1:0X:225 | Read+Write | Always
MSA_BM_Cl_ESE.Estado_vent_ret | 192.168.4.23:4660 | 1:0X:226 | Read+Write | Always
MSA_BM_Cl_ESE.Fallo_maquina | 192.168.4.23:4660 | 1:0X:320 | Read+Write | Always
MSA_BM_Cl_ESE.Fallo_recuperador | 192.168.4.23:4660 | 1:0X:319 | Read+Write | Always
MSA_BM_Cl_ESE.Fallo_vent_imp | 192.168.4.23:4660 | 1:0X:317 | Read+Write | Always
MSA_BM_Cl_ESE.Fallo_vent_ret | 192.168.4.23:4660 | 1:0X:318 | Read+Write | Always
MSA_BM_Cl_ESE.Filtro_imp | 192.168.4.23:4660 | 1:0X:201 | Read+Write | Always
MSA_BM_Cl_ESE.Filtro_recuperador | 192.168.4.23:4660 | 1:0X:241 | Read+Write | Always
MSA_BM_Cl_ESE.Filtro_ret | 192.168.4.23:4660 | 1:0X:202 | Read+Write | Always
MSA_BM_Cl_ESE.Horario_A | 192.168.4.23:4660 | 1:3X:981T80 | Read+Write | Always
MSA_BM_Cl_ESE.Horario_estado | 192.168.4.23:4660 | 1:0X:313 | Read+Write | Always
MSA_BM_Cl_ESE.Horas_funcionam | 192.168.4.23:4660 | 1:3X:1024 | Read+Write | Always
MSA_BM_Cl_ESE.Manual_horario | 192.168.4.23:4660 | 1:0X:314 | Read+Write | Always
MSA_BM_Cl_ESE.Marcha_paro | 192.168.4.23:4660 | 1:0X:315 | Read+Write | Always
MSA_BM_Cl_ESE.Orden_humectador | 192.168.4.23:4660 | 1:0X:283 | Read+Write | Always
MSA_BM_Cl_ESE.Orden_maquina | 192.168.4.23:4660 | 1:0X:275 | Read+Write | Always
MSA_BM_Cl_ESE.Orden_recuperador | 192.168.4.23:4660 | 1:0X:279 | Read+Write | Always
MSA_BM_Cl_ESE.Orden_vent_imp | 192.168.4.23:4660 | 1:0X:265 | Read+Write | Always
MSA_BM_Cl_ESE.Orden_vent_ret | 192.168.4.23:4660 | 1:0X:266 | Read+Write | Always
MSA_BM_Cl_ESE.Presostato_vent_imp | 192.168.4.23:4660 | 1:0X:217 | Read+Write | Always
MSA_BM_Cl_ESE.Presostato_vent_ret | 192.168.4.23:4660 | 1:0X:218 | Read+Write | Always
MSA_BM_Cl_ESE.Reset_horas | 192.168.4.23:4660 | 1:0X:316 | Read+Write | Always
MSA_BM_Cl_MFZCA.Estado_maquina | 192.168.4.23:4660 | 1:0X:235 | Read+Write | Always
MSA_BM_Cl_MFZCA.Estado_recuperador | 192.168.4.23:4660 | 1:0X:251 | Read+Write | Always
MSA_BM_Cl_MFZCA.Estado_vent_imp | 192.168.4.23:4660 | 1:0X:229 | Read+Write | Always
MSA_BM_Cl_MFZCA.Estado_vent_ret | 192.168.4.23:4660 | 1:0X:230 | Read+Write | Always
MSA_BM_Cl_MFZCA.Fallo_maquina | 192.168.4.23:4660 | 1:0X:336 | Read+Write | Always
MSA_BM_Cl_MFZCA.Fallo_recuperador | 192.168.4.23:4660 | 1:0X:335 | Read+Write | Always
MSA_BM_Cl_MFZCA.Fallo_vent_imp | 192.168.4.23:4660 | 1:0X:333 | Read+Write | Always
MSA_BM_Cl_MFZCA.Fallo_vent_ret | 192.168.4.23:4660 | 1:0X:334 | Read+Write | Always
MSA_BM_Cl_MFZCA.Filtro_imp | 192.168.4.23:4660 | 1:0X:205 | Read+Write | Always
MSA_BM_Cl_MFZCA.Filtro_recuperador | 192.168.4.23:4660 | 1:0X:243 | Read+Write | Always
MSA_BM_Cl_MFZCA.Filtro_ret | 192.168.4.23:4660 | 1:0X:206 | Read+Write | Always
MSA_BM_Cl_MFZCA.Horario_A | 192.168.4.23:4660 | 1:3X:893T80 | Read+Write | Always
MSA_BM_Cl_MFZCA.Horario_estado | 192.168.4.23:4660 | 1:0X:329 | Read+Write | Always
MSA_BM_Cl_MFZCA.Horas_funcionam | 192.168.4.23:4660 | 1:3X:936 | Read+Write | Always
MSA_BM_Cl_MFZCA.Manual_horario | 192.168.4.23:4660 | 1:0X:330 | Read+Write | Always
MSA_BM_Cl_MFZCA.Marcha_paro | 192.168.4.23:4660 | 1:0X:331 | Read+Write | Always
MSA_BM_Cl_MFZCA.Orden_humectador | 192.168.4.23:4660 | 1:0X:285 | Read+Write | Always
MSA_BM_Cl_MFZCA.Orden_maquina | 192.168.4.23:4660 | 1:0X:277 | Read+Write | Always
MSA_BM_Cl_MFZCA.Orden_recuperador | 192.168.4.23:4660 | 1:0X:281 | Read+Write | Always
MSA_BM_Cl_MFZCA.Orden_vent_imp | 192.168.4.23:4660 | 1:0X:269 | Read+Write | Always
MSA_BM_Cl_MFZCA.Orden_vent_ret | 192.168.4.23:4660 | 1:0X:270 | Read+Write | Always
MSA_BM_Cl_MFZCA.Presostato_vent_imp | 192.168.4.23:4660 | 1:0X:221 | Read+Write | Always
MSA_BM_Cl_MFZCA.Presostato_vent_ret | 192.168.4.23:4660 | 1:0X:222 | Read+Write | Always
MSA_BM_Cl_MFZCA.Reset_horas | 192.168.4.23:4660 | 1:0X:332 | Read+Write | Always
MSA_BM_Cl_MFZCE.Estado_maquina | 192.168.4.23:4660 | 1:0X:234 | Read+Write | Always
MSA_BM_Cl_MFZCE.Estado_recuperador | 192.168.4.23:4660 | 1:0X:250 | Read+Write | Always
MSA_BM_Cl_MFZCE.Estado_vent_imp | 192.168.4.23:4660 | 1:0X:227 | Read+Write | Always
MSA_BM_Cl_MFZCE.Estado_vent_ret | 192.168.4.23:4660 | 1:0X:228 | Read+Write | Always
MSA_BM_Cl_MFZCE.Fallo_maquina | 192.168.4.23:4660 | 1:0X:328 | Read+Write | Always
MSA_BM_Cl_MFZCE.Fallo_recuperador | 192.168.4.23:4660 | 1:0X:327 | Read+Write | Always
MSA_BM_Cl_MFZCE.Fallo_vent_imp | 192.168.4.23:4660 | 1:0X:325 | Read+Write | Always
MSA_BM_Cl_MFZCE.Fallo_vent_ret | 192.168.4.23:4660 | 1:0X:326 | Read+Write | Always
MSA_BM_Cl_MFZCE.Filtro_imp | 192.168.4.23:4660 | 1:0X:203 | Read+Write | Always
MSA_BM_Cl_MFZCE.Filtro_recuperador | 192.168.4.23:4660 | 1:0X:242 | Read+Write | Always
MSA_BM_Cl_MFZCE.Filtro_ret | 192.168.4.23:4660 | 1:0X:204 | Read+Write | Always
MSA_BM_Cl_MFZCE.Horario_A | 192.168.4.23:4660 | 1:3X:937T80 | Read+Write | Always
MSA_BM_Cl_MFZCE.Horario_estado | 192.168.4.23:4660 | 1:0X:321 | Read+Write | Always
MSA_BM_Cl_MFZCE.Horas_funcionam | 192.168.4.23:4660 | 1:3X:980 | Read+Write | Always
MSA_BM_Cl_MFZCE.Manual_horario | 192.168.4.23:4660 | 1:0X:322 | Read+Write | Always
MSA_BM_Cl_MFZCE.Marcha_paro | 192.168.4.23:4660 | 1:0X:323 | Read+Write | Always
MSA_BM_Cl_MFZCE.Orden_humectador | 192.168.4.23:4660 | 1:0X:284 | Read+Write | Always
MSA_BM_Cl_MFZCE.Orden_maquina | 192.168.4.23:4660 | 1:0X:276 | Read+Write | Always
MSA_BM_Cl_MFZCE.Orden_recuperador | 192.168.4.23:4660 | 1:0X:280 | Read+Write | Always
MSA_BM_Cl_MFZCE.Orden_vent_imp | 192.168.4.23:4660 | 1:0X:267 | Read+Write | Always
MSA_BM_Cl_MFZCE.Orden_vent_ret | 192.168.4.23:4660 | 1:0X:268 | Read+Write | Always
MSA_BM_Cl_MFZCE.Presostato_vent_imp | 192.168.4.23:4660 | 1:0X:219 | Read+Write | Always
MSA_BM_Cl_MFZCE.Presostato_vent_ret | 192.168.4.23:4660 | 1:0X:220 | Read+Write | Always
MSA_BM_Cl_MFZCE.Reset_horas | 192.168.4.23:4660 | 1:0X:324 | Read+Write | Always
MSA_BM_depositos_inercia_AC_Termostato_seg_1 | 192.168.4.23:4660 | 5:0X:242 | Read+Write | Always
MSA_BM_depositos_inercia_AC_Termostato_seg_2 | 192.168.4.23:4660 | 5:0X:243 | Read+Write | Always
MSA_BM_depositos_inercia_AF_Termostato_seg_1 | 192.168.4.23:4660 | 5:0X:240 | Read+Write | Always
MSA_BM_depositos_inercia_AF_Termostato_seg_2 | 192.168.4.23:4660 | 5:0X:241 | Read+Write | Always
MSA_BM_Produccion.Horario_A | 192.168.4.23:4660 | 4:3X:981T80 | Read+Write | Always
MSA_BM_Produccion.Horario_estado | 192.168.4.23:4660 | 4:0X:361 | Read+Write | Always
MSA_BM_Produccion.Manual_horario | 192.168.4.23:4660 | 4:0X:362 | Read+Write | Always
MSA_BM_Produccion.Marcha_paro | 192.168.4.23:4660 | 4:0X:363 | Read+Write | Always
MSA_BM_Produccion.Reset_horas | 192.168.4.23:4660 | 4:0X:364 | Read+Write | Always
MSA_BM_Produccion_Arrancar_maquina | 192.168.4.23:4660 | 4:0X:365 | Read+Write | Always
MSA_BM_Produccion_Estado_maquina | 192.168.4.23:4660 | 5:0X:201 | Read | Always
MSA_BM_Produccion_Orden_maquina | 192.168.4.23:4660 | 5:0X:287 | Read+Write | Always
MSA_BM_UTAS_IV_Bombas_paradas | 192.168.4.23:4660 | 5:0X:325 | Read+Write | Always
MSA_BM_UTAS_IV_Cambiando | 192.168.4.23:4660 | 5:0X:324 | Read+Write | Always
MSA_BM_UTAS_IV_Cambio_Bombas | 192.168.4.23:4660 | 5:0X:317 | Read+Write | Always
MSA_BM_UTAS_IV_Cambio_Valvulas | 192.168.4.23:4660 | 4:0X:328 | Read+Write | Always
MSA_BM_UTAS_IV_Valvulas_en_Posicion | 192.168.4.23:4660 | 4:0X:327 | Read+Write | Always
MSA_BM_valv_UTAS_AC_Impuls.Estado_abierta | 192.168.4.23:4660 | 4:0X:229 | Read+Write | Always
MSA_BM_valv_UTAS_AC_Impuls.Estado_cerrada | 192.168.4.23:4660 | 4:0X:230 | Read+Write | Always
MSA_BM_valv_UTAS_AC_Impuls.Fallo | 192.168.4.23:4660 | 4:0X:322 | Read+Write | Always
MSA_BM_valv_UTAS_AC_Impuls.Orden_abrir | 192.168.4.23:4660 | 4:0X:279 | Read+Write | Always
MSA_BM_valv_UTAS_AC_Retorno.Estado_abierta | 192.168.4.23:4660 | 4:0X:227 | Read+Write | Always
MSA_BM_valv_UTAS_AC_Retorno.Estado_cerrada | 192.168.4.23:4660 | 4:0X:228 | Read+Write | Always
MSA_BM_valv_UTAS_AC_Retorno.Fallo | 192.168.4.23:4660 | 4:0X:323 | Read+Write | Always
MSA_BM_valv_UTAS_AC_Retorno.Orden_abrir | 192.168.4.23:4660 | 4:0X:280 | Read+Write | Always
MSA_BM_valv_UTAS_AF_Impuls.Estado_abierta | 192.168.4.23:4660 | 4:0X:225 | Read+Write | Always
MSA_BM_valv_UTAS_AF_Impuls.Estado_cerrada | 192.168.4.23:4660 | 4:0X:226 | Read+Write | Always
MSA_BM_valv_UTAS_AF_Impuls.Fallo | 192.168.4.23:4660 | 4:0X:324 | Read+Write | Always
MSA_BM_valv_UTAS_AF_Impuls.Orden_abrir | 192.168.4.23:4660 | 4:0X:277 | Read+Write | Always
MSA_BM_valv_UTAS_AF_Retorno.Estado_abierta | 192.168.4.23:4660 | 4:0X:223 | Read+Write | Always
MSA_BM_valv_UTAS_AF_Retorno.Estado_cerrada | 192.168.4.23:4660 | 4:0X:224 | Read+Write | Always
MSA_BM_valv_UTAS_AF_Retorno.Fallo | 192.168.4.23:4660 | 4:0X:325 | Read+Write | Always
MSA_BM_valv_UTAS_AF_Retorno.Orden_abrir | 192.168.4.23:4660 | 4:0X:278 | Read+Write | Always
MSA_BM_VM_Condens_1.Estado_abierta | 192.168.4.23:4660 | 4:0X:201 | Read+Write | Always
MSA_BM_VM_Condens_1.Fallo | 192.168.4.23:4660 | 4:0X:369 | Read+Write | Always
MSA_BM_VM_Condens_1.Orden_abrir | 192.168.4.23:4660 | 4:0X:265 | Read+Write | Always
MSA_BM_VM_Condens_2.Estado_abierta | 192.168.4.23:4660 | 4:0X:202 | Read+Write | Always
MSA_BM_VM_Condens_2.Fallo | 192.168.4.23:4660 | 4:0X:370 | Read+Write | Always
MSA_BM_VM_Condens_2.Orden_abrir | 192.168.4.23:4660 | 4:0X:266 | Read+Write | Always
MSA_BM_VM_Condens_3.Estado_abierta | 192.168.4.23:4660 | 4:0X:203 | Read+Write | Always
MSA_BM_VM_Condens_3.Fallo | 192.168.4.23:4660 | 4:0X:371 | Read+Write | Always
MSA_BM_VM_Condens_3.Orden_abrir | 192.168.4.23:4660 | 4:0X:267 | Read+Write | Always
MSA_BM_VM_Condens_4.Estado_abierta | 192.168.4.23:4660 | 4:0X:204 | Read+Write | Always
MSA_BM_VM_Condens_4.Fallo | 192.168.4.23:4660 | 4:0X:372 | Read+Write | Always
MSA_BM_VM_Condens_4.Orden_abrir | 192.168.4.23:4660 | 4:0X:268 | Read+Write | Always
MSA_BT_Alumb_Acces_testa.Estado | 192.168.4.33:4660 | 2:0X:218 | Read+Write | Always
MSA_BT_Alumb_Acces_testa.Fallo | 192.168.4.33:4660 | 2:0X:389 | Read+Write | Always
MSA_BT_Alumb_Acces_testa.Horario_A | 192.168.4.33:4660 | 2:3X:585T80 | Read+Write | Always
MSA_BT_Alumb_Acces_testa.Horario_estado | 192.168.4.33:4660 | 2:0X:385 | Read+Write | Always
MSA_BT_Alumb_Acces_testa.Manual_horario | 192.168.4.33:4660 | 2:0X:386 | Read+Write | Always
MSA_BT_Alumb_Acces_testa.Marcha_paro | 192.168.4.33:4660 | 2:0X:387 | Read+Write | Always
MSA_BT_Alumb_Acces_testa.Orden | 192.168.4.33:4660 | 2:0X:276 | Read+Write | Always
MSA_BT_Alumb_Accesos_dreta.Estado | 192.168.4.33:4660 | 2:0X:217 | Read+Write | Always
MSA_BT_Alumb_Accesos_dreta.Fallo | 192.168.4.33:4660 | 2:0X:381 | Read+Write | Always
MSA_BT_Alumb_Accesos_dreta.Horario_A | 192.168.4.33:4660 | 2:3X:629T80 | Read+Write | Always
MSA_BT_Alumb_Accesos_dreta.Horario_estado | 192.168.4.33:4660 | 2:0X:377 | Read+Write | Always
MSA_BT_Alumb_Accesos_dreta.Manual_horario | 192.168.4.33:4660 | 2:0X:378 | Read+Write | Always
MSA_BT_Alumb_Accesos_dreta.Marcha_paro | 192.168.4.33:4660 | 2:0X:379 | Read+Write | Always
MSA_BT_Alumb_Accesos_dreta.Orden | 192.168.4.33:4660 | 2:0X:275 | Read+Write | Always
MSA_BT_Alumb_Accesos_esquerra.Estado | 192.168.4.33:4660 | 2:0X:208 | Read+Write | Always
MSA_BT_Alumb_Accesos_esquerra.Fallo | 192.168.4.33:4660 | 2:0X:373 | Read+Write | Always
MSA_BT_Alumb_Accesos_esquerra.Horario_A | 192.168.4.33:4660 | 2:3X:673T80 | Read+Write | Always
MSA_BT_Alumb_Accesos_esquerra.Horario_estado | 192.168.4.33:4660 | 2:0X:369 | Read+Write | Always
MSA_BT_Alumb_Accesos_esquerra.Manual_horario | 192.168.4.33:4660 | 2:0X:370 | Read+Write | Always
MSA_BT_Alumb_Accesos_esquerra.Marcha_paro | 192.168.4.33:4660 | 2:0X:371 | Read+Write | Always
MSA_BT_Alumb_Accesos_esquerra.Orden | 192.168.4.33:4660 | 2:0X:274 | Read+Write | Always
MSA_BT_Alumb_Cocina.Estado | 192.168.4.33:4660 | 7:0X:204 | Read+Write | Always
MSA_BT_Alumb_Cocina.Fallo | 192.168.4.33:4660 | 7:0X:333 | Read+Write | Always
MSA_BT_Alumb_Cocina.Horario_A | 192.168.4.33:4660 | 7:3X:893T80 | Read+Write | Always
MSA_BT_Alumb_Cocina.Horario_estado | 192.168.4.33:4660 | 7:0X:329 | Read+Write | Always
MSA_BT_Alumb_Cocina.Manual_horario | 192.168.4.33:4660 | 7:0X:330 | Read+Write | Always
MSA_BT_Alumb_Cocina.Marcha_paro | 192.168.4.33:4660 | 7:0X:331 | Read+Write | Always
MSA_BT_Alumb_Cocina.Orden | 192.168.4.33:4660 | 7:0X:267 | Read+Write | Always
MSA_BT_Alumb_Encants_Dreta.Estado | 192.168.4.33:4660 | 2:0X:206 | Read+Write | Always
MSA_BT_Alumb_Encants_Dreta.Fallo | 192.168.4.33:4660 | 2:0X:357 | Read+Write | Always
MSA_BT_Alumb_Encants_Dreta.Horario_A | 192.168.4.33:4660 | 2:3X:761T80 | Read+Write | Always
MSA_BT_Alumb_Encants_Dreta.Horario_estado | 192.168.4.33:4660 | 2:0X:353 | Read+Write | Always
MSA_BT_Alumb_Encants_Dreta.Manual_horario | 192.168.4.33:4660 | 2:0X:354 | Read+Write | Always
MSA_BT_Alumb_Encants_Dreta.Marcha_paro | 192.168.4.33:4660 | 2:0X:355 | Read+Write | Always
MSA_BT_Alumb_Encants_Dreta.Orden | 192.168.4.33:4660 | 2:0X:270 | Read+Write | Always
MSA_BT_Alumb_Encants_Gral.Estado | 192.168.4.33:4660 | 2:0X:201 | Read+Write | Always
MSA_BT_Alumb_Encants_Gral.Fallo | 192.168.4.33:4660 | 2:0X:317 | Read+Write | Always
MSA_BT_Alumb_Encants_Gral.Horario_A | 192.168.4.33:4660 | 2:3X:981T80 | Read+Write | Always
MSA_BT_Alumb_Encants_Gral.Horario_estado | 192.168.4.33:4660 | 2:0X:313 | Read+Write | Always
MSA_BT_Alumb_Encants_Gral.Manual_horario | 192.168.4.33:4660 | 2:0X:314 | Read+Write | Always
MSA_BT_Alumb_Encants_Gral.Marcha_paro | 192.168.4.33:4660 | 2:0X:315 | Read+Write | Always
MSA_BT_Alumb_Encants_Gral.Orden | 192.168.4.33:4660 | 2:0X:265 | Read+Write | Always
MSA_BT_Alumb_Encants_Preferent.Estado | 192.168.4.33:4660 | 2:0X:202 | Read+Write | Always
MSA_BT_Alumb_Encants_Preferent.Fallo | 192.168.4.33:4660 | 2:0X:325 | Read+Write | Always
MSA_BT_Alumb_Encants_Preferent.Horario_A | 192.168.4.33:4660 | 2:3X:937T80 | Read+Write | Always
MSA_BT_Alumb_Encants_Preferent.Horario_estado | 192.168.4.33:4660 | 2:0X:321 | Read+Write | Always
MSA_BT_Alumb_Encants_Preferent.Manual_horario | 192.168.4.33:4660 | 2:0X:322 | Read+Write | Always
MSA_BT_Alumb_Encants_Preferent.Marcha_paro | 192.168.4.33:4660 | 2:0X:323 | Read+Write | Always
MSA_BT_Alumb_Encants_Preferent.Orden | 192.168.4.33:4660 | 2:0X:266 | Read+Write | Always
MSA_BT_Alumb_Escalera01.Estado | 192.168.4.33:4660 | 2:0X:219 | Read+Write | Always
MSA_BT_Alumb_Escalera01.Fallo | 192.168.4.33:4660 | 2:0X:397 | Read+Write | Always
MSA_BT_Alumb_Escalera01.Horario_A | 192.168.4.33:4660 | 2:3X:541T80 | Read+Write | Always
MSA_BT_Alumb_Escalera01.Horario_estado | 192.168.4.33:4660 | 2:0X:393 | Read+Write | Always
MSA_BT_Alumb_Escalera01.Manual_horario | 192.168.4.33:4660 | 2:0X:394 | Read+Write | Always
MSA_BT_Alumb_Escalera01.Marcha_paro | 192.168.4.33:4660 | 2:0X:395 | Read+Write | Always
MSA_BT_Alumb_Escalera01.Orden | 192.168.4.33:4660 | 2:0X:277 | Read+Write | Always
MSA_BT_Alumb_Escalera02.Estado | 192.168.4.33:4660 | 2:0X:220 | Read+Write | Always
MSA_BT_Alumb_Escalera02.Fallo | 192.168.4.33:4660 | 2:0X:405 | Read+Write | Always
MSA_BT_Alumb_Escalera02.Horario_A | 192.168.4.33:4660 | 2:3X:497T80 | Read+Write | Always
MSA_BT_Alumb_Escalera02.Horario_estado | 192.168.4.33:4660 | 2:0X:401 | Read+Write | Always
MSA_BT_Alumb_Escalera02.Manual_horario | 192.168.4.33:4660 | 2:0X:402 | Read+Write | Always
MSA_BT_Alumb_Escalera02.Marcha_paro | 192.168.4.33:4660 | 2:0X:403 | Read+Write | Always
MSA_BT_Alumb_Escalera02.Orden | 192.168.4.33:4660 | 2:0X:278 | Read+Write | Always
MSA_BT_Alumb_Fachada_3.Estado | 192.168.4.33:4660 | 3:0X:203 | Read+Write | Always
MSA_BT_Alumb_Fachada_3.Fallo | 192.168.4.33:4660 | 3:0X:333 | Read+Write | Always
MSA_BT_Alumb_Fachada_3.Horario_A | 192.168.4.33:4660 | 3:3X:893T80 | Read+Write | Always
MSA_BT_Alumb_Fachada_3.Horario_estado | 192.168.4.33:4660 | 3:0X:329 | Read+Write | Always
MSA_BT_Alumb_Fachada_3.Manual_horario | 192.168.4.33:4660 | 3:0X:330 | Read+Write | Always
MSA_BT_Alumb_Fachada_3.Marcha_paro | 192.168.4.33:4660 | 3:0X:331 | Read+Write | Always
MSA_BT_Alumb_Fachada_3.Orden | 192.168.4.33:4660 | 3:0X:267 | Read+Write | Always
MSA_BT_Alumb_Fachada_4.Estado | 192.168.4.33:4660 | 3:0X:204 | Read+Write | Always
MSA_BT_Alumb_Fachada_4.Fallo | 192.168.4.33:4660 | 3:0X:349 | Read+Write | Always
MSA_BT_Alumb_Fachada_4.Horario_A | 192.168.4.33:4660 | 3:3X:805T80 | Read+Write | Always
MSA_BT_Alumb_Fachada_4.Horario_estado | 192.168.4.33:4660 | 3:0X:345 | Read+Write | Always
MSA_BT_Alumb_Fachada_4.Manual_horario | 192.168.4.33:4660 | 3:0X:346 | Read+Write | Always
MSA_BT_Alumb_Fachada_4.Marcha_paro | 192.168.4.33:4660 | 3:0X:347 | Read+Write | Always
MSA_BT_Alumb_Fachada_4.Orden | 192.168.4.33:4660 | 3:0X:268 | Read+Write | Always
MSA_BT_Alumb_general_1.Estado | 192.168.4.33:4660 | 10:0X:222 | Read+Write | Always
MSA_BT_Alumb_general_1.Fallo | 192.168.4.33:4660 | 10:0X:389 | Read+Write | Always
MSA_BT_Alumb_general_1.Horario_A | 192.168.4.33:4660 | 10:3X:585T80 | Read+Write | Always
MSA_BT_Alumb_general_1.Horario_estado | 192.168.4.33:4660 | 10:0X:385 | Read+Write | Always
MSA_BT_Alumb_general_1.Manual_horario | 192.168.4.33:4660 | 10:0X:386 | Read+Write | Always
MSA_BT_Alumb_general_1.Marcha_paro | 192.168.4.33:4660 | 10:0X:387 | Read+Write | Always
MSA_BT_Alumb_general_1.Orden | 192.168.4.33:4660 | 10:0X:276 | Read+Write | Always
MSA_BT_Alumb_general_2.Estado | 192.168.4.33:4660 | 10:0X:223 | Read+Write | Always
MSA_BT_Alumb_general_2.Fallo | 192.168.4.33:4660 | 10:0X:397 | Read+Write | Always
MSA_BT_Alumb_general_2.Horario_A | 192.168.4.33:4660 | 10:3X:541T80 | Read+Write | Always
MSA_BT_Alumb_general_2.Horario_estado | 192.168.4.33:4660 | 10:0X:393 | Read+Write | Always
MSA_BT_Alumb_general_2.Manual_horario | 192.168.4.33:4660 | 10:0X:394 | Read+Write | Always
MSA_BT_Alumb_general_2.Marcha_paro | 192.168.4.33:4660 | 10:0X:395 | Read+Write | Always
MSA_BT_Alumb_general_2.Orden | 192.168.4.33:4660 | 10:0X:277 | Read+Write | Always
MSA_BT_Alumb_General_Estado | 192.168.4.33:4660 | 10:0X:225 | Read+Write | Always
MSA_BT_Alumb_Marquesina_1.Estado | 192.168.4.33:4660 | 3:0X:201 | Read+Write | Always
MSA_BT_Alumb_Marquesina_1.Fallo | 192.168.4.33:4660 | 3:0X:317 | Read+Write | Always
MSA_BT_Alumb_Marquesina_1.Horario_A | 192.168.4.33:4660 | 3:3X:981T80 | Read+Write | Always
MSA_BT_Alumb_Marquesina_1.Horario_estado | 192.168.4.33:4660 | 3:0X:313 | Read+Write | Always
MSA_BT_Alumb_Marquesina_1.Manual_horario | 192.168.4.33:4660 | 3:0X:314 | Read+Write | Always
MSA_BT_Alumb_Marquesina_1.Marcha_paro | 192.168.4.33:4660 | 3:0X:315 | Read+Write | Always
MSA_BT_Alumb_Marquesina_1.Orden | 192.168.4.33:4660 | 3:0X:265 | Read+Write | Always
MSA_BT_Alumb_Marquesina_2.Estado | 192.168.4.33:4660 | 3:0X:202 | Read+Write | Always
MSA_BT_Alumb_Marquesina_2.Fallo | 192.168.4.33:4660 | 3:0X:325 | Read+Write | Always
MSA_BT_Alumb_Marquesina_2.Horario_A | 192.168.4.33:4660 | 3:3X:937T80 | Read+Write | Always
MSA_BT_Alumb_Marquesina_2.Horario_estado | 192.168.4.33:4660 | 3:0X:321 | Read+Write | Always
MSA_BT_Alumb_Marquesina_2.Manual_horario | 192.168.4.33:4660 | 3:0X:322 | Read+Write | Always
MSA_BT_Alumb_Marquesina_2.Marcha_paro | 192.168.4.33:4660 | 3:0X:323 | Read+Write | Always
MSA_BT_Alumb_Marquesina_2.Orden | 192.168.4.33:4660 | 3:0X:266 | Read+Write | Always
MSA_BT_Alumb_Pergolas_Carrer_1.Estado | 192.168.4.33:4660 | 1:0X:257 | Read+Write | Always
MSA_BT_Alumb_Pergolas_Carrer_1.Fallo | 192.168.4.33:4660 | 1:0X:397 | Read+Write | Always
MSA_BT_Alumb_Pergolas_Carrer_1.Horario_A | 192.168.4.33:4660 | 1:3X:541T80 | Read+Write | Always
MSA_BT_Alumb_Pergolas_Carrer_1.Horario_estado | 192.168.4.33:4660 | 1:0X:393 | Read+Write | Always
MSA_BT_Alumb_Pergolas_Carrer_1.Manual_horario | 192.168.4.33:4660 | 1:0X:394 | Read+Write | Always
MSA_BT_Alumb_Pergolas_Carrer_1.Marcha_paro | 192.168.4.33:4660 | 1:0X:395 | Read+Write | Always
MSA_BT_Alumb_Pergolas_Carrer_1.Orden | 192.168.4.33:4660 | 1:0X:301 | Read+Write | Always
MSA_BT_Alumb_Pergolas_Carrer_2.Estado | 192.168.4.33:4660 | 1:0X:258 | Read+Write | Always
MSA_BT_Alumb_Pergolas_Carrer_2.Fallo | 192.168.4.33:4660 | 1:0X:405 | Read+Write | Always
MSA_BT_Alumb_Pergolas_Carrer_2.Horario_A | 192.168.4.33:4660 | 1:3X:497T80 | Read+Write | Always
MSA_BT_Alumb_Pergolas_Carrer_2.Horario_estado | 192.168.4.33:4660 | 1:0X:401 | Read+Write | Always
MSA_BT_Alumb_Pergolas_Carrer_2.Manual_horario | 192.168.4.33:4660 | 1:0X:402 | Read+Write | Always
MSA_BT_Alumb_Pergolas_Carrer_2.Marcha_paro | 192.168.4.33:4660 | 1:0X:403 | Read+Write | Always
MSA_BT_Alumb_Pergolas_Carrer_2.Orden | 192.168.4.33:4660 | 1:0X:302 | Read+Write | Always
MSA_BT_Alumb_Pergolas_Tamarit_1.Estado | 192.168.4.33:4660 | 1:0X:259 | Read+Write | Always
MSA_BT_Alumb_Pergolas_Tamarit_1.Fallo | 192.168.4.33:4660 | 1:0X:413 | Read+Write | Always
MSA_BT_Alumb_Pergolas_Tamarit_1.Horario_A | 192.168.4.33:4660 | 1:3X:453T80 | Read+Write | Always
MSA_BT_Alumb_Pergolas_Tamarit_1.Horario_estado | 192.168.4.33:4660 | 1:0X:409 | Read+Write | Always
MSA_BT_Alumb_Pergolas_Tamarit_1.Manual_horario | 192.168.4.33:4660 | 1:0X:410 | Read+Write | Always
MSA_BT_Alumb_Pergolas_Tamarit_1.Marcha_paro | 192.168.4.33:4660 | 1:0X:411 | Read+Write | Always
MSA_BT_Alumb_Pergolas_Tamarit_1.Orden | 192.168.4.33:4660 | 1:0X:303 | Read+Write | Always
MSA_BT_Alumb_Pergolas_Tamarit_2.Estado | 192.168.4.33:4660 | 1:0X:260 | Read+Write | Always
MSA_BT_Alumb_Pergolas_Tamarit_2.Fallo | 192.168.4.33:4660 | 1:0X:421 | Read+Write | Always
MSA_BT_Alumb_Pergolas_Tamarit_2.Horario_A | 192.168.4.33:4660 | 1:3X:409T80 | Read+Write | Always
MSA_BT_Alumb_Pergolas_Tamarit_2.Horario_estado | 192.168.4.33:4660 | 1:0X:417 | Read+Write | Always
MSA_BT_Alumb_Pergolas_Tamarit_2.Manual_horario | 192.168.4.33:4660 | 1:0X:418 | Read+Write | Always
MSA_BT_Alumb_Pergolas_Tamarit_2.Marcha_paro | 192.168.4.33:4660 | 1:0X:419 | Read+Write | Always
MSA_BT_Alumb_Pergolas_Tamarit_2.Orden | 192.168.4.33:4660 | 1:0X:304 | Read+Write | Always
MSA_BT_Alumb_Plaza_B.Estado | 192.168.4.33:4660 | 3:0X:205 | Read+Write | Always
MSA_BT_Alumb_Plaza_B.Fallo | 192.168.4.33:4660 | 3:0X:357 | Read+Write | Always
MSA_BT_Alumb_Plaza_B.Horario_A | 192.168.4.33:4660 | 3:3X:761T80 | Read+Write | Always
MSA_BT_Alumb_Plaza_B.Horario_estado | 192.168.4.33:4660 | 3:0X:353 | Read+Write | Always
MSA_BT_Alumb_Plaza_B.Manual_horario | 192.168.4.33:4660 | 3:0X:354 | Read+Write | Always
MSA_BT_Alumb_Plaza_B.Marcha_paro | 192.168.4.33:4660 | 3:0X:355 | Read+Write | Always
MSA_BT_Alumb_Plaza_B.Orden | 192.168.4.33:4660 | 3:0X:269 | Read+Write | Always
MSA_BT_Alumb_Plaza_T.Estado | 192.168.4.33:4660 | 3:0X:206 | Read+Write | Always
MSA_BT_Alumb_Plaza_T.Fallo | 192.168.4.33:4660 | 3:0X:365 | Read+Write | Always
MSA_BT_Alumb_Plaza_T.Horario_A | 192.168.4.33:4660 | 3:3X:717T80 | Read+Write | Always
MSA_BT_Alumb_Plaza_T.Horario_estado | 192.168.4.33:4660 | 3:0X:361 | Read+Write | Always
MSA_BT_Alumb_Plaza_T.Manual_horario | 192.168.4.33:4660 | 3:0X:362 | Read+Write | Always
MSA_BT_Alumb_Plaza_T.Marcha_paro | 192.168.4.33:4660 | 3:0X:363 | Read+Write | Always
MSA_BT_Alumb_Plaza_T.Orden | 192.168.4.33:4660 | 3:0X:270 | Read+Write | Always
MSA_BT_Alumb_Rampa_CD_1.Estado | 192.168.4.33:4660 | 7:0X:205 | Read+Write | Always
MSA_BT_Alumb_Rampa_CD_1.Fallo | 192.168.4.33:4660 | 7:0X:341 | Read+Write | Always
MSA_BT_Alumb_Rampa_CD_1.Horario_A | 192.168.4.33:4660 | 7:3X:849T80 | Read+Write | Always
MSA_BT_Alumb_Rampa_CD_1.Horario_estado | 192.168.4.33:4660 | 7:0X:337 | Read+Write | Always
MSA_BT_Alumb_Rampa_CD_1.Manual_horario | 192.168.4.33:4660 | 7:0X:338 | Read+Write | Always
MSA_BT_Alumb_Rampa_CD_1.Marcha_paro | 192.168.4.33:4660 | 7:0X:339 | Read+Write | Always
MSA_BT_Alumb_Rampa_CD_1.Orden | 192.168.4.33:4660 | 7:0X:268 | Read+Write | Always
MSA_BT_Alumb_Rampa_CD_2.Estado | 192.168.4.33:4660 | 7:0X:206 | Read+Write | Always
MSA_BT_Alumb_Rampa_CD_2.Fallo | 192.168.4.33:4660 | 7:0X:349 | Read+Write | Always
MSA_BT_Alumb_Rampa_CD_2.Horario_A | 192.168.4.33:4660 | 7:3X:805T80 | Read+Write | Always
MSA_BT_Alumb_Rampa_CD_2.Horario_estado | 192.168.4.33:4660 | 7:0X:345 | Read+Write | Always
MSA_BT_Alumb_Rampa_CD_2.Manual_horario | 192.168.4.33:4660 | 7:0X:346 | Read+Write | Always
MSA_BT_Alumb_Rampa_CD_2.Marcha_paro | 192.168.4.33:4660 | 7:0X:347 | Read+Write | Always
MSA_BT_Alumb_Rampa_CD_2.Orden | 192.168.4.33:4660 | 7:0X:269 | Read+Write | Always
MSA_BT_Alumb_reserva.Estado | 192.168.4.33:4660 | 2:0X:232 | Read+Write | Always
MSA_BT_Alumb_reserva.Fallo | 192.168.4.33:4660 | 2:0X:421 | Read+Write | Always
MSA_BT_Alumb_reserva.Horario_A | 192.168.4.33:4660 | 2:3X:409T80 | Read+Write | Always
MSA_BT_Alumb_reserva.Horario_estado | 192.168.4.33:4660 | 2:0X:417 | Read+Write | Always
MSA_BT_Alumb_reserva.Manual_horario | 192.168.4.33:4660 | 2:0X:418 | Read+Write | Always
MSA_BT_Alumb_reserva.Marcha_paro | 192.168.4.33:4660 | 2:0X:419 | Read+Write | Always
MSA_BT_Alumb_reserva.Orden | 192.168.4.33:4660 | 2:0X:280 | Read+Write | Always
MSA_BT_Alumb_S_Tecnicas.Estado | 192.168.4.33:4660 | 10:0X:224 | Read+Write | Always
MSA_BT_Alumb_S_Tecnicas.Fallo | 192.168.4.33:4660 | 10:0X:405 | Read+Write | Always
MSA_BT_Alumb_S_Tecnicas.Horario_A | 192.168.4.33:4660 | 10:3X:497T80 | Read+Write | Always
MSA_BT_Alumb_S_Tecnicas.Horario_estado | 192.168.4.33:4660 | 10:0X:401 | Read+Write | Always
MSA_BT_Alumb_S_Tecnicas.Manual_horario | 192.168.4.33:4660 | 10:0X:402 | Read+Write | Always
MSA_BT_Alumb_S_Tecnicas.Marcha_paro | 192.168.4.33:4660 | 10:0X:403 | Read+Write | Always
MSA_BT_Alumb_S_Tecnicas.Orden | 192.168.4.33:4660 | 10:0X:278 | Read+Write | Always
MSA_BT_Alumb_Servicios.Estado | 192.168.4.33:4660 | 2:0X:221 | Read+Write | Always
MSA_BT_Alumb_Servicios.Fallo | 192.168.4.33:4660 | 2:0X:413 | Read+Write | Always
MSA_BT_Alumb_Servicios.Horario_A | 192.168.4.33:4660 | 2:3X:453T80 | Read+Write | Always
MSA_BT_Alumb_Servicios.Horario_estado | 192.168.4.33:4660 | 2:0X:409 | Read+Write | Always
MSA_BT_Alumb_Servicios.Manual_horario | 192.168.4.33:4660 | 2:0X:410 | Read+Write | Always
MSA_BT_Alumb_Servicios.Marcha_paro | 192.168.4.33:4660 | 2:0X:411 | Read+Write | Always
MSA_BT_Alumb_Servicios.Orden | 192.168.4.33:4660 | 2:0X:279 | Read+Write | Always
MSA_BT_Alumb_Vigi.Estado | 192.168.4.33:4660 | 10:0X:221 | Read+Write | Always
MSA_BT_Alumb_Vigi.Fallo | 192.168.4.33:4660 | 10:0X:381 | Read+Write | Always
MSA_BT_Alumb_Vigi.Horario_A | 192.168.4.33:4660 | 10:3X:629T80 | Read+Write | Always
MSA_BT_Alumb_Vigi.Horario_estado | 192.168.4.33:4660 | 10:0X:377 | Read+Write | Always
MSA_BT_Alumb_Vigi.Manual_horario | 192.168.4.33:4660 | 10:0X:378 | Read+Write | Always
MSA_BT_Alumb_Vigi.Marcha_paro | 192.168.4.33:4660 | 10:0X:379 | Read+Write | Always
MSA_BT_Alumb_Vigi.Orden | 192.168.4.33:4660 | 10:0X:275 | Read+Write | Always
MSA_BT_Alumb_Vigi_Encants_Dreta.Estado | 192.168.4.33:4660 | 2:0X:207 | Read+Write | Always
MSA_BT_Alumb_Vigi_Encants_Dreta.Fallo | 192.168.4.33:4660 | 2:0X:365 | Read+Write | Always
MSA_BT_Alumb_Vigi_Encants_Dreta.Horario_A | 192.168.4.33:4660 | 2:3X:717T80 | Read+Write | Always
MSA_BT_Alumb_Vigi_Encants_Dreta.Horario_estado | 192.168.4.33:4660 | 2:0X:361 | Read+Write | Always
MSA_BT_Alumb_Vigi_Encants_Dreta.Manual_horario | 192.168.4.33:4660 | 2:0X:362 | Read+Write | Always
MSA_BT_Alumb_Vigi_Encants_Dreta.Marcha_paro | 192.168.4.33:4660 | 2:0X:363 | Read+Write | Always
MSA_BT_Alumb_Vigi_Encants_Dreta.Orden | 192.168.4.33:4660 | 2:0X:273 | Read+Write | Always
MSA_BT_Alumb_Zona_Fresc_L1.Estado | 192.168.4.33:4660 | 2:0X:203 | Read+Write | Always
MSA_BT_Alumb_Zona_Fresc_L1.Fallo | 192.168.4.33:4660 | 2:0X:333 | Read+Write | Always
MSA_BT_Alumb_Zona_Fresc_L1.Horario_A | 192.168.4.33:4660 | 2:3X:893T80 | Read+Write | Always
MSA_BT_Alumb_Zona_Fresc_L1.Horario_estado | 192.168.4.33:4660 | 2:0X:329 | Read+Write | Always
MSA_BT_Alumb_Zona_Fresc_L1.Manual_horario | 192.168.4.33:4660 | 2:0X:330 | Read+Write | Always
MSA_BT_Alumb_Zona_Fresc_L1.Marcha_paro | 192.168.4.33:4660 | 2:0X:331 | Read+Write | Always
MSA_BT_Alumb_Zona_Fresc_L1.Orden | 192.168.4.33:4660 | 2:0X:267 | Read+Write | Always
MSA_BT_Alumb_Zona_Fresc_L2.Estado | 192.168.4.33:4660 | 2:0X:204 | Read+Write | Always
MSA_BT_Alumb_Zona_Fresc_L2.Fallo | 192.168.4.33:4660 | 2:0X:341 | Read+Write | Always
MSA_BT_Alumb_Zona_Fresc_L2.Horario_A | 192.168.4.33:4660 | 2:3X:849T80 | Read+Write | Always
MSA_BT_Alumb_Zona_Fresc_L2.Horario_estado | 192.168.4.33:4660 | 2:0X:337 | Read+Write | Always
MSA_BT_Alumb_Zona_Fresc_L2.Manual_horario | 192.168.4.33:4660 | 2:0X:338 | Read+Write | Always
MSA_BT_Alumb_Zona_Fresc_L2.Marcha_paro | 192.168.4.33:4660 | 2:0X:339 | Read+Write | Always
MSA_BT_Alumb_Zona_Fresc_L2.Orden | 192.168.4.33:4660 | 2:0X:268 | Read+Write | Always
MSA_BT_Alumb_Zona_Fresc_L3.Estado | 192.168.4.33:4660 | 2:0X:205 | Read+Write | Always
MSA_BT_Alumb_Zona_Fresc_L3.Fallo | 192.168.4.33:4660 | 2:0X:349 | Read+Write | Always
MSA_BT_Alumb_Zona_Fresc_L3.Horario_A | 192.168.4.33:4660 | 2:3X:805T80 | Read+Write | Always
MSA_BT_Alumb_Zona_Fresc_L3.Horario_estado | 192.168.4.33:4660 | 2:0X:345 | Read+Write | Always
MSA_BT_Alumb_Zona_Fresc_L3.Manual_horario | 192.168.4.33:4660 | 2:0X:346 | Read+Write | Always
MSA_BT_Alumb_Zona_Fresc_L3.Marcha_paro | 192.168.4.33:4660 | 2:0X:347 | Read+Write | Always
MSA_BT_Alumb_Zona_Fresc_L3.Orden | 192.168.4.33:4660 | 2:0X:269 | Read+Write | Always
MSA_BT_Arqueta_PB_Nivel_alto | 192.168.4.33:4660 | 6:0X:248 | Read+Write | Always
MSA_BT_Bomba_AC_A_Geoterm.Horario_A | 192.168.4.33:4660 | 6:3X:805T80 | Read+Write | Always
MSA_BT_Bomba_AC_A_Geoterm.Horario_estado | 192.168.4.33:4660 | 6:0X:361 | Read+Write | Always
MSA_BT_Bomba_AC_A_Geoterm.Manual_horario | 192.168.4.33:4660 | 6:0X:362 | Read+Write | Always
MSA_BT_Bomba_AC_A_Geoterm.Marcha_paro | 192.168.4.33:4660 | 6:0X:363 | Read+Write | Always
MSA_BT_Bomba_AC_A_Geoterm.Reset_horas | 192.168.4.33:4660 | 6:0X:364 | Read+Write | Always
MSA_BT_Bomba_AC_A_Geoterm_1.Alarma_variador | 192.168.4.33:4660 | 8:0X:201 | Read+Write | Always
MSA_BT_Bomba_AC_A_Geoterm_1.Estado | 192.168.4.33:4660 | 6:0X:225 | Read+Write | Always
MSA_BT_Bomba_AC_A_Geoterm_1.Fallo | 192.168.4.33:4660 | 6:0X:366 | Read+Write | Always
MSA_BT_Bomba_AC_A_Geoterm_1.Horas_funcionam | 192.168.4.33:4660 | 6:3X:496 | Read+Write | Always
MSA_BT_Bomba_AC_A_Geoterm_1.Orden | 192.168.4.33:4660 | 6:0X:285 | Read+Write | Always
MSA_BT_Bomba_AC_A_Geoterm_2.Alarma_variador | 192.168.4.33:4660 | 8:0X:202 | Read+Write | Always
MSA_BT_Bomba_AC_A_Geoterm_2.Estado | 192.168.4.33:4660 | 6:0X:226 | Read+Write | Always
MSA_BT_Bomba_AC_A_Geoterm_2.Fallo | 192.168.4.33:4660 | 6:0X:367 | Read+Write | Always
MSA_BT_Bomba_AC_A_Geoterm_2.Horas_funcionam | 192.168.4.33:4660 | 6:3X:452 | Read+Write | Always
MSA_BT_Bomba_AC_A_Geoterm_2.Orden | 192.168.4.33:4660 | 6:0X:286 | Read+Write | Always
MSA_BT_Bomba_AC_Vestuarios.Horario_A | 192.168.4.33:4660 | 6:3X:761T80 | Read+Write | Always
MSA_BT_Bomba_AC_Vestuarios.Horario_estado | 192.168.4.33:4660 | 6:0X:354 | Read+Write | Always
MSA_BT_Bomba_AC_Vestuarios.Manual_horario | 192.168.4.33:4660 | 6:0X:355 | Read+Write | Always
MSA_BT_Bomba_AC_Vestuarios.Marcha_paro | 192.168.4.33:4660 | 6:0X:356 | Read+Write | Always
MSA_BT_Bomba_AC_Vestuarios.Reset_horas | 192.168.4.33:4660 | 6:0X:357 | Read+Write | Always
MSA_BT_Bomba_AC_Vestuarios_1.Alarma_variador | 192.168.4.33:4660 | 8:0X:203 | Read+Write | Always
MSA_BT_Bomba_AC_Vestuarios_1.Estado | 192.168.4.33:4660 | 6:0X:223 | Read+Write | Always
MSA_BT_Bomba_AC_Vestuarios_1.Fallo | 192.168.4.33:4660 | 6:0X:358 | Read+Write | Always
MSA_BT_Bomba_AC_Vestuarios_1.Horas_funcionam | 192.168.4.33:4660 | 6:3X:584 | Read+Write | Always
MSA_BT_Bomba_AC_Vestuarios_1.Orden | 192.168.4.33:4660 | 6:0X:283 | Read+Write | Always
MSA_BT_Bomba_AC_Vestuarios_2.Alarma_variador | 192.168.4.33:4660 | 8:0X:204 | Read+Write | Always
MSA_BT_Bomba_AC_Vestuarios_2.Estado | 192.168.4.33:4660 | 6:0X:224 | Read+Write | Always
MSA_BT_Bomba_AC_Vestuarios_2.Fallo | 192.168.4.33:4660 | 6:0X:359 | Read+Write | Always
MSA_BT_Bomba_AC_Vestuarios_2.Horas_funcionam | 192.168.4.33:4660 | 6:3X:540 | Read+Write | Always
MSA_BT_Bomba_AC_Vestuarios_2.Orden | 192.168.4.33:4660 | 6:0X:284 | Read+Write | Always
MSA_BT_Bomba_AF_A_Geoterm.Horario_A | 192.168.4.33:4660 | 6:3X:849T80 | Read+Write | Always
MSA_BT_Bomba_AF_A_Geoterm.Horario_estado | 192.168.4.33:4660 | 6:0X:337 | Read+Write | Always
MSA_BT_Bomba_AF_A_Geoterm.Manual_horario | 192.168.4.33:4660 | 6:0X:338 | Read+Write | Always
MSA_BT_Bomba_AF_A_Geoterm.Marcha_paro | 192.168.4.33:4660 | 6:0X:339 | Read+Write | Always
MSA_BT_Bomba_AF_A_Geoterm.Reset_horas | 192.168.4.33:4660 | 6:0X:340 | Read+Write | Always
MSA_BT_Bomba_AF_A_Geoterm_1.Alarma_variador | 192.168.4.33:4660 | 6:0X:246 | Read+Write | Always
MSA_BT_Bomba_AF_A_Geoterm_1.Estado | 192.168.4.33:4660 | 6:0X:204 | Read+Write | Always
MSA_BT_Bomba_AF_A_Geoterm_1.Fallo | 192.168.4.33:4660 | 6:0X:342 | Read+Write | Always
MSA_BT_Bomba_AF_A_Geoterm_1.Horas_funcionam | 192.168.4.33:4660 | 6:3X:672 | Read+Write | Always
MSA_BT_Bomba_AF_A_Geoterm_1.Orden | 192.168.4.33:4660 | 6:0X:275 | Read+Write | Always
MSA_BT_Bomba_AF_A_Geoterm_2.Alarma_variador | 192.168.4.33:4660 | 6:0X:247 | Read+Write | Always
MSA_BT_Bomba_AF_A_Geoterm_2.Estado | 192.168.4.33:4660 | 6:0X:205 | Read+Write | Always
MSA_BT_Bomba_AF_A_Geoterm_2.Fallo | 192.168.4.33:4660 | 6:0X:343 | Read+Write | Always
MSA_BT_Bomba_AF_A_Geoterm_2.Horas_funcionam | 192.168.4.33:4660 | 6:3X:628 | Read+Write | Always
MSA_BT_Bomba_AF_A_Geoterm_2.Orden | 192.168.4.33:4660 | 6:0X:276 | Read+Write | Always
MSA_BT_Bomba_calor_1.Estado | 192.168.4.33:4660 | 5:0X:221 | Read+Write | Always
MSA_BT_Bomba_calor_1.Horas_funcionam | 192.168.4.33:4660 | 5:3X:848 | Read+Write | Always
MSA_BT_Bomba_calor_2.Estado | 192.168.4.33:4660 | 5:0X:222 | Read+Write | Always
MSA_BT_Bomba_calor_2.Horas_funcionam | 192.168.4.33:4660 | 5:3X:804 | Read+Write | Always
MSA_BT_Bomba_calor_Fallo | 192.168.4.33:4660 | 5:0X:337 | Read+Write | Always
MSA_BT_Bomba_calor_Orden | 192.168.4.33:4660 | 5:0X:275 | Read+Write | Always
MSA_BT_Bomba_Condens_1.Estado | 192.168.4.33:4660 | 5:0X:217 | Read+Write | Always
MSA_BT_Bomba_Condens_1.Horas_funcionam | 192.168.4.33:4660 | 5:3X:1024 | Read+Write | Always
MSA_BT_Bomba_Condens_2.Estado | 192.168.4.33:4660 | 5:0X:218 | Read+Write | Always
MSA_BT_Bomba_Condens_2.Horas_funcionam | 192.168.4.33:4660 | 5:3X:980 | Read+Write | Always
MSA_BT_Bomba_frio_1.Estado | 192.168.4.33:4660 | 5:0X:219 | Read+Write | Always
MSA_BT_Bomba_frio_1.Horas_funcionam | 192.168.4.33:4660 | 5:3X:936 | Read+Write | Always
MSA_BT_Bomba_frio_2.Estado | 192.168.4.33:4660 | 5:0X:220 | Read+Write | Always
MSA_BT_Bomba_frio_2.Horas_funcionam | 192.168.4.33:4660 | 5:3X:892 | Read+Write | Always
MSA_BT_Bomba_frio_Fallo | 192.168.4.33:4660 | 5:0X:334 | Read+Write | Always
MSA_BT_Bomba_frio_Orden | 192.168.4.33:4660 | 5:0X:273 | Read+Write | Always
MSA_BT_Bombas_ACS_P_Inf.Horario_A | 192.168.4.33:4660 | 6:3X:937T80 | Read+Write | Always
MSA_BT_Bombas_ACS_P_Inf.Horario_estado | 192.168.4.33:4660 | 6:0X:322 | Read+Write | Always
MSA_BT_Bombas_ACS_P_Inf.Manual_horario | 192.168.4.33:4660 | 6:0X:323 | Read+Write | Always
MSA_BT_Bombas_ACS_P_Inf.Marcha_paro | 192.168.4.33:4660 | 6:0X:324 | Read+Write | Always
MSA_BT_Bombas_ACS_P_Inf.Reset_horas | 192.168.4.33:4660 | 6:0X:325 | Read+Write | Always
MSA_BT_Bombas_ACS_P_Inf_1.Alarma_variador | 192.168.4.33:4660 | 6:0X:229 | Read+Write | Always
MSA_BT_Bombas_ACS_P_Inf_1.Estado | 192.168.4.33:4660 | 6:0X:219 | Read+Write | Always
MSA_BT_Bombas_ACS_P_Inf_1.Fallo | 192.168.4.33:4660 | 6:0X:326 | Read+Write | Always
MSA_BT_Bombas_ACS_P_Inf_1.Horas_funcionam | 192.168.4.33:4660 | 6:3X:848 | Read+Write | Always
MSA_BT_Bombas_ACS_P_Inf_1.Orden | 192.168.4.33:4660 | 6:0X:279 | Read+Write | Always
MSA_BT_Bombas_ACS_P_Inf_2.Alarma_variador | 192.168.4.33:4660 | 6:0X:231 | Read+Write | Always
MSA_BT_Bombas_ACS_P_Inf_2.Estado | 192.168.4.33:4660 | 6:0X:220 | Read+Write | Always
MSA_BT_Bombas_ACS_P_Inf_2.Fallo | 192.168.4.33:4660 | 6:0X:327 | Read+Write | Always
MSA_BT_Bombas_ACS_P_Inf_2.Horas_funcionam | 192.168.4.33:4660 | 6:3X:804 | Read+Write | Always
MSA_BT_Bombas_ACS_P_Inf_2.Orden | 192.168.4.33:4660 | 6:0X:280 | Read+Write | Always
MSA_BT_Bombas_ACS_PB.Horario_A | 192.168.4.33:4660 | 6:3X:893T80 | Read+Write | Always
MSA_BT_Bombas_ACS_PB.Horario_estado | 192.168.4.33:4660 | 6:0X:330 | Read+Write | Always
MSA_BT_Bombas_ACS_PB.Manual_horario | 192.168.4.33:4660 | 6:0X:331 | Read+Write | Always
MSA_BT_Bombas_ACS_PB.Marcha_paro | 192.168.4.33:4660 | 6:0X:332 | Read+Write | Always
MSA_BT_Bombas_ACS_PB.Reset_horas | 192.168.4.33:4660 | 6:0X:333 | Read+Write | Always
MSA_BT_Bombas_ACS_PB_1.Alarma_variador | 192.168.4.33:4660 | 6:0X:206 | Read+Write | Always
MSA_BT_Bombas_ACS_PB_1.Estado | 192.168.4.33:4660 | 6:0X:217 | Read+Write | Always
MSA_BT_Bombas_ACS_PB_1.Fallo | 192.168.4.33:4660 | 6:0X:334 | Read+Write | Always
MSA_BT_Bombas_ACS_PB_1.Horas_funcionam | 192.168.4.33:4660 | 6:3X:760 | Read+Write | Always
MSA_BT_Bombas_ACS_PB_1.Orden | 192.168.4.33:4660 | 6:0X:277 | Read+Write | Always
MSA_BT_Bombas_ACS_PB_2.Alarma_variador | 192.168.4.33:4660 | 6:0X:207 | Read+Write | Always
MSA_BT_Bombas_ACS_PB_2.Estado | 192.168.4.33:4660 | 6:0X:218 | Read+Write | Always
MSA_BT_Bombas_ACS_PB_2.Fallo | 192.168.4.33:4660 | 6:0X:335 | Read+Write | Always
MSA_BT_Bombas_ACS_PB_2.Horas_funcionam | 192.168.4.33:4660 | 6:3X:716 | Read+Write | Always
MSA_BT_Bombas_ACS_PB_2.Orden | 192.168.4.33:4660 | 6:0X:278 | Read+Write | Always
MSA_BT_Bombas_Condens_Fallo | 192.168.4.33:4660 | 5:0X:326 | Read+Write | Always
MSA_BT_Bombas_Condens_Orden | 192.168.4.33:4660 | 5:0X:269 | Read+Write | Always
MSA_BT_Bombas_UTAS.Horario_A | 192.168.4.33:4660 | 6:3X:981T80 | Read+Write | Always
MSA_BT_Bombas_UTAS.Horario_estado | 192.168.4.33:4660 | 6:0X:313 | Read+Write | Always
MSA_BT_Bombas_UTAS.Manual_horario | 192.168.4.33:4660 | 6:0X:314 | Read+Write | Always
MSA_BT_Bombas_UTAS.Marcha_paro | 192.168.4.33:4660 | 6:0X:315 | Read+Write | Always
MSA_BT_Bombas_UTAS.Reset_horas | 192.168.4.33:4660 | 6:0X:316 | Read+Write | Always
MSA_BT_Bombas_UTAS_AC_1.Alarma_variador | 192.168.4.33:4660 | 6:0X:244 | Read+Write | Always
MSA_BT_Bombas_UTAS_AC_1.Estado | 192.168.4.33:4660 | 6:0X:221 | Read+Write | Always
MSA_BT_Bombas_UTAS_AC_1.Fallo | 192.168.4.33:4660 | 6:0X:318 | Read+Write | Always
MSA_BT_Bombas_UTAS_AC_1.Horas_funcionam | 192.168.4.33:4660 | 6:3X:1024 | Read+Write | Always
MSA_BT_Bombas_UTAS_AC_1.Orden | 192.168.4.33:4660 | 6:0X:281 | Read+Write | Always
MSA_BT_Bombas_UTAS_AC_2.Alarma_variador | 192.168.4.33:4660 | 6:0X:245 | Read+Write | Always
MSA_BT_Bombas_UTAS_AC_2.Estado | 192.168.4.33:4660 | 6:0X:222 | Read+Write | Always
MSA_BT_Bombas_UTAS_AC_2.Fallo | 192.168.4.33:4660 | 6:0X:319 | Read+Write | Always
MSA_BT_Bombas_UTAS_AC_2.Horas_funcionam | 192.168.4.33:4660 | 6:3X:980 | Read+Write | Always
MSA_BT_Bombas_UTAS_AC_2.Orden | 192.168.4.33:4660 | 6:0X:282 | Read+Write | Always
MSA_BT_Bombas_UTAS_AF_1.Alarma_variador | 192.168.4.33:4660 | 6:0X:227 | Read+Write | Always
MSA_BT_Bombas_UTAS_AF_1.Estado | 192.168.4.33:4660 | 6:0X:202 | Read+Write | Always
MSA_BT_Bombas_UTAS_AF_1.Fallo | 192.168.4.33:4660 | 6:0X:371 | Read+Write | Always
MSA_BT_Bombas_UTAS_AF_1.Horas_funcionam | 192.168.4.33:4660 | 6:3X:936 | Read+Write | Always
MSA_BT_Bombas_UTAS_AF_1.Orden | 192.168.4.33:4660 | 6:0X:273 | Read+Write | Always
MSA_BT_Bombas_UTAS_AF_2.Alarma_variador | 192.168.4.33:4660 | 6:0X:228 | Read+Write | Always
MSA_BT_Bombas_UTAS_AF_2.Estado | 192.168.4.33:4660 | 6:0X:203 | Read+Write | Always
MSA_BT_Bombas_UTAS_AF_2.Fallo | 192.168.4.33:4660 | 6:0X:372 | Read+Write | Always
MSA_BT_Bombas_UTAS_AF_2.Horas_funcionam | 192.168.4.33:4660 | 6:3X:892 | Read+Write | Always
MSA_BT_Bombas_UTAS_AF_2.Orden | 192.168.4.33:4660 | 6:0X:274 | Read+Write | Always
MSA_BT_Circuito_calor_Interruptor_flujo | 192.168.4.33:4660 | 6:0X:232 | Read+Write | Always
MSA_BT_Circuito_calor_Presostato_maxima | 192.168.4.33:4660 | 6:0X:238 | Read+Write | Always
MSA_BT_Circuito_calor_Presostato_minima | 192.168.4.33:4660 | 6:0X:239 | Read+Write | Always
MSA_BT_Circuito_Condens_Interruptor_flujo | 192.168.4.33:4660 | 6:0X:208 | Read+Write | Always
MSA_BT_Circuito_Condens_Presostato_maxima | 192.168.4.33:4660 | 6:0X:234 | Read+Write | Always
MSA_BT_Circuito_Condens_Presostato_minima | 192.168.4.33:4660 | 6:0X:235 | Read+Write | Always
MSA_BT_Circuito_frio_Interruptor_flujo | 192.168.4.33:4660 | 6:0X:230 | Read+Write | Always
MSA_BT_Circuito_frio_Presostato_maxima | 192.168.4.33:4660 | 6:0X:236 | Read+Write | Always
MSA_BT_Circuito_frio_Presostato_minima | 192.168.4.33:4660 | 6:0X:237 | Read+Write | Always
MSA_BT_Cl_ESD.Estado_maquina | 192.168.4.33:4660 | 1:0X:236 | Read+Write | Always
MSA_BT_Cl_ESD.Estado_recuperador | 192.168.4.33:4660 | 1:0X:252 | Read+Write | Always
MSA_BT_Cl_ESD.Estado_vent_imp | 192.168.4.33:4660 | 1:0X:231 | Read+Write | Always
MSA_BT_Cl_ESD.Estado_vent_ret | 192.168.4.33:4660 | 1:0X:232 | Read+Write | Always
MSA_BT_Cl_ESD.Fallo_maquina | 192.168.4.33:4660 | 1:0X:344 | Read+Write | Always
MSA_BT_Cl_ESD.Fallo_recuperador | 192.168.4.33:4660 | 1:0X:343 | Read+Write | Always
MSA_BT_Cl_ESD.Fallo_vent_imp | 192.168.4.33:4660 | 1:0X:341 | Read+Write | Always
MSA_BT_Cl_ESD.Fallo_vent_ret | 192.168.4.33:4660 | 1:0X:342 | Read+Write | Always
MSA_BT_Cl_ESD.Filtro_imp | 192.168.4.33:4660 | 1:0X:207 | Read+Write | Always
MSA_BT_Cl_ESD.Filtro_recuperador | 192.168.4.33:4660 | 1:0X:244 | Read+Write | Always
MSA_BT_Cl_ESD.Filtro_ret | 192.168.4.33:4660 | 1:0X:208 | Read+Write | Always
MSA_BT_Cl_ESD.Horario_A | 192.168.4.33:4660 | 1:3X:849T80 | Read+Write | Always
MSA_BT_Cl_ESD.Horario_estado | 192.168.4.33:4660 | 1:0X:337 | Read+Write | Always
MSA_BT_Cl_ESD.Horas_funcionam | 192.168.4.33:4660 | 1:3X:892 | Read+Write | Always
MSA_BT_Cl_ESD.Manual_horario | 192.168.4.33:4660 | 1:0X:338 | Read+Write | Always
MSA_BT_Cl_ESD.Marcha_paro | 192.168.4.33:4660 | 1:0X:339 | Read+Write | Always
MSA_BT_Cl_ESD.Orden_humectador | 192.168.4.33:4660 | 1:0X:286 | Read+Write | Always
MSA_BT_Cl_ESD.Orden_maquina | 192.168.4.33:4660 | 1:0X:278 | Read+Write | Always
MSA_BT_Cl_ESD.Orden_recuperador | 192.168.4.33:4660 | 1:0X:282 | Read+Write | Always
MSA_BT_Cl_ESD.Orden_vent_imp | 192.168.4.33:4660 | 1:0X:273 | Read+Write | Always
MSA_BT_Cl_ESD.Orden_vent_ret | 192.168.4.33:4660 | 1:0X:274 | Read+Write | Always
MSA_BT_Cl_ESD.Presostato_vent_imp | 192.168.4.33:4660 | 1:0X:223 | Read+Write | Always
MSA_BT_Cl_ESD.Presostato_vent_ret | 192.168.4.33:4660 | 1:0X:224 | Read+Write | Always
MSA_BT_Cl_ESD.Reset_horas | 192.168.4.33:4660 | 1:0X:340 | Read+Write | Always
MSA_BT_Cl_ESE.Estado_maquina | 192.168.4.33:4660 | 1:0X:233 | Read+Write | Always
MSA_BT_Cl_ESE.Estado_recuperador | 192.168.4.33:4660 | 1:0X:249 | Read+Write | Always
MSA_BT_Cl_ESE.Estado_vent_imp | 192.168.4.33:4660 | 1:0X:225 | Read+Write | Always
MSA_BT_Cl_ESE.Estado_vent_ret | 192.168.4.33:4660 | 1:0X:226 | Read+Write | Always
MSA_BT_Cl_ESE.Fallo_maquina | 192.168.4.33:4660 | 1:0X:320 | Read+Write | Always
MSA_BT_Cl_ESE.Fallo_recuperador | 192.168.4.33:4660 | 1:0X:319 | Read+Write | Always
MSA_BT_Cl_ESE.Fallo_vent_imp | 192.168.4.33:4660 | 1:0X:317 | Read+Write | Always
MSA_BT_Cl_ESE.Fallo_vent_ret | 192.168.4.33:4660 | 1:0X:318 | Read+Write | Always
MSA_BT_Cl_ESE.Filtro_imp | 192.168.4.33:4660 | 1:0X:201 | Read+Write | Always
MSA_BT_Cl_ESE.Filtro_recuperador | 192.168.4.33:4660 | 1:0X:241 | Read+Write | Always
MSA_BT_Cl_ESE.Filtro_ret | 192.168.4.33:4660 | 1:0X:202 | Read+Write | Always
MSA_BT_Cl_ESE.Horario_A | 192.168.4.33:4660 | 1:3X:981T80 | Read+Write | Always
MSA_BT_Cl_ESE.Horario_estado | 192.168.4.33:4660 | 1:0X:313 | Read+Write | Always
MSA_BT_Cl_ESE.Horas_funcionam | 192.168.4.33:4660 | 1:3X:1024 | Read+Write | Always
MSA_BT_Cl_ESE.Manual_horario | 192.168.4.33:4660 | 1:0X:314 | Read+Write | Always
MSA_BT_Cl_ESE.Marcha_paro | 192.168.4.33:4660 | 1:0X:315 | Read+Write | Always
MSA_BT_Cl_ESE.Orden_humectador | 192.168.4.33:4660 | 1:0X:283 | Read+Write | Always
MSA_BT_Cl_ESE.Orden_maquina | 192.168.4.33:4660 | 1:0X:275 | Read+Write | Always
MSA_BT_Cl_ESE.Orden_recuperador | 192.168.4.33:4660 | 1:0X:279 | Read+Write | Always
MSA_BT_Cl_ESE.Orden_vent_imp | 192.168.4.33:4660 | 1:0X:265 | Read+Write | Always
MSA_BT_Cl_ESE.Orden_vent_ret | 192.168.4.33:4660 | 1:0X:266 | Read+Write | Always
MSA_BT_Cl_ESE.Presostato_vent_imp | 192.168.4.33:4660 | 1:0X:217 | Read+Write | Always
MSA_BT_Cl_ESE.Presostato_vent_ret | 192.168.4.33:4660 | 1:0X:218 | Read+Write | Always
MSA_BT_Cl_ESE.Reset_horas | 192.168.4.33:4660 | 1:0X:316 | Read+Write | Always
MSA_BT_Cl_MFZCA.Estado_maquina | 192.168.4.33:4660 | 1:0X:235 | Read+Write | Always
MSA_BT_Cl_MFZCA.Estado_recuperador | 192.168.4.33:4660 | 1:0X:251 | Read+Write | Always
MSA_BT_Cl_MFZCA.Estado_vent_imp | 192.168.4.33:4660 | 1:0X:229 | Read+Write | Always
MSA_BT_Cl_MFZCA.Estado_vent_ret | 192.168.4.33:4660 | 1:0X:230 | Read+Write | Always
MSA_BT_Cl_MFZCA.Fallo_maquina | 192.168.4.33:4660 | 1:0X:336 | Read+Write | Always
MSA_BT_Cl_MFZCA.Fallo_recuperador | 192.168.4.33:4660 | 1:0X:335 | Read+Write | Always
MSA_BT_Cl_MFZCA.Fallo_vent_imp | 192.168.4.33:4660 | 1:0X:333 | Read+Write | Always
MSA_BT_Cl_MFZCA.Fallo_vent_ret | 192.168.4.33:4660 | 1:0X:334 | Read+Write | Always
MSA_BT_Cl_MFZCA.Filtro_imp | 192.168.4.33:4660 | 1:0X:205 | Read+Write | Always
MSA_BT_Cl_MFZCA.Filtro_recuperador | 192.168.4.33:4660 | 1:0X:243 | Read+Write | Always
MSA_BT_Cl_MFZCA.Filtro_ret | 192.168.4.33:4660 | 1:0X:206 | Read+Write | Always
MSA_BT_Cl_MFZCA.Horario_A | 192.168.4.33:4660 | 1:3X:893T80 | Read+Write | Always
MSA_BT_Cl_MFZCA.Horario_estado | 192.168.4.33:4660 | 1:0X:329 | Read+Write | Always
MSA_BT_Cl_MFZCA.Horas_funcionam | 192.168.4.33:4660 | 1:3X:936 | Read+Write | Always
MSA_BT_Cl_MFZCA.Manual_horario | 192.168.4.33:4660 | 1:0X:330 | Read+Write | Always
MSA_BT_Cl_MFZCA.Marcha_paro | 192.168.4.33:4660 | 1:0X:331 | Read+Write | Always
MSA_BT_Cl_MFZCA.Orden_humectador | 192.168.4.33:4660 | 1:0X:285 | Read+Write | Always
MSA_BT_Cl_MFZCA.Orden_maquina | 192.168.4.33:4660 | 1:0X:277 | Read+Write | Always
MSA_BT_Cl_MFZCA.Orden_recuperador | 192.168.4.33:4660 | 1:0X:281 | Read+Write | Always
MSA_BT_Cl_MFZCA.Orden_vent_imp | 192.168.4.33:4660 | 1:0X:269 | Read+Write | Always
MSA_BT_Cl_MFZCA.Orden_vent_ret | 192.168.4.33:4660 | 1:0X:270 | Read+Write | Always
MSA_BT_Cl_MFZCA.Presostato_vent_imp | 192.168.4.33:4660 | 1:0X:221 | Read+Write | Always
MSA_BT_Cl_MFZCA.Presostato_vent_ret | 192.168.4.33:4660 | 1:0X:222 | Read+Write | Always
MSA_BT_Cl_MFZCA.Reset_horas | 192.168.4.33:4660 | 1:0X:332 | Read+Write | Always
MSA_BT_Cl_MFZCE.Estado_maquina | 192.168.4.33:4660 | 1:0X:234 | Read+Write | Always
MSA_BT_Cl_MFZCE.Estado_recuperador | 192.168.4.33:4660 | 1:0X:250 | Read+Write | Always
MSA_BT_Cl_MFZCE.Estado_vent_imp | 192.168.4.33:4660 | 1:0X:227 | Read+Write | Always
MSA_BT_Cl_MFZCE.Estado_vent_ret | 192.168.4.33:4660 | 1:0X:228 | Read+Write | Always
MSA_BT_Cl_MFZCE.Fallo_maquina | 192.168.4.33:4660 | 1:0X:328 | Read+Write | Always
MSA_BT_Cl_MFZCE.Fallo_recuperador | 192.168.4.33:4660 | 1:0X:327 | Read+Write | Always
MSA_BT_Cl_MFZCE.Fallo_vent_imp | 192.168.4.33:4660 | 1:0X:325 | Read+Write | Always
MSA_BT_Cl_MFZCE.Fallo_vent_ret | 192.168.4.33:4660 | 1:0X:326 | Read+Write | Always
MSA_BT_Cl_MFZCE.Filtro_imp | 192.168.4.33:4660 | 1:0X:203 | Read+Write | Always
MSA_BT_Cl_MFZCE.Filtro_recuperador | 192.168.4.33:4660 | 1:0X:242 | Read+Write | Always
MSA_BT_Cl_MFZCE.Filtro_ret | 192.168.4.33:4660 | 1:0X:204 | Read+Write | Always
MSA_BT_Cl_MFZCE.Horario_A | 192.168.4.33:4660 | 1:3X:937T80 | Read+Write | Always
MSA_BT_Cl_MFZCE.Horario_estado | 192.168.4.33:4660 | 1:0X:321 | Read+Write | Always
MSA_BT_Cl_MFZCE.Horas_funcionam | 192.168.4.33:4660 | 1:3X:980 | Read+Write | Always
MSA_BT_Cl_MFZCE.Manual_horario | 192.168.4.33:4660 | 1:0X:322 | Read+Write | Always
MSA_BT_Cl_MFZCE.Marcha_paro | 192.168.4.33:4660 | 1:0X:323 | Read+Write | Always
MSA_BT_Cl_MFZCE.Orden_humectador | 192.168.4.33:4660 | 1:0X:284 | Read+Write | Always
MSA_BT_Cl_MFZCE.Orden_maquina | 192.168.4.33:4660 | 1:0X:276 | Read+Write | Always
MSA_BT_Cl_MFZCE.Orden_recuperador | 192.168.4.33:4660 | 1:0X:280 | Read+Write | Always
MSA_BT_Cl_MFZCE.Orden_vent_imp | 192.168.4.33:4660 | 1:0X:267 | Read+Write | Always
MSA_BT_Cl_MFZCE.Orden_vent_ret | 192.168.4.33:4660 | 1:0X:268 | Read+Write | Always
MSA_BT_Cl_MFZCE.Presostato_vent_imp | 192.168.4.33:4660 | 1:0X:219 | Read+Write | Always
MSA_BT_Cl_MFZCE.Presostato_vent_ret | 192.168.4.33:4660 | 1:0X:220 | Read+Write | Always
MSA_BT_Cl_MFZCE.Reset_horas | 192.168.4.33:4660 | 1:0X:324 | Read+Write | Always
MSA_BT_depositos_inercia_AC_Termostato_seg_1 | 192.168.4.33:4660 | 6:0X:242 | Read+Write | Always
MSA_BT_depositos_inercia_AC_Termostato_seg_2 | 192.168.4.33:4660 | 6:0X:243 | Read+Write | Always
MSA_BT_depositos_inercia_AF_Termostato_seg_1 | 192.168.4.33:4660 | 6:0X:240 | Read+Write | Always
MSA_BT_depositos_inercia_AF_Termostato_seg_2 | 192.168.4.33:4660 | 6:0X:241 | Read+Write | Always
MSA_BT_Patio_testa_Gral.Estado | 192.168.4.33:4660 | 7:0X:202 | Read+Write | Always
MSA_BT_Patio_testa_Gral.Fallo | 192.168.4.33:4660 | 7:0X:317 | Read+Write | Always
MSA_BT_Patio_testa_Gral.Horario_A | 192.168.4.33:4660 | 7:3X:981T80 | Read+Write | Always
MSA_BT_Patio_testa_Gral.Horario_estado | 192.168.4.33:4660 | 7:0X:313 | Read+Write | Always
MSA_BT_Patio_testa_Gral.Manual_horario | 192.168.4.33:4660 | 7:0X:314 | Read+Write | Always
MSA_BT_Patio_testa_Gral.Marcha_paro | 192.168.4.33:4660 | 7:0X:315 | Read+Write | Always
MSA_BT_Patio_testa_Gral.Orden | 192.168.4.33:4660 | 7:0X:265 | Read+Write | Always
MSA_BT_Produccion.Horario_A | 192.168.4.33:4660 | 5:3X:981T80 | Read+Write | Always
MSA_BT_Produccion.Horario_estado | 192.168.4.33:4660 | 5:0X:313 | Read+Write | Always
MSA_BT_Produccion.Manual_horario | 192.168.4.33:4660 | 5:0X:314 | Read+Write | Always
MSA_BT_Produccion.Marcha_paro | 192.168.4.33:4660 | 5:0X:315 | Read+Write | Always
MSA_BT_Produccion.Reset_horas | 192.168.4.33:4660 | 5:0X:316 | Read+Write | Always
MSA_BT_Produccion_Arrancar_maquina | 192.168.4.33:4660 | 5:0X:317 | Read+Write | Always
MSA_BT_Produccion_Estado_maquina | 192.168.4.33:4660 | 6:0X:201 | Read | Always
MSA_BT_Produccion_Orden_maquina | 192.168.4.33:4660 | 6:0X:287 | Read+Write | Always
MSA_BT_UTAS_IV_Bombas_paradas | 192.168.4.33:4660 | 6:0X:370 | Read+Write | Always
MSA_BT_UTAS_IV_Cambiando | 192.168.4.33:4660 | 6:0X:369 | Read+Write | Always
MSA_BT_UTAS_IV_Cambio_Bombas | 192.168.4.33:4660 | 6:0X:317 | Read+Write | Always
MSA_BT_UTAS_IV_Cambio_Valvulas | 192.168.4.33:4660 | 5:0X:328 | Read+Write | Always
MSA_BT_UTAS_IV_Valvulas_en_Posicion | 192.168.4.33:4660 | 5:0X:327 | Read+Write | Always
MSA_BT_valv_UTAS_AC_Impuls.Estado_abierta | 192.168.4.33:4660 | 5:0X:229 | Read+Write | Always
MSA_BT_valv_UTAS_AC_Impuls.Estado_cerrada | 192.168.4.33:4660 | 5:0X:230 | Read+Write | Always
MSA_BT_valv_UTAS_AC_Impuls.Fallo | 192.168.4.33:4660 | 5:0X:369 | Read+Write | Always
MSA_BT_valv_UTAS_AC_Impuls.Orden_abrir | 192.168.4.33:4660 | 5:0X:279 | Read+Write | Always
MSA_BT_valv_UTAS_AC_Retorno.Estado_abierta | 192.168.4.33:4660 | 5:0X:227 | Read+Write | Always
MSA_BT_valv_UTAS_AC_Retorno.Estado_cerrada | 192.168.4.33:4660 | 5:0X:228 | Read+Write | Always
MSA_BT_valv_UTAS_AC_Retorno.Fallo | 192.168.4.33:4660 | 5:0X:370 | Read+Write | Always
MSA_BT_valv_UTAS_AC_Retorno.Orden_abrir | 192.168.4.33:4660 | 5:0X:280 | Read+Write | Always
MSA_BT_valv_UTAS_AF_Impuls.Estado_abierta | 192.168.4.33:4660 | 5:0X:225 | Read+Write | Always
MSA_BT_valv_UTAS_AF_Impuls.Estado_cerrada | 192.168.4.33:4660 | 5:0X:226 | Read+Write | Always
MSA_BT_valv_UTAS_AF_Impuls.Fallo | 192.168.4.33:4660 | 5:0X:373 | Read+Write | Always
MSA_BT_valv_UTAS_AF_Impuls.Orden_abrir | 192.168.4.33:4660 | 5:0X:277 | Read+Write | Always
MSA_BT_valv_UTAS_AF_Retorno.Estado_abierta | 192.168.4.33:4660 | 5:0X:223 | Read+Write | Always
MSA_BT_valv_UTAS_AF_Retorno.Estado_cerrada | 192.168.4.33:4660 | 5:0X:224 | Read+Write | Always
MSA_BT_valv_UTAS_AF_Retorno.Fallo | 192.168.4.33:4660 | 5:0X:374 | Read+Write | Always
MSA_BT_valv_UTAS_AF_Retorno.Orden_abrir | 192.168.4.33:4660 | 5:0X:278 | Read+Write | Always
MSA_BT_VM_Condens_1.Estado_abierta | 192.168.4.33:4660 | 5:0X:201 | Read+Write | Always
MSA_BT_VM_Condens_1.Fallo | 192.168.4.33:4660 | 5:0X:322 | Read+Write | Always
MSA_BT_VM_Condens_1.Orden_abrir | 192.168.4.33:4660 | 5:0X:265 | Read+Write | Always
MSA_BT_VM_Condens_2.Estado_abierta | 192.168.4.33:4660 | 5:0X:202 | Read+Write | Always
MSA_BT_VM_Condens_2.Fallo | 192.168.4.33:4660 | 5:0X:323 | Read+Write | Always
MSA_BT_VM_Condens_2.Orden_abrir | 192.168.4.33:4660 | 5:0X:266 | Read+Write | Always
MSA_BT_VM_Condens_3.Estado_abierta | 192.168.4.33:4660 | 5:0X:203 | Read+Write | Always
MSA_BT_VM_Condens_3.Fallo | 192.168.4.33:4660 | 5:0X:324 | Read+Write | Always
MSA_BT_VM_Condens_3.Orden_abrir | 192.168.4.33:4660 | 5:0X:267 | Read+Write | Always
MSA_BT_VM_Condens_4.Estado_abierta | 192.168.4.33:4660 | 5:0X:204 | Read+Write | Always
MSA_BT_VM_Condens_4.Fallo | 192.168.4.33:4660 | 5:0X:325 | Read+Write | Always
MSA_BT_VM_Condens_4.Orden_abrir | 192.168.4.33:4660 | 5:0X:268 | Read+Write | Always
MSA_UM_53_Alumb_Servicios.Estado | 192.168.4.53:4660 | 10:0X:204 | Read+Write | Always
MSA_UM_53_Alumb_Servicios.Fallo | 192.168.4.53:4660 | 10:0X:341 | Read+Write | Always
MSA_UM_53_Alumb_Servicios.Horario_A | 192.168.4.53:4660 | 10:3X:849T80 | Read+Write | Always
MSA_UM_53_Alumb_Servicios.Horario_estado | 192.168.4.53:4660 | 10:0X:337 | Read+Write | Always
MSA_UM_53_Alumb_Servicios.Manual_horario | 192.168.4.53:4660 | 10:0X:338 | Read+Write | Always
MSA_UM_53_Alumb_Servicios.Marcha_paro | 192.168.4.53:4660 | 10:0X:339 | Read+Write | Always
MSA_UM_53_Alumb_Servicios.Orden | 192.168.4.53:4660 | 10:0X:268 | Read+Write | Always
MSA_UM_60_Alumb_Servicios.Estado | 192.168.4.53:4660 | 2:0X:221 | Read+Write | Always
MSA_UM_60_Alumb_Servicios.Fallo | 192.168.4.53:4660 | 2:0X:421 | Read+Write | Always
MSA_UM_60_Alumb_Servicios.Horario_A | 192.168.4.53:4660 | 2:3X:409T80 | Read+Write | Always
MSA_UM_60_Alumb_Servicios.Horario_estado | 192.168.4.53:4660 | 2:0X:417 | Read+Write | Always
MSA_UM_60_Alumb_Servicios.Manual_horario | 192.168.4.53:4660 | 2:0X:418 | Read+Write | Always
MSA_UM_60_Alumb_Servicios.Marcha_paro | 192.168.4.53:4660 | 2:0X:419 | Read+Write | Always
MSA_UM_60_Alumb_Servicios.Orden | 192.168.4.53:4660 | 2:0X:279 | Read+Write | Always
MSA_UM_Alumb_acces_testa.Estado | 192.168.4.53:4660 | 2:0X:218 | Read+Write | Always
MSA_UM_Alumb_acces_testa.Fallo | 192.168.4.53:4660 | 2:0X:389 | Read+Write | Always
MSA_UM_Alumb_acces_testa.Horario_A | 192.168.4.53:4660 | 2:3X:585T80 | Read+Write | Always
MSA_UM_Alumb_acces_testa.Horario_estado | 192.168.4.53:4660 | 2:0X:385 | Read+Write | Always
MSA_UM_Alumb_acces_testa.Manual_horario | 192.168.4.53:4660 | 2:0X:386 | Read+Write | Always
MSA_UM_Alumb_acces_testa.Marcha_paro | 192.168.4.53:4660 | 2:0X:387 | Read+Write | Always
MSA_UM_Alumb_acces_testa.Orden | 192.168.4.53:4660 | 2:0X:276 | Read+Write | Always
MSA_UM_Alumb_Accesos_Dcha.Estado | 192.168.4.53:4660 | 2:0X:217 | Read+Write | Always
MSA_UM_Alumb_Accesos_Dcha.Fallo | 192.168.4.53:4660 | 2:0X:381 | Read+Write | Always
MSA_UM_Alumb_Accesos_Dcha.Horario_A | 192.168.4.53:4660 | 2:3X:629T80 | Read+Write | Always
MSA_UM_Alumb_Accesos_Dcha.Horario_estado | 192.168.4.53:4660 | 2:0X:377 | Read+Write | Always
MSA_UM_Alumb_Accesos_Dcha.Manual_horario | 192.168.4.53:4660 | 2:0X:378 | Read+Write | Always
MSA_UM_Alumb_Accesos_Dcha.Marcha_paro | 192.168.4.53:4660 | 2:0X:379 | Read+Write | Always
MSA_UM_Alumb_Accesos_Dcha.Orden | 192.168.4.53:4660 | 2:0X:275 | Read+Write | Always
MSA_UM_Alumb_Accesos_Izqda.Estado | 192.168.4.53:4660 | 2:0X:208 | Read+Write | Always
MSA_UM_Alumb_Accesos_Izqda.Fallo | 192.168.4.53:4660 | 2:0X:373 | Read+Write | Always
MSA_UM_Alumb_Accesos_Izqda.Horario_A | 192.168.4.53:4660 | 2:3X:673T80 | Read+Write | Always
MSA_UM_Alumb_Accesos_Izqda.Horario_estado | 192.168.4.53:4660 | 2:0X:369 | Read+Write | Always
MSA_UM_Alumb_Accesos_Izqda.Manual_horario | 192.168.4.53:4660 | 2:0X:370 | Read+Write | Always
MSA_UM_Alumb_Accesos_Izqda.Marcha_paro | 192.168.4.53:4660 | 2:0X:371 | Read+Write | Always
MSA_UM_Alumb_Accesos_Izqda.Orden | 192.168.4.53:4660 | 2:0X:274 | Read+Write | Always
MSA_UM_Alumb_Corona.Estado | 192.168.4.53:4660 | 6:0X:202 | Read+Write | Always
MSA_UM_Alumb_Corona.Fallo | 192.168.4.53:4660 | 6:0X:333 | Read+Write | Always
MSA_UM_Alumb_Corona.Horario_A | 192.168.4.53:4660 | 6:3X:893T80 | Read+Write | Always
MSA_UM_Alumb_Corona.Horario_estado | 192.168.4.53:4660 | 6:0X:329 | Read+Write | Always
MSA_UM_Alumb_Corona.Manual_horario | 192.168.4.53:4660 | 6:0X:330 | Read+Write | Always
MSA_UM_Alumb_Corona.Marcha_paro | 192.168.4.53:4660 | 6:0X:331 | Read+Write | Always
MSA_UM_Alumb_Corona.Orden | 192.168.4.53:4660 | 6:0X:266 | Read+Write | Always
MSA_UM_Alumb_Encants_Dcha.Estado | 192.168.4.53:4660 | 2:0X:206 | Read+Write | Always
MSA_UM_Alumb_Encants_Dcha.Fallo | 192.168.4.53:4660 | 2:0X:357 | Read+Write | Always
MSA_UM_Alumb_Encants_Dcha.Horario_A | 192.168.4.53:4660 | 2:3X:761T80 | Read+Write | Always
MSA_UM_Alumb_Encants_Dcha.Horario_estado | 192.168.4.53:4660 | 2:0X:353 | Read+Write | Always
MSA_UM_Alumb_Encants_Dcha.Manual_horario | 192.168.4.53:4660 | 2:0X:354 | Read+Write | Always
MSA_UM_Alumb_Encants_Dcha.Marcha_paro | 192.168.4.53:4660 | 2:0X:355 | Read+Write | Always
MSA_UM_Alumb_Encants_Dcha.Orden | 192.168.4.53:4660 | 2:0X:270 | Read+Write | Always
MSA_UM_Alumb_Encants_Dcha_Vigi.Estado | 192.168.4.53:4660 | 2:0X:207 | Read+Write | Always
MSA_UM_Alumb_Encants_Dcha_Vigi.Fallo | 192.168.4.53:4660 | 2:0X:365 | Read+Write | Always
MSA_UM_Alumb_Encants_Dcha_Vigi.Horario_A | 192.168.4.53:4660 | 2:3X:717T80 | Read+Write | Always
MSA_UM_Alumb_Encants_Dcha_Vigi.Horario_estado | 192.168.4.53:4660 | 2:0X:361 | Read+Write | Always
MSA_UM_Alumb_Encants_Dcha_Vigi.Manual_horario | 192.168.4.53:4660 | 2:0X:362 | Read+Write | Always
MSA_UM_Alumb_Encants_Dcha_Vigi.Marcha_paro | 192.168.4.53:4660 | 2:0X:363 | Read+Write | Always
MSA_UM_Alumb_Encants_Dcha_Vigi.Orden | 192.168.4.53:4660 | 2:0X:273 | Read+Write | Always
MSA_UM_Alumb_Escalera.Estado | 192.168.4.53:4660 | 3:0X:206 | Read+Write | Always
MSA_UM_Alumb_Escalera.Fallo | 192.168.4.53:4660 | 3:0X:413 | Read+Write | Always
MSA_UM_Alumb_Escalera.Horario_A | 192.168.4.53:4660 | 3:3X:453T80 | Read+Write | Always
MSA_UM_Alumb_Escalera.Horario_estado | 192.168.4.53:4660 | 3:0X:409 | Read+Write | Always
MSA_UM_Alumb_Escalera.Manual_horario | 192.168.4.53:4660 | 3:0X:410 | Read+Write | Always
MSA_UM_Alumb_Escalera.Marcha_paro | 192.168.4.53:4660 | 3:0X:411 | Read+Write | Always
MSA_UM_Alumb_Escalera.Orden | 192.168.4.53:4660 | 3:0X:270 | Read+Write | Always
MSA_UM_Alumb_Esp_Multifunc.Estado | 192.168.4.53:4660 | 6:0X:206 | Read+Write | Always
MSA_UM_Alumb_Esp_Multifunc.Fallo | 192.168.4.53:4660 | 6:0X:365 | Read+Write | Always
MSA_UM_Alumb_Esp_Multifunc.Horario_A | 192.168.4.53:4660 | 6:3X:717T80 | Read+Write | Always
MSA_UM_Alumb_Esp_Multifunc.Horario_estado | 192.168.4.53:4660 | 6:0X:361 | Read+Write | Always
MSA_UM_Alumb_Esp_Multifunc.Manual_horario | 192.168.4.53:4660 | 6:0X:362 | Read+Write | Always
MSA_UM_Alumb_Esp_Multifunc.Marcha_paro | 192.168.4.53:4660 | 6:0X:363 | Read+Write | Always
MSA_UM_Alumb_Esp_Multifunc.Orden | 192.168.4.53:4660 | 6:0X:270 | Read+Write | Always
MSA_UM_Alumb_Fachada_3.Estado | 192.168.4.53:4660 | 3:0X:202 | Read+Write | Always
MSA_UM_Alumb_Fachada_3.Fallo | 192.168.4.53:4660 | 3:0X:325 | Read+Write | Always
MSA_UM_Alumb_Fachada_3.Horario_A | 192.168.4.53:4660 | 3:3X:937T80 | Read+Write | Always
MSA_UM_Alumb_Fachada_3.Horario_estado | 192.168.4.53:4660 | 3:0X:321 | Read+Write | Always
MSA_UM_Alumb_Fachada_3.Manual_horario | 192.168.4.53:4660 | 3:0X:322 | Read+Write | Always
MSA_UM_Alumb_Fachada_3.Marcha_paro | 192.168.4.53:4660 | 3:0X:323 | Read+Write | Always
MSA_UM_Alumb_Fachada_3.Orden | 192.168.4.53:4660 | 3:0X:266 | Read+Write | Always
MSA_UM_Alumb_Fachada_4.Estado | 192.168.4.53:4660 | 3:0X:203 | Read+Write | Always
MSA_UM_Alumb_Fachada_4.Fallo | 192.168.4.53:4660 | 3:0X:333 | Read+Write | Always
MSA_UM_Alumb_Fachada_4.Horario_A | 192.168.4.53:4660 | 3:3X:893T80 | Read+Write | Always
MSA_UM_Alumb_Fachada_4.Horario_estado | 192.168.4.53:4660 | 3:0X:329 | Read+Write | Always
MSA_UM_Alumb_Fachada_4.Manual_horario | 192.168.4.53:4660 | 3:0X:330 | Read+Write | Always
MSA_UM_Alumb_Fachada_4.Marcha_paro | 192.168.4.53:4660 | 3:0X:331 | Read+Write | Always
MSA_UM_Alumb_Fachada_4.Orden | 192.168.4.53:4660 | 3:0X:267 | Read+Write | Always
MSA_UM_Alumb_Fresco_1.Estado | 192.168.4.53:4660 | 2:0X:203 | Read+Write | Always
MSA_UM_Alumb_Fresco_1.Fallo | 192.168.4.53:4660 | 2:0X:333 | Read+Write | Always
MSA_UM_Alumb_Fresco_1.Horario_A | 192.168.4.53:4660 | 2:3X:893T80 | Read+Write | Always
MSA_UM_Alumb_Fresco_1.Horario_estado | 192.168.4.53:4660 | 2:0X:329 | Read+Write | Always
MSA_UM_Alumb_Fresco_1.Manual_horario | 192.168.4.53:4660 | 2:0X:330 | Read+Write | Always
MSA_UM_Alumb_Fresco_1.Marcha_paro | 192.168.4.53:4660 | 2:0X:331 | Read+Write | Always
MSA_UM_Alumb_Fresco_1.Orden | 192.168.4.53:4660 | 2:0X:267 | Read+Write | Always
MSA_UM_Alumb_Fresco_2.Estado | 192.168.4.53:4660 | 2:0X:204 | Read+Write | Always
MSA_UM_Alumb_Fresco_2.Fallo | 192.168.4.53:4660 | 2:0X:341 | Read+Write | Always
MSA_UM_Alumb_Fresco_2.Horario_A | 192.168.4.53:4660 | 2:3X:849T80 | Read+Write | Always
MSA_UM_Alumb_Fresco_2.Horario_estado | 192.168.4.53:4660 | 2:0X:337 | Read+Write | Always
MSA_UM_Alumb_Fresco_2.Manual_horario | 192.168.4.53:4660 | 2:0X:338 | Read+Write | Always
MSA_UM_Alumb_Fresco_2.Marcha_paro | 192.168.4.53:4660 | 2:0X:339 | Read+Write | Always
MSA_UM_Alumb_Fresco_2.Orden | 192.168.4.53:4660 | 2:0X:268 | Read+Write | Always
MSA_UM_Alumb_Fresco_Vigi.Estado | 192.168.4.53:4660 | 2:0X:205 | Read+Write | Always
MSA_UM_Alumb_Fresco_Vigi.Fallo | 192.168.4.53:4660 | 2:0X:349 | Read+Write | Always
MSA_UM_Alumb_Fresco_Vigi.Horario_A | 192.168.4.53:4660 | 2:3X:805T80 | Read+Write | Always
MSA_UM_Alumb_Fresco_Vigi.Horario_estado | 192.168.4.53:4660 | 2:0X:345 | Read+Write | Always
MSA_UM_Alumb_Fresco_Vigi.Manual_horario | 192.168.4.53:4660 | 2:0X:346 | Read+Write | Always
MSA_UM_Alumb_Fresco_Vigi.Marcha_paro | 192.168.4.53:4660 | 2:0X:347 | Read+Write | Always
MSA_UM_Alumb_Fresco_Vigi.Orden | 192.168.4.53:4660 | 2:0X:269 | Read+Write | Always
MSA_UM_Alumb_General_Zonas_Estado | 192.168.4.53:4660 | 10:0X:207 | Read+Write | Always
MSA_UM_Alumb_Gral_1.Estado | 192.168.4.53:4660 | 10:0X:202 | Read+Write | Always
MSA_UM_Alumb_Gral_1.Fallo | 192.168.4.53:4660 | 10:0X:325 | Read+Write | Always
MSA_UM_Alumb_Gral_1.Horario_A | 192.168.4.53:4660 | 10:3X:937T80 | Read+Write | Always
MSA_UM_Alumb_Gral_1.Horario_estado | 192.168.4.53:4660 | 10:0X:321 | Read+Write | Always
MSA_UM_Alumb_Gral_1.Manual_horario | 192.168.4.53:4660 | 10:0X:322 | Read+Write | Always
MSA_UM_Alumb_Gral_1.Marcha_paro | 192.168.4.53:4660 | 10:0X:323 | Read+Write | Always
MSA_UM_Alumb_Gral_1.Orden | 192.168.4.53:4660 | 10:0X:266 | Read+Write | Always
MSA_UM_Alumb_Gral_2.Estado | 192.168.4.53:4660 | 10:0X:203 | Read+Write | Always
MSA_UM_Alumb_Gral_2.Fallo | 192.168.4.53:4660 | 10:0X:333 | Read+Write | Always
MSA_UM_Alumb_Gral_2.Horario_A | 192.168.4.53:4660 | 10:3X:893T80 | Read+Write | Always
MSA_UM_Alumb_Gral_2.Horario_estado | 192.168.4.53:4660 | 10:0X:329 | Read+Write | Always
MSA_UM_Alumb_Gral_2.Manual_horario | 192.168.4.53:4660 | 10:0X:330 | Read+Write | Always
MSA_UM_Alumb_Gral_2.Marcha_paro | 192.168.4.53:4660 | 10:0X:331 | Read+Write | Always
MSA_UM_Alumb_Gral_2.Orden | 192.168.4.53:4660 | 10:0X:267 | Read+Write | Always
MSA_UM_Alumb_Gral_Izq_Encants.Estado | 192.168.4.53:4660 | 2:0X:201 | Read+Write | Always
MSA_UM_Alumb_Gral_Izq_Encants.Fallo | 192.168.4.53:4660 | 2:0X:317 | Read+Write | Always
MSA_UM_Alumb_Gral_Izq_Encants.Horario_A | 192.168.4.53:4660 | 2:3X:981T80 | Read+Write | Always
MSA_UM_Alumb_Gral_Izq_Encants.Horario_estado | 192.168.4.53:4660 | 2:0X:313 | Read+Write | Always
MSA_UM_Alumb_Gral_Izq_Encants.Manual_horario | 192.168.4.53:4660 | 2:0X:314 | Read+Write | Always
MSA_UM_Alumb_Gral_Izq_Encants.Marcha_paro | 192.168.4.53:4660 | 2:0X:315 | Read+Write | Always
MSA_UM_Alumb_Gral_Izq_Encants.Orden | 192.168.4.53:4660 | 2:0X:265 | Read+Write | Always
MSA_UM_Alumb_Gral_vigi.Estado | 192.168.4.53:4660 | 10:0X:201 | Read+Write | Always
MSA_UM_Alumb_Gral_vigi.Fallo | 192.168.4.53:4660 | 10:0X:317 | Read+Write | Always
MSA_UM_Alumb_Gral_vigi.Horario_A | 192.168.4.53:4660 | 10:3X:981T80 | Read+Write | Always
MSA_UM_Alumb_Gral_vigi.Horario_estado | 192.168.4.53:4660 | 10:0X:313 | Read+Write | Always
MSA_UM_Alumb_Gral_vigi.Manual_horario | 192.168.4.53:4660 | 10:0X:314 | Read+Write | Always
MSA_UM_Alumb_Gral_vigi.Marcha_paro | 192.168.4.53:4660 | 10:0X:315 | Read+Write | Always
MSA_UM_Alumb_Gral_vigi.Orden | 192.168.4.53:4660 | 10:0X:265 | Read+Write | Always
MSA_UM_Alumb_Izq_Encants_Vigi.Estado | 192.168.4.53:4660 | 2:0X:202 | Read+Write | Always
MSA_UM_Alumb_Izq_Encants_Vigi.Fallo | 192.168.4.53:4660 | 2:0X:325 | Read+Write | Always
MSA_UM_Alumb_Izq_Encants_Vigi.Horario_A | 192.168.4.53:4660 | 2:3X:937T80 | Read+Write | Always
MSA_UM_Alumb_Izq_Encants_Vigi.Horario_estado | 192.168.4.53:4660 | 2:0X:321 | Read+Write | Always
MSA_UM_Alumb_Izq_Encants_Vigi.Manual_horario | 192.168.4.53:4660 | 2:0X:322 | Read+Write | Always
MSA_UM_Alumb_Izq_Encants_Vigi.Marcha_paro | 192.168.4.53:4660 | 2:0X:323 | Read+Write | Always
MSA_UM_Alumb_Izq_Encants_Vigi.Orden | 192.168.4.53:4660 | 2:0X:266 | Read+Write | Always
MSA_UM_Alumb_Marquesina_1.Estado | 192.168.4.53:4660 | 2:0X:222 | Read+Write | Always
MSA_UM_Alumb_Marquesina_1.Fallo | 192.168.4.53:4660 | 2:0X:413 | Read+Write | Always
MSA_UM_Alumb_Marquesina_1.Horario_A | 192.168.4.53:4660 | 2:3X:453T80 | Read+Write | Always
MSA_UM_Alumb_Marquesina_1.Horario_estado | 192.168.4.53:4660 | 2:0X:409 | Read+Write | Always
MSA_UM_Alumb_Marquesina_1.Manual_horario | 192.168.4.53:4660 | 2:0X:410 | Read+Write | Always
MSA_UM_Alumb_Marquesina_1.Marcha_paro | 192.168.4.53:4660 | 2:0X:411 | Read+Write | Always
MSA_UM_Alumb_Marquesina_1.Orden | 192.168.4.53:4660 | 2:0X:280 | Read+Write | Always
MSA_UM_Alumb_Marquesina_2.Estado | 192.168.4.53:4660 | 3:0X:201 | Read+Write | Always
MSA_UM_Alumb_Marquesina_2.Fallo | 192.168.4.53:4660 | 3:0X:317 | Read+Write | Always
MSA_UM_Alumb_Marquesina_2.Horario_A | 192.168.4.53:4660 | 3:3X:981T80 | Read+Write | Always
MSA_UM_Alumb_Marquesina_2.Horario_estado | 192.168.4.53:4660 | 3:0X:313 | Read+Write | Always
MSA_UM_Alumb_Marquesina_2.Manual_horario | 192.168.4.53:4660 | 3:0X:314 | Read+Write | Always
MSA_UM_Alumb_Marquesina_2.Marcha_paro | 192.168.4.53:4660 | 3:0X:315 | Read+Write | Always
MSA_UM_Alumb_Marquesina_2.Orden | 192.168.4.53:4660 | 3:0X:265 | Read+Write | Always
MSA_UM_Alumb_pasillos.Estado | 192.168.4.53:4660 | 6:0X:222 | Read+Write | Always
MSA_UM_Alumb_pasillos.Fallo | 192.168.4.53:4660 | 6:0X:413 | Read+Write | Always
MSA_UM_Alumb_pasillos.Horario_A | 192.168.4.53:4660 | 6:3X:453T80 | Read+Write | Always
MSA_UM_Alumb_pasillos.Horario_estado | 192.168.4.53:4660 | 6:0X:409 | Read+Write | Always
MSA_UM_Alumb_pasillos.Manual_horario | 192.168.4.53:4660 | 6:0X:410 | Read+Write | Always
MSA_UM_Alumb_pasillos.Marcha_paro | 192.168.4.53:4660 | 6:0X:411 | Read+Write | Always
MSA_UM_Alumb_pasillos.Orden | 192.168.4.53:4660 | 6:0X:278 | Read+Write | Always
MSA_UM_Alumb_Patio_testa.Estado | 192.168.4.53:4660 | 6:0X:201 | Read+Write | Always
MSA_UM_Alumb_Patio_testa.Fallo | 192.168.4.53:4660 | 6:0X:317 | Read+Write | Always
MSA_UM_Alumb_Patio_testa.Horario_A | 192.168.4.53:4660 | 6:3X:981T80 | Read+Write | Always
MSA_UM_Alumb_Patio_testa.Horario_estado | 192.168.4.53:4660 | 6:0X:313 | Read+Write | Always
MSA_UM_Alumb_Patio_testa.Manual_horario | 192.168.4.53:4660 | 6:0X:314 | Read+Write | Always
MSA_UM_Alumb_Patio_testa.Marcha_paro | 192.168.4.53:4660 | 6:0X:315 | Read+Write | Always
MSA_UM_Alumb_Patio_testa.Orden | 192.168.4.53:4660 | 6:0X:265 | Read+Write | Always
MSA_UM_Alumb_Pergolas_1_Urgel.Estado | 192.168.4.53:4660 | 1:0X:257 | Read+Write | Always
MSA_UM_Alumb_Pergolas_1_Urgel.Fallo | 192.168.4.53:4660 | 1:0X:421 | Read+Write | Always
MSA_UM_Alumb_Pergolas_1_Urgel.Horario_A | 192.168.4.53:4660 | 1:3X:409T80 | Read+Write | Always
MSA_UM_Alumb_Pergolas_1_Urgel.Horario_estado | 192.168.4.53:4660 | 1:0X:417 | Read+Write | Always
MSA_UM_Alumb_Pergolas_1_Urgel.Manual_horario | 192.168.4.53:4660 | 1:0X:418 | Read+Write | Always
MSA_UM_Alumb_Pergolas_1_Urgel.Marcha_paro | 192.168.4.53:4660 | 1:0X:419 | Read+Write | Always
MSA_UM_Alumb_Pergolas_1_Urgel.Orden | 192.168.4.53:4660 | 1:0X:293 | Read+Write | Always
MSA_UM_Alumb_Pergolas_2_Urgel.Estado | 192.168.4.53:4660 | 1:0X:258 | Read+Write | Always
MSA_UM_Alumb_Pergolas_2_Urgel.Fallo | 192.168.4.53:4660 | 1:0X:429 | Read+Write | Always
MSA_UM_Alumb_Pergolas_2_Urgel.Horario_A | 192.168.4.53:4660 | 1:3X:365T80 | Read+Write | Always
MSA_UM_Alumb_Pergolas_2_Urgel.Horario_estado | 192.168.4.53:4660 | 1:0X:425 | Read+Write | Always
MSA_UM_Alumb_Pergolas_2_Urgel.Manual_horario | 192.168.4.53:4660 | 1:0X:426 | Read+Write | Always
MSA_UM_Alumb_Pergolas_2_Urgel.Marcha_paro | 192.168.4.53:4660 | 1:0X:427 | Read+Write | Always
MSA_UM_Alumb_Pergolas_2_Urgel.Orden | 192.168.4.53:4660 | 1:0X:294 | Read+Write | Always
MSA_UM_Alumb_Plaza_1.Estado | 192.168.4.53:4660 | 7:0X:202 | Read+Write | Always
MSA_UM_Alumb_Plaza_1.Fallo | 192.168.4.53:4660 | 7:0X:325 | Read+Write | Always
MSA_UM_Alumb_Plaza_1.Horario_A | 192.168.4.53:4660 | 7:3X:937T80 | Read+Write | Always
MSA_UM_Alumb_Plaza_1.Horario_estado | 192.168.4.53:4660 | 7:0X:321 | Read+Write | Always
MSA_UM_Alumb_Plaza_1.Manual_horario | 192.168.4.53:4660 | 7:0X:322 | Read+Write | Always
MSA_UM_Alumb_Plaza_1.Marcha_paro | 192.168.4.53:4660 | 7:0X:323 | Read+Write | Always
MSA_UM_Alumb_Plaza_1.Orden | 192.168.4.53:4660 | 7:0X:266 | Read+Write | Always
MSA_UM_Alumb_Plaza_2.Estado | 192.168.4.53:4660 | 7:0X:203 | Read+Write | Always
MSA_UM_Alumb_Plaza_2.Fallo | 192.168.4.53:4660 | 7:0X:333 | Read+Write | Always
MSA_UM_Alumb_Plaza_2.Horario_A | 192.168.4.53:4660 | 7:3X:893T80 | Read+Write | Always
MSA_UM_Alumb_Plaza_2.Horario_estado | 192.168.4.53:4660 | 7:0X:329 | Read+Write | Always
MSA_UM_Alumb_Plaza_2.Manual_horario | 192.168.4.53:4660 | 7:0X:330 | Read+Write | Always
MSA_UM_Alumb_Plaza_2.Marcha_paro | 192.168.4.53:4660 | 7:0X:331 | Read+Write | Always
MSA_UM_Alumb_Plaza_2.Orden | 192.168.4.53:4660 | 7:0X:267 | Read+Write | Always
MSA_UM_Alumb_Plaza_B.Estado | 192.168.4.53:4660 | 3:0X:204 | Read+Write | Always
MSA_UM_Alumb_Plaza_B.Fallo | 192.168.4.53:4660 | 3:0X:341 | Read+Write | Always
MSA_UM_Alumb_Plaza_B.Horario_A | 192.168.4.53:4660 | 3:3X:849T80 | Read+Write | Always
MSA_UM_Alumb_Plaza_B.Horario_estado | 192.168.4.53:4660 | 3:0X:337 | Read+Write | Always
MSA_UM_Alumb_Plaza_B.Manual_horario | 192.168.4.53:4660 | 3:0X:338 | Read+Write | Always
MSA_UM_Alumb_Plaza_B.Marcha_paro | 192.168.4.53:4660 | 3:0X:339 | Read+Write | Always
MSA_UM_Alumb_Plaza_B.Orden | 192.168.4.53:4660 | 3:0X:268 | Read+Write | Always
MSA_UM_Alumb_Plaza_M.Estado | 192.168.4.53:4660 | 3:0X:205 | Read+Write | Always
MSA_UM_Alumb_Plaza_M.Fallo | 192.168.4.53:4660 | 3:0X:349 | Read+Write | Always
MSA_UM_Alumb_Plaza_M.Horario_A | 192.168.4.53:4660 | 3:3X:805T80 | Read+Write | Always
MSA_UM_Alumb_Plaza_M.Horario_estado | 192.168.4.53:4660 | 3:0X:345 | Read+Write | Always
MSA_UM_Alumb_Plaza_M.Manual_horario | 192.168.4.53:4660 | 3:0X:346 | Read+Write | Always
MSA_UM_Alumb_Plaza_M.Marcha_paro | 192.168.4.53:4660 | 3:0X:347 | Read+Write | Always
MSA_UM_Alumb_Plaza_M.Orden | 192.168.4.53:4660 | 3:0X:269 | Read+Write | Always
MSA_UM_Alumb_Reserva.Estado | 192.168.4.53:4660 | 10:0X:206 | Read+Write | Always
MSA_UM_Alumb_Reserva.Fallo | 192.168.4.53:4660 | 10:0X:357 | Read+Write | Always
MSA_UM_Alumb_Reserva.Horario_A | 192.168.4.53:4660 | 10:3X:761T80 | Read+Write | Always
MSA_UM_Alumb_Reserva.Horario_estado | 192.168.4.53:4660 | 10:0X:353 | Read+Write | Always
MSA_UM_Alumb_Reserva.Manual_horario | 192.168.4.53:4660 | 10:0X:354 | Read+Write | Always
MSA_UM_Alumb_Reserva.Marcha_paro | 192.168.4.53:4660 | 10:0X:355 | Read+Write | Always
MSA_UM_Alumb_Reserva.Orden | 192.168.4.53:4660 | 10:0X:270 | Read+Write | Always
MSA_UM_Alumb_Reserva_01.Estado | 192.168.4.53:4660 | 7:0X:201 | Read+Write | Always
MSA_UM_Alumb_Reserva_01.Fallo | 192.168.4.53:4660 | 7:0X:317 | Read+Write | Always
MSA_UM_Alumb_Reserva_01.Horario_A | 192.168.4.53:4660 | 7:3X:981T80 | Read+Write | Always
MSA_UM_Alumb_Reserva_01.Horario_estado | 192.168.4.53:4660 | 7:0X:313 | Read+Write | Always
MSA_UM_Alumb_Reserva_01.Manual_horario | 192.168.4.53:4660 | 7:0X:314 | Read+Write | Always
MSA_UM_Alumb_Reserva_01.Marcha_paro | 192.168.4.53:4660 | 7:0X:315 | Read+Write | Always
MSA_UM_Alumb_Reserva_01.Orden | 192.168.4.53:4660 | 7:0X:265 | Read+Write | Always
MSA_UM_Alumb_Reserva_2.Estado | 192.168.4.53:4660 | 11:0X:201 | Read+Write | Always
MSA_UM_Alumb_Reserva_2.Fallo | 192.168.4.53:4660 | 11:0X:317 | Read+Write | Always
MSA_UM_Alumb_Reserva_2.Horario_A | 192.168.4.53:4660 | 11:3X:981T80 | Read+Write | Always
MSA_UM_Alumb_Reserva_2.Horario_estado | 192.168.4.53:4660 | 11:0X:313 | Read+Write | Always
MSA_UM_Alumb_Reserva_2.Manual_horario | 192.168.4.53:4660 | 11:0X:314 | Read+Write | Always
MSA_UM_Alumb_Reserva_2.Marcha_paro | 192.168.4.53:4660 | 11:0X:315 | Read+Write | Always
MSA_UM_Alumb_Reserva_2.Orden | 192.168.4.53:4660 | 11:0X:265 | Read+Write | Always
MSA_UM_Alumb_S_Tecnicas.Estado | 192.168.4.53:4660 | 10:0X:205 | Read+Write | Always
MSA_UM_Alumb_S_Tecnicas.Fallo | 192.168.4.53:4660 | 10:0X:349 | Read+Write | Always
MSA_UM_Alumb_S_Tecnicas.Horario_A | 192.168.4.53:4660 | 10:3X:805T80 | Read+Write | Always
MSA_UM_Alumb_S_Tecnicas.Horario_estado | 192.168.4.53:4660 | 10:0X:345 | Read+Write | Always
MSA_UM_Alumb_S_Tecnicas.Manual_horario | 192.168.4.53:4660 | 10:0X:346 | Read+Write | Always
MSA_UM_Alumb_S_Tecnicas.Marcha_paro | 192.168.4.53:4660 | 10:0X:347 | Read+Write | Always
MSA_UM_Alumb_S_Tecnicas.Orden | 192.168.4.53:4660 | 10:0X:269 | Read+Write | Always
MSA_UM_Alumb_Travelator_Gral.Estado | 192.168.4.53:4660 | 2:0X:220 | Read+Write | Always
MSA_UM_Alumb_Travelator_Gral.Fallo | 192.168.4.53:4660 | 2:0X:405 | Read+Write | Always
MSA_UM_Alumb_Travelator_Gral.Horario_A | 192.168.4.53:4660 | 2:3X:497T80 | Read+Write | Always
MSA_UM_Alumb_Travelator_Gral.Horario_estado | 192.168.4.53:4660 | 2:0X:401 | Read+Write | Always
MSA_UM_Alumb_Travelator_Gral.Manual_horario | 192.168.4.53:4660 | 2:0X:402 | Read+Write | Always
MSA_UM_Alumb_Travelator_Gral.Marcha_paro | 192.168.4.53:4660 | 2:0X:403 | Read+Write | Always
MSA_UM_Alumb_Travelator_Gral.Orden | 192.168.4.53:4660 | 2:0X:278 | Read+Write | Always
MSA_UM_Alumb_Travelator_Vigi.Estado | 192.168.4.53:4660 | 2:0X:219 | Read+Write | Always
MSA_UM_Alumb_Travelator_Vigi.Fallo | 192.168.4.53:4660 | 2:0X:397 | Read+Write | Always
MSA_UM_Alumb_Travelator_Vigi.Horario_A | 192.168.4.53:4660 | 2:3X:541T80 | Read+Write | Always
MSA_UM_Alumb_Travelator_Vigi.Horario_estado | 192.168.4.53:4660 | 2:0X:393 | Read+Write | Always
MSA_UM_Alumb_Travelator_Vigi.Manual_horario | 192.168.4.53:4660 | 2:0X:394 | Read+Write | Always
MSA_UM_Alumb_Travelator_Vigi.Marcha_paro | 192.168.4.53:4660 | 2:0X:395 | Read+Write | Always
MSA_UM_Alumb_Travelator_Vigi.Orden | 192.168.4.53:4660 | 2:0X:277 | Read+Write | Always
MSA_UM_Alumb_Vigi_pasillos.Estado | 192.168.4.53:4660 | 6:0X:218 | Read+Write | Always
MSA_UM_Alumb_Vigi_pasillos.Fallo | 192.168.4.53:4660 | 6:0X:381 | Read+Write | Always
MSA_UM_Alumb_Vigi_pasillos.Horario_A | 192.168.4.53:4660 | 6:3X:629T80 | Read+Write | Always
MSA_UM_Alumb_Vigi_pasillos.Horario_estado | 192.168.4.53:4660 | 6:0X:377 | Read+Write | Always
MSA_UM_Alumb_Vigi_pasillos.Manual_horario | 192.168.4.53:4660 | 6:0X:378 | Read+Write | Always
MSA_UM_Alumb_Vigi_pasillos.Marcha_paro | 192.168.4.53:4660 | 6:0X:379 | Read+Write | Always
MSA_UM_Alumb_Vigi_pasillos.Orden | 192.168.4.53:4660 | 6:0X:274 | Read+Write | Always
MSA_UM_Bomba_AC_A_Geoterm.Horario_A | 192.168.4.53:4660 | 5:3X:937T80 | Read+Write | Always
MSA_UM_Bomba_AC_A_Geoterm.Horario_estado | 192.168.4.53:4660 | 5:0X:321 | Read+Write | Always
MSA_UM_Bomba_AC_A_Geoterm.Manual_horario | 192.168.4.53:4660 | 5:0X:322 | Read+Write | Always
MSA_UM_Bomba_AC_A_Geoterm.Marcha_paro | 192.168.4.53:4660 | 5:0X:323 | Read+Write | Always
MSA_UM_Bomba_AC_A_Geoterm.Reset_horas | 192.168.4.53:4660 | 5:0X:324 | Read+Write | Always
MSA_UM_Bomba_AC_A_Geoterm_1.Alarma_variador | 192.168.4.53:4660 | 8:0X:201 | Read+Write | Always
MSA_UM_Bomba_AC_A_Geoterm_1.Estado | 192.168.4.53:4660 | 5:0X:223 | Read+Write | Always
MSA_UM_Bomba_AC_A_Geoterm_1.Fallo | 192.168.4.53:4660 | 5:0X:325 | Read+Write | Always
MSA_UM_Bomba_AC_A_Geoterm_1.Horas_funcionam | 192.168.4.53:4660 | 5:3X:804 | Read+Write | Always
MSA_UM_Bomba_AC_A_Geoterm_1.Orden | 192.168.4.53:4660 | 5:0X:283 | Read+Write | Always
MSA_UM_Bomba_AC_A_Geoterm_2.Alarma_variador | 192.168.4.53:4660 | 8:0X:202 | Read+Write | Always
MSA_UM_Bomba_AC_A_Geoterm_2.Estado | 192.168.4.53:4660 | 5:0X:224 | Read+Write | Always
MSA_UM_Bomba_AC_A_Geoterm_2.Fallo | 192.168.4.53:4660 | 5:0X:326 | Read+Write | Always
MSA_UM_Bomba_AC_A_Geoterm_2.Horas_funcionam | 192.168.4.53:4660 | 5:3X:760 | Read+Write | Always
MSA_UM_Bomba_AC_A_Geoterm_2.Orden | 192.168.4.53:4660 | 5:0X:284 | Read+Write | Always
MSA_UM_Bomba_AF_A_Geoterm.Horario_A | 192.168.4.53:4660 | 5:3X:849T80 | Read+Write | Always
MSA_UM_Bomba_AF_A_Geoterm.Horario_estado | 192.168.4.53:4660 | 5:0X:361 | Read+Write | Always
MSA_UM_Bomba_AF_A_Geoterm.Manual_horario | 192.168.4.53:4660 | 5:0X:362 | Read+Write | Always
MSA_UM_Bomba_AF_A_Geoterm.Marcha_paro | 192.168.4.53:4660 | 5:0X:363 | Read+Write | Always
MSA_UM_Bomba_AF_A_Geoterm.Reset_horas | 192.168.4.53:4660 | 5:0X:364 | Read+Write | Always
MSA_UM_Bomba_AF_A_Geoterm_1.Alarma_variador | 192.168.4.53:4660 | 8:0X:203 | Read+Write | Always
MSA_UM_Bomba_AF_A_Geoterm_1.Estado | 192.168.4.53:4660 | 5:0X:204 | Read+Write | Always
MSA_UM_Bomba_AF_A_Geoterm_1.Fallo | 192.168.4.53:4660 | 5:0X:367 | Read+Write | Always
MSA_UM_Bomba_AF_A_Geoterm_1.Horas_funcionam | 192.168.4.53:4660 | 5:3X:540 | Read+Write | Always
MSA_UM_Bomba_AF_A_Geoterm_1.Orden | 192.168.4.53:4660 | 5:0X:275 | Read+Write | Always
MSA_UM_Bomba_AF_A_Geoterm_2.Alarma_variador | 192.168.4.53:4660 | 8:0X:204 | Read+Write | Always
MSA_UM_Bomba_AF_A_Geoterm_2.Estado | 192.168.4.53:4660 | 5:0X:205 | Read+Write | Always
MSA_UM_Bomba_AF_A_Geoterm_2.Fallo | 192.168.4.53:4660 | 5:0X:366 | Read+Write | Always
MSA_UM_Bomba_AF_A_Geoterm_2.Horas_funcionam | 192.168.4.53:4660 | 5:3X:496 | Read+Write | Always
MSA_UM_Bomba_AF_A_Geoterm_2.Orden | 192.168.4.53:4660 | 5:0X:268 | Read+Write | Always
MSA_UM_Bomba_calor_1.Estado | 192.168.4.53:4660 | 4:0X:221 | Read+Write | Always
MSA_UM_Bomba_calor_1.Horas_funcionam | 192.168.4.53:4660 | 4:3X:848 | Read+Write | Always
MSA_UM_Bomba_calor_2.Estado | 192.168.4.53:4660 | 4:0X:222 | Read+Write | Always
MSA_UM_Bomba_calor_2.Horas_funcionam | 192.168.4.53:4660 | 4:3X:804 | Read+Write | Always
MSA_UM_Bomba_Condens_1.Estado | 192.168.4.53:4660 | 4:0X:217 | Read+Write | Always
MSA_UM_Bomba_Condens_1.Horas_funcionam | 192.168.4.53:4660 | 4:3X:1024 | Read+Write | Always
MSA_UM_Bomba_Condens_2.Estado | 192.168.4.53:4660 | 4:0X:218 | Read+Write | Always
MSA_UM_Bomba_Condens_2.Horas_funcionam | 192.168.4.53:4660 | 4:3X:980 | Read+Write | Always
MSA_UM_Bomba_frio_1.Estado | 192.168.4.53:4660 | 4:0X:219 | Read+Write | Always
MSA_UM_Bomba_frio_1.Horas_funcionam | 192.168.4.53:4660 | 4:3X:936 | Read+Write | Always
MSA_UM_Bomba_frio_2.Estado | 192.168.4.53:4660 | 4:0X:220 | Read+Write | Always
MSA_UM_Bomba_frio_2.Horas_funcionam | 192.168.4.53:4660 | 4:3X:892 | Read+Write | Always
MSA_UM_Bombas_ACS_P_Inf.Horario_A | 192.168.4.53:4660 | 5:3X:893T80 | Read+Write | Always
MSA_UM_Bombas_ACS_P_Inf.Horario_estado | 192.168.4.53:4660 | 5:0X:329 | Read+Write | Always
MSA_UM_Bombas_ACS_P_Inf.Manual_horario | 192.168.4.53:4660 | 5:0X:330 | Read+Write | Always
MSA_UM_Bombas_ACS_P_Inf.Marcha_paro | 192.168.4.53:4660 | 5:0X:331 | Read+Write | Always
MSA_UM_Bombas_ACS_P_Inf.Reset_horas | 192.168.4.53:4660 | 5:0X:332 | Read+Write | Always
MSA_UM_Bombas_ACS_P_Inf_1.Alarma_variador | 192.168.4.53:4660 | 5:0X:229 | Read+Write | Always
MSA_UM_Bombas_ACS_P_Inf_1.Estado | 192.168.4.53:4660 | 5:0X:219 | Read+Write | Always
MSA_UM_Bombas_ACS_P_Inf_1.Fallo | 192.168.4.53:4660 | 5:0X:333 | Read+Write | Always
MSA_UM_Bombas_ACS_P_Inf_1.Horas_funcionam | 192.168.4.53:4660 | 5:3X:716 | Read+Write | Always
MSA_UM_Bombas_ACS_P_Inf_1.Orden | 192.168.4.53:4660 | 5:0X:279 | Read+Write | Always
MSA_UM_Bombas_ACS_P_Inf_2.Alarma_variador | 192.168.4.53:4660 | 5:0X:231 | Read+Write | Always
MSA_UM_Bombas_ACS_P_Inf_2.Estado | 192.168.4.53:4660 | 5:0X:220 | Read+Write | Always
MSA_UM_Bombas_ACS_P_Inf_2.Fallo | 192.168.4.53:4660 | 5:0X:334 | Read+Write | Always
MSA_UM_Bombas_ACS_P_Inf_2.Horas_funcionam | 192.168.4.53:4660 | 5:3X:672 | Read+Write | Always
MSA_UM_Bombas_ACS_P_Inf_2.Orden | 192.168.4.53:4660 | 5:0X:280 | Read+Write | Always
MSA_UM_Bombas_ACS_PB.Horario_A | 192.168.4.53:4660 | 5:3X:761T80 | Read+Write | Always
MSA_UM_Bombas_ACS_PB.Horario_estado | 192.168.4.53:4660 | 5:0X:353 | Read+Write | Always
MSA_UM_Bombas_ACS_PB.Manual_horario | 192.168.4.53:4660 | 5:0X:354 | Read+Write | Always
MSA_UM_Bombas_ACS_PB.Marcha_paro | 192.168.4.53:4660 | 5:0X:355 | Read+Write | Always
MSA_UM_Bombas_ACS_PB.Reset_horas | 192.168.4.53:4660 | 5:0X:356 | Read+Write | Always
MSA_UM_Bombas_ACS_PB_1.Alarma_variador | 192.168.4.53:4660 | 5:0X:206 | Read+Write | Always
MSA_UM_Bombas_ACS_PB_1.Estado | 192.168.4.53:4660 | 5:0X:217 | Read+Write | Always
MSA_UM_Bombas_ACS_PB_1.Fallo | 192.168.4.53:4660 | 5:0X:357 | Read+Write | Always
MSA_UM_Bombas_ACS_PB_1.Horas_funcionam | 192.168.4.53:4660 | 5:3X:628 | Read+Write | Always
MSA_UM_Bombas_ACS_PB_1.Orden | 192.168.4.53:4660 | 5:0X:277 | Read+Write | Always
MSA_UM_Bombas_ACS_PB_2.Alarma_variador | 192.168.4.53:4660 | 5:0X:207 | Read+Write | Always
MSA_UM_Bombas_ACS_PB_2.Estado | 192.168.4.53:4660 | 5:0X:218 | Read+Write | Always
MSA_UM_Bombas_ACS_PB_2.Fallo | 192.168.4.53:4660 | 5:0X:358 | Read+Write | Always
MSA_UM_Bombas_ACS_PB_2.Horas_funcionam | 192.168.4.53:4660 | 5:3X:584 | Read+Write | Always
MSA_UM_Bombas_ACS_PB_2.Orden | 192.168.4.53:4660 | 5:0X:278 | Read+Write | Always
MSA_UM_Bombas_calor_Fallo | 192.168.4.53:4660 | 4:0X:333 | Read+Write | Always
MSA_UM_Bombas_calor_Orden | 192.168.4.53:4660 | 4:0X:275 | Read+Write | Always
MSA_UM_Bombas_Condens_Fallo | 192.168.4.53:4660 | 4:0X:329 | Read+Write | Always
MSA_UM_Bombas_Condens_Orden | 192.168.4.53:4660 | 4:0X:269 | Read+Write | Always
MSA_UM_Bombas_frio_Fallo | 192.168.4.53:4660 | 4:0X:331 | Read+Write | Always
MSA_UM_Bombas_frio_Orden | 192.168.4.53:4660 | 4:0X:273 | Read+Write | Always
MSA_UM_Bombas_UTAS.Horario_A | 192.168.4.53:4660 | 5:3X:981T80 | Read+Write | Always
MSA_UM_Bombas_UTAS.Horario_estado | 192.168.4.53:4660 | 5:0X:313 | Read+Write | Always
MSA_UM_Bombas_UTAS.Manual_horario | 192.168.4.53:4660 | 5:0X:314 | Read+Write | Always
MSA_UM_Bombas_UTAS.Marcha_paro | 192.168.4.53:4660 | 5:0X:315 | Read+Write | Always
MSA_UM_Bombas_UTAS.Reset_horas | 192.168.4.53:4660 | 5:0X:316 | Read+Write | Always
MSA_UM_Bombas_UTAS_AC_1.Alarma_variador | 192.168.4.53:4660 | 5:0X:225 | Read+Write | Always
MSA_UM_Bombas_UTAS_AC_1.Estado | 192.168.4.53:4660 | 5:0X:221 | Read+Write | Always
MSA_UM_Bombas_UTAS_AC_1.Fallo | 192.168.4.53:4660 | 5:0X:317 | Read+Write | Always
MSA_UM_Bombas_UTAS_AC_1.Horas_funcionam | 192.168.4.53:4660 | 5:3X:980 | Read+Write | Always
MSA_UM_Bombas_UTAS_AC_1.Orden | 192.168.4.53:4660 | 5:0X:281 | Read+Write | Always
MSA_UM_Bombas_UTAS_AC_2.Alarma_variador | 192.168.4.53:4660 | 5:0X:226 | Read+Write | Always
MSA_UM_Bombas_UTAS_AC_2.Estado | 192.168.4.53:4660 | 5:0X:222 | Read+Write | Always
MSA_UM_Bombas_UTAS_AC_2.Fallo | 192.168.4.53:4660 | 5:0X:318 | Read+Write | Always
MSA_UM_Bombas_UTAS_AC_2.Horas_funcionam | 192.168.4.53:4660 | 5:3X:936 | Read+Write | Always
MSA_UM_Bombas_UTAS_AC_2.Orden | 192.168.4.53:4660 | 5:0X:282 | Read+Write | Always
MSA_UM_Bombas_UTAS_AF_1.Alarma_variador | 192.168.4.53:4660 | 5:0X:227 | Read+Write | Always
MSA_UM_Bombas_UTAS_AF_1.Estado | 192.168.4.53:4660 | 5:0X:202 | Read+Write | Always
MSA_UM_Bombas_UTAS_AF_1.Fallo | 192.168.4.53:4660 | 5:0X:319 | Read+Write | Always
MSA_UM_Bombas_UTAS_AF_1.Horas_funcionam | 192.168.4.53:4660 | 5:3X:892 | Read+Write | Always
MSA_UM_Bombas_UTAS_AF_1.Orden | 192.168.4.53:4660 | 5:0X:273 | Read+Write | Always
MSA_UM_Bombas_UTAS_AF_2.Alarma_variador | 192.168.4.53:4660 | 5:0X:228 | Read+Write | Always
MSA_UM_Bombas_UTAS_AF_2.Estado | 192.168.4.53:4660 | 5:0X:203 | Read+Write | Always
MSA_UM_Bombas_UTAS_AF_2.Fallo | 192.168.4.53:4660 | 5:0X:320 | Read+Write | Always
MSA_UM_Bombas_UTAS_AF_2.Horas_funcionam | 192.168.4.53:4660 | 5:3X:848 | Read+Write | Always
MSA_UM_Bombas_UTAS_AF_2.Orden | 192.168.4.53:4660 | 5:0X:274 | Read+Write | Always
MSA_UM_Circuito_calor_Interruptor_flujo | 192.168.4.53:4660 | 5:0X:232 | Read+Write | Always
MSA_UM_Circuito_calor_Presostato_maxima | 192.168.4.53:4660 | 5:0X:238 | Read+Write | Always
MSA_UM_Circuito_calor_Presostato_minima | 192.168.4.53:4660 | 5:0X:239 | Read+Write | Always
MSA_UM_Circuito_Condens_Interruptor_flujo | 192.168.4.53:4660 | 5:0X:208 | Read+Write | Always
MSA_UM_Circuito_Condens_Presostato_maxima | 192.168.4.53:4660 | 5:0X:234 | Read+Write | Always
MSA_UM_Circuito_Condens_Presostato_minima | 192.168.4.53:4660 | 5:0X:235 | Read+Write | Always
MSA_UM_Circuito_frio_Interruptor_flujo | 192.168.4.53:4660 | 5:0X:230 | Read+Write | Always
MSA_UM_Circuito_frio_Presostato_maxima | 192.168.4.53:4660 | 5:0X:236 | Read+Write | Always
MSA_UM_Circuito_frio_Presostato_minima | 192.168.4.53:4660 | 5:0X:237 | Read+Write | Always
MSA_UM_Cl_ESD.Estado_maquina | 192.168.4.53:4660 | 1:0X:236 | Read+Write | Always
MSA_UM_Cl_ESD.Estado_recuperador | 192.168.4.53:4660 | 1:0X:252 | Read+Write | Always
MSA_UM_Cl_ESD.Estado_vent_imp | 192.168.4.53:4660 | 1:0X:231 | Read+Write | Always
MSA_UM_Cl_ESD.Estado_vent_ret | 192.168.4.53:4660 | 1:0X:232 | Read+Write | Always
MSA_UM_Cl_ESD.Fallo_maquina | 192.168.4.53:4660 | 1:0X:344 | Read+Write | Always
MSA_UM_Cl_ESD.Fallo_recuperador | 192.168.4.53:4660 | 1:0X:343 | Read+Write | Always
MSA_UM_Cl_ESD.Fallo_vent_imp | 192.168.4.53:4660 | 1:0X:341 | Read+Write | Always
MSA_UM_Cl_ESD.Fallo_vent_ret | 192.168.4.53:4660 | 1:0X:342 | Read+Write | Always
MSA_UM_Cl_ESD.Filtro_imp | 192.168.4.53:4660 | 1:0X:207 | Read+Write | Always
MSA_UM_Cl_ESD.Filtro_recuperador | 192.168.4.53:4660 | 1:0X:244 | Read+Write | Always
MSA_UM_Cl_ESD.Filtro_ret | 192.168.4.53:4660 | 1:0X:208 | Read+Write | Always
MSA_UM_Cl_ESD.Horario_A | 192.168.4.53:4660 | 1:3X:849T80 | Read+Write | Always
MSA_UM_Cl_ESD.Horario_estado | 192.168.4.53:4660 | 1:0X:337 | Read+Write | Always
MSA_UM_Cl_ESD.Horas_funcionam | 192.168.4.53:4660 | 1:3X:892 | Read+Write | Always
MSA_UM_Cl_ESD.Manual_horario | 192.168.4.53:4660 | 1:0X:338 | Read+Write | Always
MSA_UM_Cl_ESD.Marcha_paro | 192.168.4.53:4660 | 1:0X:339 | Read+Write | Always
MSA_UM_Cl_ESD.Orden_humectador | 192.168.4.53:4660 | 1:0X:286 | Read+Write | Always
MSA_UM_Cl_ESD.Orden_maquina | 192.168.4.53:4660 | 1:0X:278 | Read+Write | Always
MSA_UM_Cl_ESD.Orden_recuperador | 192.168.4.53:4660 | 1:0X:282 | Read+Write | Always
MSA_UM_Cl_ESD.Orden_vent_imp | 192.168.4.53:4660 | 1:0X:273 | Read+Write | Always
MSA_UM_Cl_ESD.Orden_vent_ret | 192.168.4.53:4660 | 1:0X:274 | Read+Write | Always
MSA_UM_Cl_ESD.Presostato_vent_imp | 192.168.4.53:4660 | 1:0X:223 | Read+Write | Always
MSA_UM_Cl_ESD.Presostato_vent_ret | 192.168.4.53:4660 | 1:0X:224 | Read+Write | Always
MSA_UM_Cl_ESD.Reset_horas | 192.168.4.53:4660 | 1:0X:340 | Read+Write | Always
MSA_UM_Cl_ESE.Estado_maquina | 192.168.4.53:4660 | 1:0X:233 | Read+Write | Always
MSA_UM_Cl_ESE.Estado_recuperador | 192.168.4.53:4660 | 1:0X:249 | Read+Write | Always
MSA_UM_Cl_ESE.Estado_vent_imp | 192.168.4.53:4660 | 1:0X:225 | Read+Write | Always
MSA_UM_Cl_ESE.Estado_vent_ret | 192.168.4.53:4660 | 1:0X:226 | Read+Write | Always
MSA_UM_Cl_ESE.Fallo_maquina | 192.168.4.53:4660 | 1:0X:320 | Read+Write | Always
MSA_UM_Cl_ESE.Fallo_recuperador | 192.168.4.53:4660 | 1:0X:319 | Read+Write | Always
MSA_UM_Cl_ESE.Fallo_vent_imp | 192.168.4.53:4660 | 1:0X:317 | Read+Write | Always
MSA_UM_Cl_ESE.Fallo_vent_ret | 192.168.4.53:4660 | 1:0X:318 | Read+Write | Always
MSA_UM_Cl_ESE.Filtro_imp | 192.168.4.53:4660 | 1:0X:201 | Read+Write | Always
MSA_UM_Cl_ESE.Filtro_recuperador | 192.168.4.53:4660 | 1:0X:241 | Read+Write | Always
MSA_UM_Cl_ESE.Filtro_ret | 192.168.4.53:4660 | 1:0X:202 | Read+Write | Always
MSA_UM_Cl_ESE.Horario_A | 192.168.4.53:4660 | 1:3X:981T80 | Read+Write | Always
MSA_UM_Cl_ESE.Horario_estado | 192.168.4.53:4660 | 1:0X:313 | Read+Write | Always
MSA_UM_Cl_ESE.Horas_funcionam | 192.168.4.53:4660 | 1:3X:1024 | Read+Write | Always
MSA_UM_Cl_ESE.Manual_horario | 192.168.4.53:4660 | 1:0X:314 | Read+Write | Always
MSA_UM_Cl_ESE.Marcha_paro | 192.168.4.53:4660 | 1:0X:315 | Read+Write | Always
MSA_UM_Cl_ESE.Orden_humectador | 192.168.4.53:4660 | 1:0X:283 | Read+Write | Always
MSA_UM_Cl_ESE.Orden_maquina | 192.168.4.53:4660 | 1:0X:275 | Read+Write | Always
MSA_UM_Cl_ESE.Orden_recuperador | 192.168.4.53:4660 | 1:0X:279 | Read+Write | Always
MSA_UM_Cl_ESE.Orden_vent_imp | 192.168.4.53:4660 | 1:0X:265 | Read+Write | Always
MSA_UM_Cl_ESE.Orden_vent_ret | 192.168.4.53:4660 | 1:0X:266 | Read+Write | Always
MSA_UM_Cl_ESE.Presostato_vent_imp | 192.168.4.53:4660 | 1:0X:217 | Read+Write | Always
MSA_UM_Cl_ESE.Presostato_vent_ret | 192.168.4.53:4660 | 1:0X:218 | Read+Write | Always
MSA_UM_Cl_ESE.Reset_horas | 192.168.4.53:4660 | 1:0X:316 | Read+Write | Always
MSA_UM_Cl_MFZCA.Estado_maquina | 192.168.4.53:4660 | 1:0X:235 | Read+Write | Always
MSA_UM_Cl_MFZCA.Estado_recuperador | 192.168.4.53:4660 | 1:0X:251 | Read+Write | Always
MSA_UM_Cl_MFZCA.Estado_vent_imp | 192.168.4.53:4660 | 1:0X:229 | Read+Write | Always
MSA_UM_Cl_MFZCA.Estado_vent_ret | 192.168.4.53:4660 | 1:0X:230 | Read+Write | Always
MSA_UM_Cl_MFZCA.Fallo_maquina | 192.168.4.53:4660 | 1:0X:336 | Read+Write | Always
MSA_UM_Cl_MFZCA.Fallo_recuperador | 192.168.4.53:4660 | 1:0X:335 | Read+Write | Always
MSA_UM_Cl_MFZCA.Fallo_vent_imp | 192.168.4.53:4660 | 1:0X:333 | Read+Write | Always
MSA_UM_Cl_MFZCA.Fallo_vent_ret | 192.168.4.53:4660 | 1:0X:334 | Read+Write | Always
MSA_UM_Cl_MFZCA.Filtro_imp | 192.168.4.53:4660 | 1:0X:205 | Read+Write | Always
MSA_UM_Cl_MFZCA.Filtro_recuperador | 192.168.4.53:4660 | 1:0X:243 | Read+Write | Always
MSA_UM_Cl_MFZCA.Filtro_ret | 192.168.4.53:4660 | 1:0X:206 | Read+Write | Always
MSA_UM_Cl_MFZCA.Horario_A | 192.168.4.53:4660 | 1:3X:893T80 | Read+Write | Always
MSA_UM_Cl_MFZCA.Horario_estado | 192.168.4.53:4660 | 1:0X:329 | Read+Write | Always
MSA_UM_Cl_MFZCA.Horas_funcionam | 192.168.4.53:4660 | 1:3X:936 | Read+Write | Always
MSA_UM_Cl_MFZCA.Manual_horario | 192.168.4.53:4660 | 1:0X:330 | Read+Write | Always
MSA_UM_Cl_MFZCA.Marcha_paro | 192.168.4.53:4660 | 1:0X:331 | Read+Write | Always
MSA_UM_Cl_MFZCA.Orden_humectador | 192.168.4.53:4660 | 1:0X:285 | Read+Write | Always
MSA_UM_Cl_MFZCA.Orden_maquina | 192.168.4.53:4660 | 1:0X:277 | Read+Write | Always
MSA_UM_Cl_MFZCA.Orden_recuperador | 192.168.4.53:4660 | 1:0X:281 | Read+Write | Always
MSA_UM_Cl_MFZCA.Orden_vent_imp | 192.168.4.53:4660 | 1:0X:269 | Read+Write | Always
MSA_UM_Cl_MFZCA.Orden_vent_ret | 192.168.4.53:4660 | 1:0X:270 | Read+Write | Always
MSA_UM_Cl_MFZCA.Presostato_vent_imp | 192.168.4.53:4660 | 1:0X:221 | Read+Write | Always
MSA_UM_Cl_MFZCA.Presostato_vent_ret | 192.168.4.53:4660 | 1:0X:222 | Read+Write | Always
MSA_UM_Cl_MFZCA.Reset_horas | 192.168.4.53:4660 | 1:0X:332 | Read+Write | Always
MSA_UM_Cl_MFZCE.Estado_maquina | 192.168.4.53:4660 | 1:0X:234 | Read+Write | Always
MSA_UM_Cl_MFZCE.Estado_recuperador | 192.168.4.53:4660 | 1:0X:250 | Read+Write | Always
MSA_UM_Cl_MFZCE.Estado_vent_imp | 192.168.4.53:4660 | 1:0X:227 | Read+Write | Always
MSA_UM_Cl_MFZCE.Estado_vent_ret | 192.168.4.53:4660 | 1:0X:228 | Read+Write | Always
MSA_UM_Cl_MFZCE.Fallo_maquina | 192.168.4.53:4660 | 1:0X:328 | Read+Write | Always
MSA_UM_Cl_MFZCE.Fallo_recuperador | 192.168.4.53:4660 | 1:0X:327 | Read+Write | Always
MSA_UM_Cl_MFZCE.Fallo_vent_imp | 192.168.4.53:4660 | 1:0X:325 | Read+Write | Always
MSA_UM_Cl_MFZCE.Fallo_vent_ret | 192.168.4.53:4660 | 1:0X:326 | Read+Write | Always
MSA_UM_Cl_MFZCE.Filtro_imp | 192.168.4.53:4660 | 1:0X:203 | Read+Write | Always
MSA_UM_Cl_MFZCE.Filtro_recuperador | 192.168.4.53:4660 | 1:0X:242 | Read+Write | Always
MSA_UM_Cl_MFZCE.Filtro_ret | 192.168.4.53:4660 | 1:0X:204 | Read+Write | Always
MSA_UM_Cl_MFZCE.Horario_A | 192.168.4.53:4660 | 1:3X:937T80 | Read+Write | Always
MSA_UM_Cl_MFZCE.Horario_estado | 192.168.4.53:4660 | 1:0X:321 | Read+Write | Always
MSA_UM_Cl_MFZCE.Horas_funcionam | 192.168.4.53:4660 | 1:3X:980 | Read+Write | Always
MSA_UM_Cl_MFZCE.Manual_horario | 192.168.4.53:4660 | 1:0X:322 | Read+Write | Always
MSA_UM_Cl_MFZCE.Marcha_paro | 192.168.4.53:4660 | 1:0X:323 | Read+Write | Always
MSA_UM_Cl_MFZCE.Orden_humectador | 192.168.4.53:4660 | 1:0X:284 | Read+Write | Always
MSA_UM_Cl_MFZCE.Orden_maquina | 192.168.4.53:4660 | 1:0X:276 | Read+Write | Always
MSA_UM_Cl_MFZCE.Orden_recuperador | 192.168.4.53:4660 | 1:0X:280 | Read+Write | Always
MSA_UM_Cl_MFZCE.Orden_vent_imp | 192.168.4.53:4660 | 1:0X:267 | Read+Write | Always
MSA_UM_Cl_MFZCE.Orden_vent_ret | 192.168.4.53:4660 | 1:0X:268 | Read+Write | Always
MSA_UM_Cl_MFZCE.Presostato_vent_imp | 192.168.4.53:4660 | 1:0X:219 | Read+Write | Always
MSA_UM_Cl_MFZCE.Presostato_vent_ret | 192.168.4.53:4660 | 1:0X:220 | Read+Write | Always
MSA_UM_Cl_MFZCE.Reset_horas | 192.168.4.53:4660 | 1:0X:324 | Read+Write | Always
MSA_UM_depositos_inercia_AC_Termostato_seg_1 | 192.168.4.53:4660 | 5:0X:242 | Read+Write | Always
MSA_UM_depositos_inercia_AC_Termostato_seg_2 | 192.168.4.53:4660 | 5:0X:243 | Read+Write | Always
MSA_UM_depositos_inercia_AF_Termostato_seg_1 | 192.168.4.53:4660 | 5:0X:240 | Read+Write | Always
MSA_UM_depositos_inercia_AF_Termostato_seg_2 | 192.168.4.53:4660 | 5:0X:241 | Read+Write | Always
MSA_UM_Produccion.Horario_A | 192.168.4.53:4660 | 4:3X:981T80 | Read+Write | Always
MSA_UM_Produccion.Horario_estado | 192.168.4.53:4660 | 4:0X:313 | Read+Write | Always
MSA_UM_Produccion.Manual_horario | 192.168.4.53:4660 | 4:0X:314 | Read+Write | Always
MSA_UM_Produccion.Marcha_paro | 192.168.4.53:4660 | 4:0X:315 | Read+Write | Always
MSA_UM_Produccion.Reset_horas | 192.168.4.53:4660 | 4:0X:316 | Read+Write | Always
MSA_UM_Produccion_Arrancar_maquina | 192.168.4.53:4660 | 4:0X:317 | Read+Write | Always
MSA_UM_Produccion_Estado_maquina | 192.168.4.53:4660 | 5:0X:201 | Read | Always
MSA_UM_Produccion_Orden_maquina | 192.168.4.53:4660 | 5:0X:287 | Read+Write | Always
MSA_UM_UTAS_IV_Bombas_paradas | 192.168.4.53:4660 | 5:0X:343 | Read+Write | Always
MSA_UM_UTAS_IV_Cambiando | 192.168.4.53:4660 | 5:0X:342 | Read+Write | Always
MSA_UM_UTAS_IV_Cambio_Bombas | 192.168.4.53:4660 | 5:0X:341 | Read+Write | Always
MSA_UM_UTAS_IV_Cambio_Valvulas | 192.168.4.53:4660 | 4:0X:328 | Read+Write | Always
MSA_UM_UTAS_IV_Valvulas_en_Posicion | 192.168.4.53:4660 | 4:0X:327 | Read+Write | Always
MSA_UM_valv_UTAS_AC_Imp.Estado_abierta | 192.168.4.53:4660 | 4:0X:225 | Read+Write | Always
MSA_UM_valv_UTAS_AC_Imp.Estado_cerrada | 192.168.4.53:4660 | 4:0X:229 | Read+Write | Always
MSA_UM_valv_UTAS_AC_Imp.Fallo | 192.168.4.53:4660 | 4:0X:345 | Read+Write | Always
MSA_UM_valv_UTAS_AC_Imp.Orden_abrir | 192.168.4.53:4660 | 4:0X:279 | Read+Write | Always
MSA_UM_valv_UTAS_AC_Ret.Estado_abierta | 192.168.4.53:4660 | 4:0X:226 | Read+Write | Always
MSA_UM_valv_UTAS_AC_Ret.Estado_cerrada | 192.168.4.53:4660 | 4:0X:230 | Read+Write | Always
MSA_UM_valv_UTAS_AC_Ret.Fallo | 192.168.4.53:4660 | 4:0X:346 | Read+Write | Always
MSA_UM_valv_UTAS_AC_Ret.Orden_abrir | 192.168.4.53:4660 | 4:0X:280 | Read+Write | Always
MSA_UM_valv_UTAS_AF_imp.Estado_abierta | 192.168.4.53:4660 | 4:0X:223 | Read+Write | Always
MSA_UM_valv_UTAS_AF_imp.Estado_cerrada | 192.168.4.53:4660 | 4:0X:227 | Read+Write | Always
MSA_UM_valv_UTAS_AF_imp.Fallo | 192.168.4.53:4660 | 4:0X:347 | Read+Write | Always
MSA_UM_valv_UTAS_AF_imp.Orden_abrir | 192.168.4.53:4660 | 4:0X:277 | Read+Write | Always
MSA_UM_valv_UTAS_AF_ret.Estado_abierta | 192.168.4.53:4660 | 4:0X:224 | Read+Write | Always
MSA_UM_valv_UTAS_AF_ret.Estado_cerrada | 192.168.4.53:4660 | 4:0X:228 | Read+Write | Always
MSA_UM_valv_UTAS_AF_ret.Fallo | 192.168.4.53:4660 | 4:0X:348 | Read+Write | Always
MSA_UM_valv_UTAS_AF_ret.Orden_abrir | 192.168.4.53:4660 | 4:0X:278 | Read+Write | Always
MSA_UM_VM_Condens_1.Estado_abierta | 192.168.4.53:4660 | 4:0X:201 | Read+Write | Always
MSA_UM_VM_Condens_1.Fallo | 192.168.4.53:4660 | 4:0X:322 | Read+Write | Always
MSA_UM_VM_Condens_1.Orden_abrir | 192.168.4.53:4660 | 4:0X:265 | Read+Write | Always
MSA_UM_VM_Condens_2.Estado_abierta | 192.168.4.53:4660 | 4:0X:202 | Read+Write | Always
MSA_UM_VM_Condens_2.Fallo | 192.168.4.53:4660 | 4:0X:323 | Read+Write | Always
MSA_UM_VM_Condens_2.Orden_abrir | 192.168.4.53:4660 | 4:0X:266 | Read+Write | Always
MSA_UM_VM_Condens_3.Estado_abierta | 192.168.4.53:4660 | 4:0X:203 | Read+Write | Always
MSA_UM_VM_Condens_3.Fallo | 192.168.4.53:4660 | 4:0X:324 | Read+Write | Always
MSA_UM_VM_Condens_3.Orden_abrir | 192.168.4.53:4660 | 4:0X:267 | Read+Write | Always
MSA_UM_VM_Condens_4.Estado_abierta | 192.168.4.53:4660 | 4:0X:204 | Read+Write | Always
MSA_UM_VM_Condens_4.Fallo | 192.168.4.53:4660 | 4:0X:325 | Read+Write | Always
MSA_UM_VM_Condens_4.Orden_abrir | 192.168.4.53:4660 | 4:0X:268 | Read+Write | Always
MSA_UT_Alumb_Accesos_Dcha.Estado | 192.168.4.43:4660 | 2:0X:218 | Read+Write | Always
MSA_UT_Alumb_Accesos_Dcha.Fallo | 192.168.4.43:4660 | 2:0X:381 | Read+Write | Always
MSA_UT_Alumb_Accesos_Dcha.Horario_A | 192.168.4.43:4660 | 2:3X:629T80 | Read+Write | Always
MSA_UT_Alumb_Accesos_Dcha.Horario_estado | 192.168.4.43:4660 | 2:0X:377 | Read+Write | Always
MSA_UT_Alumb_Accesos_Dcha.Manual_horario | 192.168.4.43:4660 | 2:0X:378 | Read+Write | Always
MSA_UT_Alumb_Accesos_Dcha.Marcha_paro | 192.168.4.43:4660 | 2:0X:379 | Read+Write | Always
MSA_UT_Alumb_Accesos_Dcha.Orden | 192.168.4.43:4660 | 2:0X:275 | Read+Write | Always
MSA_UT_Alumb_Accesos_Izauierda.Estado | 192.168.4.43:4660 | 2:0X:208 | Read+Write | Always
MSA_UT_Alumb_Accesos_Izauierda.Fallo | 192.168.4.43:4660 | 2:0X:373 | Read+Write | Always
MSA_UT_Alumb_Accesos_Izauierda.Horario_A | 192.168.4.43:4660 | 2:3X:673T80 | Read+Write | Always
MSA_UT_Alumb_Accesos_Izauierda.Horario_estado | 192.168.4.43:4660 | 2:0X:369 | Read+Write | Always
MSA_UT_Alumb_Accesos_Izauierda.Manual_horario | 192.168.4.43:4660 | 2:0X:370 | Read+Write | Always
MSA_UT_Alumb_Accesos_Izauierda.Marcha_paro | 192.168.4.43:4660 | 2:0X:371 | Read+Write | Always
MSA_UT_Alumb_Accesos_Izauierda.Orden | 192.168.4.43:4660 | 2:0X:274 | Read+Write | Always
MSA_UT_Alumb_Accesos_testa.Estado | 192.168.4.43:4660 | 2:0X:219 | Read+Write | Always
MSA_UT_Alumb_Accesos_testa.Fallo | 192.168.4.43:4660 | 2:0X:389 | Read+Write | Always
MSA_UT_Alumb_Accesos_testa.Horario_A | 192.168.4.43:4660 | 2:3X:585T80 | Read+Write | Always
MSA_UT_Alumb_Accesos_testa.Horario_estado | 192.168.4.43:4660 | 2:0X:385 | Read+Write | Always
MSA_UT_Alumb_Accesos_testa.Manual_horario | 192.168.4.43:4660 | 2:0X:386 | Read+Write | Always
MSA_UT_Alumb_Accesos_testa.Marcha_paro | 192.168.4.43:4660 | 2:0X:387 | Read+Write | Always
MSA_UT_Alumb_Accesos_testa.Orden | 192.168.4.43:4660 | 2:0X:276 | Read+Write | Always
MSA_UT_Alumb_Encants.Estado | 192.168.4.43:4660 | 2:0X:201 | Read+Write | Always
MSA_UT_Alumb_Encants.Fallo | 192.168.4.43:4660 | 2:0X:317 | Read+Write | Always
MSA_UT_Alumb_Encants.Horario_A | 192.168.4.43:4660 | 2:3X:981T80 | Read+Write | Always
MSA_UT_Alumb_Encants.Horario_estado | 192.168.4.43:4660 | 2:0X:313 | Read+Write | Always
MSA_UT_Alumb_Encants.Manual_horario | 192.168.4.43:4660 | 2:0X:314 | Read+Write | Always
MSA_UT_Alumb_Encants.Marcha_paro | 192.168.4.43:4660 | 2:0X:315 | Read+Write | Always
MSA_UT_Alumb_Encants.Orden | 192.168.4.43:4660 | 2:0X:265 | Read+Write | Always
MSA_UT_Alumb_Encants_Dcha.Estado | 192.168.4.43:4660 | 2:0X:206 | Read+Write | Always
MSA_UT_Alumb_Encants_Dcha.Fallo | 192.168.4.43:4660 | 2:0X:357 | Read+Write | Always
MSA_UT_Alumb_Encants_Dcha.Horario_A | 192.168.4.43:4660 | 2:3X:761T80 | Read+Write | Always
MSA_UT_Alumb_Encants_Dcha.Horario_estado | 192.168.4.43:4660 | 2:0X:353 | Read+Write | Always
MSA_UT_Alumb_Encants_Dcha.Manual_horario | 192.168.4.43:4660 | 2:0X:354 | Read+Write | Always
MSA_UT_Alumb_Encants_Dcha.Marcha_paro | 192.168.4.43:4660 | 2:0X:355 | Read+Write | Always
MSA_UT_Alumb_Encants_Dcha.Orden | 192.168.4.43:4660 | 2:0X:270 | Read+Write | Always
MSA_UT_Alumb_Encants_Dcha_Vigi.Estado | 192.168.4.43:4660 | 2:0X:207 | Read+Write | Always
MSA_UT_Alumb_Encants_Dcha_Vigi.Fallo | 192.168.4.43:4660 | 2:0X:365 | Read+Write | Always
MSA_UT_Alumb_Encants_Dcha_Vigi.Horario_A | 192.168.4.43:4660 | 2:3X:717T80 | Read+Write | Always
MSA_UT_Alumb_Encants_Dcha_Vigi.Horario_estado | 192.168.4.43:4660 | 2:0X:361 | Read+Write | Always
MSA_UT_Alumb_Encants_Dcha_Vigi.Manual_horario | 192.168.4.43:4660 | 2:0X:362 | Read+Write | Always
MSA_UT_Alumb_Encants_Dcha_Vigi.Marcha_paro | 192.168.4.43:4660 | 2:0X:363 | Read+Write | Always
MSA_UT_Alumb_Encants_Dcha_Vigi.Orden | 192.168.4.43:4660 | 2:0X:273 | Read+Write | Always
MSA_UT_Alumb_Encants_Vigi.Estado | 192.168.4.43:4660 | 2:0X:202 | Read+Write | Always
MSA_UT_Alumb_Encants_Vigi.Fallo | 192.168.4.43:4660 | 2:0X:325 | Read+Write | Always
MSA_UT_Alumb_Encants_Vigi.Horario_A | 192.168.4.43:4660 | 2:3X:937T80 | Read+Write | Always
MSA_UT_Alumb_Encants_Vigi.Horario_estado | 192.168.4.43:4660 | 2:0X:321 | Read+Write | Always
MSA_UT_Alumb_Encants_Vigi.Manual_horario | 192.168.4.43:4660 | 2:0X:322 | Read+Write | Always
MSA_UT_Alumb_Encants_Vigi.Marcha_paro | 192.168.4.43:4660 | 2:0X:323 | Read+Write | Always
MSA_UT_Alumb_Encants_Vigi.Orden | 192.168.4.43:4660 | 2:0X:266 | Read+Write | Always
MSA_UT_Alumb_Escalera_1.Estado | 192.168.4.43:4660 | 2:0X:219 | Read+Write | Always
MSA_UT_Alumb_Escalera_1.Fallo | 192.168.4.43:4660 | 2:0X:397 | Read+Write | Always
MSA_UT_Alumb_Escalera_1.Horario_A | 192.168.4.43:4660 | 2:3X:541T80 | Read+Write | Always
MSA_UT_Alumb_Escalera_1.Horario_estado | 192.168.4.43:4660 | 2:0X:393 | Read+Write | Always
MSA_UT_Alumb_Escalera_1.Manual_horario | 192.168.4.43:4660 | 2:0X:394 | Read+Write | Always
MSA_UT_Alumb_Escalera_1.Marcha_paro | 192.168.4.43:4660 | 2:0X:395 | Read+Write | Always
MSA_UT_Alumb_Escalera_1.Orden | 192.168.4.43:4660 | 2:0X:277 | Read+Write | Always
MSA_UT_Alumb_Escalera_2.Estado | 192.168.4.43:4660 | 2:0X:220 | Read+Write | Always
MSA_UT_Alumb_Escalera_2.Fallo | 192.168.4.43:4660 | 2:0X:405 | Read+Write | Always
MSA_UT_Alumb_Escalera_2.Horario_A | 192.168.4.43:4660 | 2:3X:497T80 | Read+Write | Always
MSA_UT_Alumb_Escalera_2.Horario_estado | 192.168.4.43:4660 | 2:0X:401 | Read+Write | Always
MSA_UT_Alumb_Escalera_2.Manual_horario | 192.168.4.43:4660 | 2:0X:402 | Read+Write | Always
MSA_UT_Alumb_Escalera_2.Marcha_paro | 192.168.4.43:4660 | 2:0X:403 | Read+Write | Always
MSA_UT_Alumb_Escalera_2.Orden | 192.168.4.43:4660 | 2:0X:278 | Read+Write | Always
MSA_UT_Alumb_Escalera_3.Estado | 192.168.4.43:4660 | 2:0X:221 | Read+Write | Always
MSA_UT_Alumb_Escalera_3.Fallo | 192.168.4.43:4660 | 2:0X:413 | Read+Write | Always
MSA_UT_Alumb_Escalera_3.Horario_A | 192.168.4.43:4660 | 2:3X:453T80 | Read+Write | Always
MSA_UT_Alumb_Escalera_3.Horario_estado | 192.168.4.43:4660 | 2:0X:409 | Read+Write | Always
MSA_UT_Alumb_Escalera_3.Manual_horario | 192.168.4.43:4660 | 2:0X:410 | Read+Write | Always
MSA_UT_Alumb_Escalera_3.Marcha_paro | 192.168.4.43:4660 | 2:0X:411 | Read+Write | Always
MSA_UT_Alumb_Escalera_3.Orden | 192.168.4.43:4660 | 2:0X:279 | Read+Write | Always
MSA_UT_Alumb_Escalera_4.Estado | 192.168.4.43:4660 | 2:0X:222 | Read+Write | Always
MSA_UT_Alumb_Escalera_4.Fallo | 192.168.4.43:4660 | 2:0X:421 | Read+Write | Always
MSA_UT_Alumb_Escalera_4.Horario_A | 192.168.4.43:4660 | 2:3X:409T80 | Read+Write | Always
MSA_UT_Alumb_Escalera_4.Horario_estado | 192.168.4.43:4660 | 2:0X:417 | Read+Write | Always
MSA_UT_Alumb_Escalera_4.Manual_horario | 192.168.4.43:4660 | 2:0X:418 | Read+Write | Always
MSA_UT_Alumb_Escalera_4.Marcha_paro | 192.168.4.43:4660 | 2:0X:419 | Read+Write | Always
MSA_UT_Alumb_Escalera_4.Orden | 192.168.4.43:4660 | 2:0X:280 | Read+Write | Always
MSA_UT_Alumb_Fachada_3.Estado | 192.168.4.43:4660 | 3:0X:203 | Read+Write | Always
MSA_UT_Alumb_Fachada_3.Fallo | 192.168.4.43:4660 | 3:0X:333 | Read+Write | Always
MSA_UT_Alumb_Fachada_3.Horario_A | 192.168.4.43:4660 | 3:3X:893T80 | Read+Write | Always
MSA_UT_Alumb_Fachada_3.Horario_estado | 192.168.4.43:4660 | 3:0X:329 | Read+Write | Always
MSA_UT_Alumb_Fachada_3.Manual_horario | 192.168.4.43:4660 | 3:0X:330 | Read+Write | Always
MSA_UT_Alumb_Fachada_3.Marcha_paro | 192.168.4.43:4660 | 3:0X:331 | Read+Write | Always
MSA_UT_Alumb_Fachada_3.Orden | 192.168.4.43:4660 | 3:0X:267 | Read+Write | Always
MSA_UT_Alumb_Fachada_4.Estado | 192.168.4.43:4660 | 3:0X:204 | Read+Write | Always
MSA_UT_Alumb_Fachada_4.Fallo | 192.168.4.43:4660 | 3:0X:341 | Read+Write | Always
MSA_UT_Alumb_Fachada_4.Horario_A | 192.168.4.43:4660 | 3:3X:849T80 | Read+Write | Always
MSA_UT_Alumb_Fachada_4.Horario_estado | 192.168.4.43:4660 | 3:0X:337 | Read+Write | Always
MSA_UT_Alumb_Fachada_4.Manual_horario | 192.168.4.43:4660 | 3:0X:338 | Read+Write | Always
MSA_UT_Alumb_Fachada_4.Marcha_paro | 192.168.4.43:4660 | 3:0X:339 | Read+Write | Always
MSA_UT_Alumb_Fachada_4.Orden | 192.168.4.43:4660 | 3:0X:268 | Read+Write | Always
MSA_UT_Alumb_Fresco_1.Estado | 192.168.4.43:4660 | 2:0X:203 | Read+Write | Always
MSA_UT_Alumb_Fresco_1.Fallo | 192.168.4.43:4660 | 2:0X:333 | Read+Write | Always
MSA_UT_Alumb_Fresco_1.Horario_A | 192.168.4.43:4660 | 2:3X:893T80 | Read+Write | Always
MSA_UT_Alumb_Fresco_1.Horario_estado | 192.168.4.43:4660 | 2:0X:329 | Read+Write | Always
MSA_UT_Alumb_Fresco_1.Manual_horario | 192.168.4.43:4660 | 2:0X:330 | Read+Write | Always
MSA_UT_Alumb_Fresco_1.Marcha_paro | 192.168.4.43:4660 | 2:0X:331 | Read+Write | Always
MSA_UT_Alumb_Fresco_1.Orden | 192.168.4.43:4660 | 2:0X:267 | Read+Write | Always
MSA_UT_Alumb_Fresco_2.Estado | 192.168.4.43:4660 | 2:0X:204 | Read+Write | Always
MSA_UT_Alumb_Fresco_2.Fallo | 192.168.4.43:4660 | 2:0X:341 | Read+Write | Always
MSA_UT_Alumb_Fresco_2.Horario_A | 192.168.4.43:4660 | 2:3X:849T80 | Read+Write | Always
MSA_UT_Alumb_Fresco_2.Horario_estado | 192.168.4.43:4660 | 2:0X:337 | Read+Write | Always
MSA_UT_Alumb_Fresco_2.Manual_horario | 192.168.4.43:4660 | 2:0X:338 | Read+Write | Always
MSA_UT_Alumb_Fresco_2.Marcha_paro | 192.168.4.43:4660 | 2:0X:339 | Read+Write | Always
MSA_UT_Alumb_Fresco_2.Orden | 192.168.4.43:4660 | 2:0X:268 | Read+Write | Always
MSA_UT_Alumb_Fresco_Vigi.Estado | 192.168.4.43:4660 | 2:0X:205 | Read+Write | Always
MSA_UT_Alumb_Fresco_Vigi.Fallo | 192.168.4.43:4660 | 2:0X:349 | Read+Write | Always
MSA_UT_Alumb_Fresco_Vigi.Horario_A | 192.168.4.43:4660 | 2:3X:805T80 | Read+Write | Always
MSA_UT_Alumb_Fresco_Vigi.Horario_estado | 192.168.4.43:4660 | 2:0X:345 | Read+Write | Always
MSA_UT_Alumb_Fresco_Vigi.Manual_horario | 192.168.4.43:4660 | 2:0X:346 | Read+Write | Always
MSA_UT_Alumb_Fresco_Vigi.Marcha_paro | 192.168.4.43:4660 | 2:0X:347 | Read+Write | Always
MSA_UT_Alumb_Fresco_Vigi.Orden | 192.168.4.43:4660 | 2:0X:269 | Read+Write | Always
MSA_UT_Alumb_LED_1.Estado | 192.168.4.43:4660 | 8:0X:201 | Read+Write | Always
MSA_UT_Alumb_LED_1.Fallo | 192.168.4.43:4660 | 8:0X:317 | Read+Write | Always
MSA_UT_Alumb_LED_1.Horario_A | 192.168.4.43:4660 | 8:3X:981T80 | Read+Write | Always
MSA_UT_Alumb_LED_1.Horario_estado | 192.168.4.43:4660 | 8:0X:313 | Read+Write | Always
MSA_UT_Alumb_LED_1.Manual_horario | 192.168.4.43:4660 | 8:0X:314 | Read+Write | Always
MSA_UT_Alumb_LED_1.Marcha_paro | 192.168.4.43:4660 | 8:0X:315 | Read+Write | Always
MSA_UT_Alumb_LED_1.Orden | 192.168.4.43:4660 | 8:0X:265 | Read+Write | Always
MSA_UT_Alumb_LED_2.Estado | 192.168.4.43:4660 | 8:0X:202 | Read+Write | Always
MSA_UT_Alumb_LED_2.Fallo | 192.168.4.43:4660 | 8:0X:325 | Read+Write | Always
MSA_UT_Alumb_LED_2.Horario_A | 192.168.4.43:4660 | 8:3X:937T80 | Read+Write | Always
MSA_UT_Alumb_LED_2.Horario_estado | 192.168.4.43:4660 | 8:0X:321 | Read+Write | Always
MSA_UT_Alumb_LED_2.Manual_horario | 192.168.4.43:4660 | 8:0X:322 | Read+Write | Always
MSA_UT_Alumb_LED_2.Marcha_paro | 192.168.4.43:4660 | 8:0X:323 | Read+Write | Always
MSA_UT_Alumb_LED_2.Orden | 192.168.4.43:4660 | 8:0X:266 | Read+Write | Always
MSA_UT_Alumb_LED_3.Estado | 192.168.4.43:4660 | 8:0X:203 | Read+Write | Always
MSA_UT_Alumb_LED_3.Fallo | 192.168.4.43:4660 | 8:0X:333 | Read+Write | Always
MSA_UT_Alumb_LED_3.Horario_A | 192.168.4.43:4660 | 8:3X:893T80 | Read+Write | Always
MSA_UT_Alumb_LED_3.Horario_estado | 192.168.4.43:4660 | 8:0X:329 | Read+Write | Always
MSA_UT_Alumb_LED_3.Manual_horario | 192.168.4.43:4660 | 8:0X:330 | Read+Write | Always
MSA_UT_Alumb_LED_3.Marcha_paro | 192.168.4.43:4660 | 8:0X:331 | Read+Write | Always
MSA_UT_Alumb_LED_3.Orden | 192.168.4.43:4660 | 8:0X:267 | Read+Write | Always
MSA_UT_Alumb_Linea_02.Estado | 192.168.4.43:4660 | 11:0X:201 | Read+Write | Always
MSA_UT_Alumb_Linea_02.Fallo | 192.168.4.43:4660 | 11:0X:317 | Read+Write | Always
MSA_UT_Alumb_Linea_02.Horario_A | 192.168.4.43:4660 | 11:3X:981T80 | Read+Write | Always
MSA_UT_Alumb_Linea_02.Horario_estado | 192.168.4.43:4660 | 11:0X:313 | Read+Write | Always
MSA_UT_Alumb_Linea_02.Manual_horario | 192.168.4.43:4660 | 11:0X:314 | Read+Write | Always
MSA_UT_Alumb_Linea_02.Marcha_paro | 192.168.4.43:4660 | 11:0X:315 | Read+Write | Always
MSA_UT_Alumb_Linea_02.Orden | 192.168.4.43:4660 | 11:0X:265 | Read+Write | Always
MSA_UT_Alumb_Linea_o1.Estado | 192.168.4.43:4660 | 10:0X:206 | Read+Write | Always
MSA_UT_Alumb_Linea_o1.Fallo | 192.168.4.43:4660 | 10:0X:357 | Read+Write | Always
MSA_UT_Alumb_Linea_o1.Horario_A | 192.168.4.43:4660 | 10:3X:761T80 | Read+Write | Always
MSA_UT_Alumb_Linea_o1.Horario_estado | 192.168.4.43:4660 | 10:0X:353 | Read+Write | Always
MSA_UT_Alumb_Linea_o1.Manual_horario | 192.168.4.43:4660 | 10:0X:354 | Read+Write | Always
MSA_UT_Alumb_Linea_o1.Marcha_paro | 192.168.4.43:4660 | 10:0X:355 | Read+Write | Always
MSA_UT_Alumb_Linea_o1.Orden | 192.168.4.43:4660 | 10:0X:270 | Read+Write | Always
MSA_UT_Alumb_Marquesina_1.Estado | 192.168.4.43:4660 | 3:0X:201 | Read+Write | Always
MSA_UT_Alumb_Marquesina_1.Fallo | 192.168.4.43:4660 | 3:0X:317 | Read+Write | Always
MSA_UT_Alumb_Marquesina_1.Horario_A | 192.168.4.43:4660 | 3:3X:981T80 | Read+Write | Always
MSA_UT_Alumb_Marquesina_1.Horario_estado | 192.168.4.43:4660 | 3:0X:313 | Read+Write | Always
MSA_UT_Alumb_Marquesina_1.Manual_horario | 192.168.4.43:4660 | 3:0X:314 | Read+Write | Always
MSA_UT_Alumb_Marquesina_1.Marcha_paro | 192.168.4.43:4660 | 3:0X:315 | Read+Write | Always
MSA_UT_Alumb_Marquesina_1.Orden | 192.168.4.43:4660 | 3:0X:265 | Read+Write | Always
MSA_UT_Alumb_Marquesina_2.Estado | 192.168.4.43:4660 | 3:0X:202 | Read+Write | Always
MSA_UT_Alumb_Marquesina_2.Fallo | 192.168.4.43:4660 | 3:0X:325 | Read+Write | Always
MSA_UT_Alumb_Marquesina_2.Horario_A | 192.168.4.43:4660 | 3:3X:937T80 | Read+Write | Always
MSA_UT_Alumb_Marquesina_2.Horario_estado | 192.168.4.43:4660 | 3:0X:321 | Read+Write | Always
MSA_UT_Alumb_Marquesina_2.Manual_horario | 192.168.4.43:4660 | 3:0X:322 | Read+Write | Always
MSA_UT_Alumb_Marquesina_2.Marcha_paro | 192.168.4.43:4660 | 3:0X:323 | Read+Write | Always
MSA_UT_Alumb_Marquesina_2.Orden | 192.168.4.43:4660 | 3:0X:266 | Read+Write | Always
MSA_UT_Alumb_Patio_testa.Estado | 192.168.4.43:4660 | 7:0X:201 | Read+Write | Always
MSA_UT_Alumb_Patio_testa.Fallo | 192.168.4.43:4660 | 7:0X:317 | Read+Write | Always
MSA_UT_Alumb_Patio_testa.Horario_A | 192.168.4.43:4660 | 7:3X:981T80 | Read+Write | Always
MSA_UT_Alumb_Patio_testa.Horario_estado | 192.168.4.43:4660 | 7:0X:313 | Read+Write | Always
MSA_UT_Alumb_Patio_testa.Manual_horario | 192.168.4.43:4660 | 7:0X:314 | Read+Write | Always
MSA_UT_Alumb_Patio_testa.Marcha_paro | 192.168.4.43:4660 | 7:0X:315 | Read+Write | Always
MSA_UT_Alumb_Patio_testa.Orden | 192.168.4.43:4660 | 7:0X:265 | Read+Write | Always
MSA_UT_Alumb_Perimetro_01.Estado | 192.168.4.43:4660 | 8:0X:204 | Read+Write | Always
MSA_UT_Alumb_Perimetro_01.Fallo | 192.168.4.43:4660 | 8:0X:341 | Read+Write | Always
MSA_UT_Alumb_Perimetro_01.Horario_A | 192.168.4.43:4660 | 8:3X:849T80 | Read+Write | Always
MSA_UT_Alumb_Perimetro_01.Horario_estado | 192.168.4.43:4660 | 8:0X:337 | Read+Write | Always
MSA_UT_Alumb_Perimetro_01.Manual_horario | 192.168.4.43:4660 | 8:0X:338 | Read+Write | Always
MSA_UT_Alumb_Perimetro_01.Marcha_paro | 192.168.4.43:4660 | 8:0X:339 | Read+Write | Always
MSA_UT_Alumb_Perimetro_01.Orden | 192.168.4.43:4660 | 8:0X:268 | Read+Write | Always
MSA_UT_Alumb_Perimetro_02.Estado | 192.168.4.43:4660 | 8:0X:205 | Read+Write | Always
MSA_UT_Alumb_Perimetro_02.Fallo | 192.168.4.43:4660 | 8:0X:349 | Read+Write | Always
MSA_UT_Alumb_Perimetro_02.Horario_A | 192.168.4.43:4660 | 8:3X:805T80 | Read+Write | Always
MSA_UT_Alumb_Perimetro_02.Horario_estado | 192.168.4.43:4660 | 8:0X:345 | Read+Write | Always
MSA_UT_Alumb_Perimetro_02.Manual_horario | 192.168.4.43:4660 | 8:0X:346 | Read+Write | Always
MSA_UT_Alumb_Perimetro_02.Marcha_paro | 192.168.4.43:4660 | 8:0X:347 | Read+Write | Always
MSA_UT_Alumb_Perimetro_02.Orden | 192.168.4.43:4660 | 8:0X:269 | Read+Write | Always
MSA_UT_Alumb_Perimetro_03.Estado | 192.168.4.43:4660 | 8:0X:206 | Read+Write | Always
MSA_UT_Alumb_Perimetro_03.Fallo | 192.168.4.43:4660 | 8:0X:357 | Read+Write | Always
MSA_UT_Alumb_Perimetro_03.Horario_A | 192.168.4.43:4660 | 8:3X:761T80 | Read+Write | Always
MSA_UT_Alumb_Perimetro_03.Horario_estado | 192.168.4.43:4660 | 8:0X:353 | Read+Write | Always
MSA_UT_Alumb_Perimetro_03.Manual_horario | 192.168.4.43:4660 | 8:0X:354 | Read+Write | Always
MSA_UT_Alumb_Perimetro_03.Marcha_paro | 192.168.4.43:4660 | 8:0X:355 | Read+Write | Always
MSA_UT_Alumb_Perimetro_03.Orden | 192.168.4.43:4660 | 8:0X:270 | Read+Write | Always
MSA_UT_Alumb_Plaza_B.Estado | 192.168.4.43:4660 | 3:0X:205 | Read+Write | Always
MSA_UT_Alumb_Plaza_B.Fallo | 192.168.4.43:4660 | 3:0X:349 | Read+Write | Always
MSA_UT_Alumb_Plaza_B.Horario_A | 192.168.4.43:4660 | 3:3X:805T80 | Read+Write | Always
MSA_UT_Alumb_Plaza_B.Horario_estado | 192.168.4.43:4660 | 3:0X:345 | Read+Write | Always
MSA_UT_Alumb_Plaza_B.Manual_horario | 192.168.4.43:4660 | 3:0X:346 | Read+Write | Always
MSA_UT_Alumb_Plaza_B.Marcha_paro | 192.168.4.43:4660 | 3:0X:347 | Read+Write | Always
MSA_UT_Alumb_Plaza_B.Orden | 192.168.4.43:4660 | 3:0X:269 | Read+Write | Always
MSA_UT_Alumb_Plaza_T.Estado | 192.168.4.43:4660 | 3:0X:206 | Read+Write | Always
MSA_UT_Alumb_Plaza_T.Fallo | 192.168.4.43:4660 | 3:0X:357 | Read+Write | Always
MSA_UT_Alumb_Plaza_T.Horario_A | 192.168.4.43:4660 | 3:3X:453T80 | Read+Write | Always
MSA_UT_Alumb_Plaza_T.Horario_estado | 192.168.4.43:4660 | 3:0X:409 | Read+Write | Always
MSA_UT_Alumb_Plaza_T.Manual_horario | 192.168.4.43:4660 | 3:0X:410 | Read+Write | Always
MSA_UT_Alumb_Plaza_T.Marcha_paro | 192.168.4.43:4660 | 3:0X:411 | Read+Write | Always
MSA_UT_Alumb_Plaza_T.Orden | 192.168.4.43:4660 | 3:0X:270 | Read+Write | Always
MSA_UT_Alumb_Salas_Tecnicas.Estado | 192.168.4.43:4660 | 11:0X:202 | Read+Write | Always
MSA_UT_Alumb_Salas_Tecnicas.Fallo | 192.168.4.43:4660 | 11:0X:325 | Read+Write | Always
MSA_UT_Alumb_Salas_Tecnicas.Horario_A | 192.168.4.43:4660 | 11:3X:937T80 | Read+Write | Always
MSA_UT_Alumb_Salas_Tecnicas.Horario_estado | 192.168.4.43:4660 | 11:0X:321 | Read+Write | Always
MSA_UT_Alumb_Salas_Tecnicas.Manual_horario | 192.168.4.43:4660 | 11:0X:322 | Read+Write | Always
MSA_UT_Alumb_Salas_Tecnicas.Marcha_paro | 192.168.4.43:4660 | 11:0X:323 | Read+Write | Always
MSA_UT_Alumb_Salas_Tecnicas.Orden | 192.168.4.43:4660 | 11:0X:266 | Read+Write | Always
MSA_UT_Alumb_Salas_tecnicas_Qm42.Estado | 192.168.4.43:4660 | 6:0X:233 | Read+Write | Always
MSA_UT_Alumb_Salas_tecnicas_Qm42.Fallo | 192.168.4.43:4660 | 6:0X:405 | Read+Write | Always
MSA_UT_Alumb_Salas_tecnicas_Qm42.Horario_A | 192.168.4.43:4660 | 6:3X:497T80 | Read+Write | Always
MSA_UT_Alumb_Salas_tecnicas_Qm42.Horario_estado | 192.168.4.43:4660 | 6:0X:401 | Read+Write | Always
MSA_UT_Alumb_Salas_tecnicas_Qm42.Manual_horario | 192.168.4.43:4660 | 6:0X:402 | Read+Write | Always
MSA_UT_Alumb_Salas_tecnicas_Qm42.Marcha_paro | 192.168.4.43:4660 | 6:0X:403 | Read+Write | Always
MSA_UT_Alumb_Salas_tecnicas_Qm42.Orden | 192.168.4.43:4660 | 6:0X:286 | Read+Write | Always
MSA_UT_Alumb_Vigi.Estado | 192.168.4.43:4660 | 10:0X:205 | Read+Write | Always
MSA_UT_Alumb_Vigi.Fallo | 192.168.4.43:4660 | 10:0X:349 | Read+Write | Always
MSA_UT_Alumb_Vigi.Horario_A | 192.168.4.43:4660 | 10:3X:805T80 | Read+Write | Always
MSA_UT_Alumb_Vigi.Horario_estado | 192.168.4.43:4660 | 10:0X:345 | Read+Write | Always
MSA_UT_Alumb_Vigi.Manual_horario | 192.168.4.43:4660 | 10:0X:346 | Read+Write | Always
MSA_UT_Alumb_Vigi.Marcha_paro | 192.168.4.43:4660 | 10:0X:347 | Read+Write | Always
MSA_UT_Alumb_Vigi.Orden | 192.168.4.43:4660 | 10:0X:269 | Read+Write | Always
MSA_UT_Alumb_Vigi_1.Estado | 192.168.4.43:4660 | 7:0X:202 | Read+Write | Always
MSA_UT_Alumb_Vigi_1.Fallo | 192.168.4.43:4660 | 7:0X:325 | Read+Write | Always
MSA_UT_Alumb_Vigi_1.Horario_A | 192.168.4.43:4660 | 7:3X:937T80 | Read+Write | Always
MSA_UT_Alumb_Vigi_1.Horario_estado | 192.168.4.43:4660 | 7:0X:321 | Read+Write | Always
MSA_UT_Alumb_Vigi_1.Manual_horario | 192.168.4.43:4660 | 7:0X:322 | Read+Write | Always
MSA_UT_Alumb_Vigi_1.Marcha_paro | 192.168.4.43:4660 | 7:0X:323 | Read+Write | Always
MSA_UT_Alumb_Vigi_1.Orden | 192.168.4.43:4660 | 7:0X:266 | Read+Write | Always
MSA_UT_Alumb_Vigi_2.Estado | 192.168.4.43:4660 | 7:0X:203 | Read+Write | Always
MSA_UT_Alumb_Vigi_2.Fallo | 192.168.4.43:4660 | 7:0X:333 | Read+Write | Always
MSA_UT_Alumb_Vigi_2.Horario_A | 192.168.4.43:4660 | 7:3X:893T80 | Read+Write | Always
MSA_UT_Alumb_Vigi_2.Horario_estado | 192.168.4.43:4660 | 7:0X:329 | Read+Write | Always
MSA_UT_Alumb_Vigi_2.Manual_horario | 192.168.4.43:4660 | 7:0X:330 | Read+Write | Always
MSA_UT_Alumb_Vigi_2.Marcha_paro | 192.168.4.43:4660 | 7:0X:331 | Read+Write | Always
MSA_UT_Alumb_Vigi_2.Orden | 192.168.4.43:4660 | 7:0X:267 | Read+Write | Always
MSA_UT_Alumb_Vigi_3.Estado | 192.168.4.43:4660 | 7:0X:204 | Read+Write | Always
MSA_UT_Alumb_Vigi_3.Fallo | 192.168.4.43:4660 | 7:0X:341 | Read+Write | Always
MSA_UT_Alumb_Vigi_3.Horario_A | 192.168.4.43:4660 | 7:3X:849T80 | Read+Write | Always
MSA_UT_Alumb_Vigi_3.Horario_estado | 192.168.4.43:4660 | 7:0X:337 | Read+Write | Always
MSA_UT_Alumb_Vigi_3.Manual_horario | 192.168.4.43:4660 | 7:0X:338 | Read+Write | Always
MSA_UT_Alumb_Vigi_3.Marcha_paro | 192.168.4.43:4660 | 7:0X:339 | Read+Write | Always
MSA_UT_Alumb_Vigi_3.Orden | 192.168.4.43:4660 | 7:0X:268 | Read+Write | Always
MSA_UT_Bomba_AC_A_Geoterm.Horario_A | 192.168.4.43:4660 | 6:3X:893T80 | Read+Write | Always
MSA_UT_Bomba_AC_A_Geoterm.Horario_estado | 192.168.4.43:4660 | 6:0X:313 | Read+Write | Always
MSA_UT_Bomba_AC_A_Geoterm.Manual_horario | 192.168.4.43:4660 | 6:0X:314 | Read+Write | Always
MSA_UT_Bomba_AC_A_Geoterm.Marcha_paro | 192.168.4.43:4660 | 6:0X:315 | Read+Write | Always
MSA_UT_Bomba_AC_A_Geoterm.Reset_horas | 192.168.4.43:4660 | 6:0X:316 | Read+Write | Always
MSA_UT_Bomba_AC_A_Geoterm_1.Alarma_variador | 192.168.4.43:4660 | 6:0X:247 | Read+Write | Always
MSA_UT_Bomba_AC_A_Geoterm_1.Estado | 192.168.4.43:4660 | 6:0X:223 | Read+Write | Always
MSA_UT_Bomba_AC_A_Geoterm_1.Fallo | 192.168.4.43:4660 | 6:0X:317 | Read+Write | Always
MSA_UT_Bomba_AC_A_Geoterm_1.Horas_funcionam | 192.168.4.43:4660 | 6:3X:848 | Read+Write | Always
MSA_UT_Bomba_AC_A_Geoterm_1.Orden | 192.168.4.43:4660 | 6:0X:283 | Read+Write | Always
MSA_UT_Bomba_AC_A_Geoterm_2.Alarma_variador | 192.168.4.43:4660 | 6:0X:248 | Read+Write | Always
MSA_UT_Bomba_AC_A_Geoterm_2.Estado | 192.168.4.43:4660 | 6:0X:224 | Read+Write | Always
MSA_UT_Bomba_AC_A_Geoterm_2.Fallo | 192.168.4.43:4660 | 6:0X:318 | Read+Write | Always
MSA_UT_Bomba_AC_A_Geoterm_2.Horas_funcionam | 192.168.4.43:4660 | 6:3X:804 | Read+Write | Always
MSA_UT_Bomba_AC_A_Geoterm_2.Orden | 192.168.4.43:4660 | 6:0X:284 | Read+Write | Always
MSA_UT_Bomba_AF_A_Geoterm.Horario_A | 192.168.4.43:4660 | 6:3X:761T80 | Read+Write | Always
MSA_UT_Bomba_AF_A_Geoterm.Horario_estado | 192.168.4.43:4660 | 6:0X:353 | Read+Write | Always
MSA_UT_Bomba_AF_A_Geoterm.Manual_horario | 192.168.4.43:4660 | 6:0X:354 | Read+Write | Always
MSA_UT_Bomba_AF_A_Geoterm.Marcha_paro | 192.168.4.43:4660 | 6:0X:355 | Read+Write | Always
MSA_UT_Bomba_AF_A_Geoterm.Reset_horas | 192.168.4.43:4660 | 6:0X:356 | Read+Write | Always
MSA_UT_Bomba_AF_A_Geoterm_1.Alarma_variador | 192.168.4.43:4660 | 6:0X:245 | Read+Write | Always
MSA_UT_Bomba_AF_A_Geoterm_1.Estado | 192.168.4.43:4660 | 6:0X:204 | Read+Write | Always
MSA_UT_Bomba_AF_A_Geoterm_1.Fallo | 192.168.4.43:4660 | 6:0X:333 | Read+Write | Always
MSA_UT_Bomba_AF_A_Geoterm_1.Horas_funcionam | 192.168.4.43:4660 | 6:3X:584 | Read+Write | Always
MSA_UT_Bomba_AF_A_Geoterm_1.Orden | 192.168.4.43:4660 | 6:0X:275 | Read+Write | Always
MSA_UT_Bomba_AF_A_Geoterm_2.Alarma_variador | 192.168.4.43:4660 | 6:0X:246 | Read+Write | Always
MSA_UT_Bomba_AF_A_Geoterm_2.Estado | 192.168.4.43:4660 | 6:0X:205 | Read+Write | Always
MSA_UT_Bomba_AF_A_Geoterm_2.Fallo | 192.168.4.43:4660 | 6:0X:334 | Read+Write | Always
MSA_UT_Bomba_AF_A_Geoterm_2.Horas_funcionam | 192.168.4.43:4660 | 6:3X:540 | Read+Write | Always
MSA_UT_Bomba_AF_A_Geoterm_2.Orden | 192.168.4.43:4660 | 6:0X:276 | Read+Write | Always
MSA_UT_Bomba_calor_1.Estado | 192.168.4.43:4660 | 5:0X:221 | Read+Write | Always
MSA_UT_Bomba_calor_1.Horas_funcionam | 192.168.4.43:4660 | 5:3X:848 | Read+Write | Always
MSA_UT_Bomba_calor_2.Estado | 192.168.4.43:4660 | 5:0X:222 | Read+Write | Always
MSA_UT_Bomba_calor_2.Horas_funcionam | 192.168.4.43:4660 | 5:3X:804 | Read+Write | Always
MSA_UT_Bomba_Condens_1.Estado | 192.168.4.43:4660 | 5:0X:217 | Read+Write | Always
MSA_UT_Bomba_Condens_1.Horas_funcionam | 192.168.4.43:4660 | 5:3X:1024 | Read+Write | Always
MSA_UT_Bomba_Condens_2.Estado | 192.168.4.43:4660 | 5:0X:218 | Read+Write | Always
MSA_UT_Bomba_Condens_2.Horas_funcionam | 192.168.4.43:4660 | 5:3X:980 | Read+Write | Always
MSA_UT_Bomba_frio_1.Estado | 192.168.4.43:4660 | 5:0X:219 | Read+Write | Always
MSA_UT_Bomba_frio_1.Horas_funcionam | 192.168.4.43:4660 | 5:3X:936 | Read+Write | Always
MSA_UT_Bomba_frio_2.Estado | 192.168.4.43:4660 | 5:0X:220 | Read+Write | Always
MSA_UT_Bomba_frio_2.Horas_funcionam | 192.168.4.43:4660 | 5:3X:892 | Read+Write | Always
MSA_UT_Bombas_ACS_P_Inf.Horario_A | 192.168.4.43:4660 | 6:3X:849T80 | Read+Write | Always
MSA_UT_Bombas_ACS_P_Inf.Horario_estado | 192.168.4.43:4660 | 6:0X:337 | Read+Write | Always
MSA_UT_Bombas_ACS_P_Inf.Manual_horario | 192.168.4.43:4660 | 6:0X:338 | Read+Write | Always
MSA_UT_Bombas_ACS_P_Inf.Marcha_paro | 192.168.4.43:4660 | 6:0X:339 | Read+Write | Always
MSA_UT_Bombas_ACS_P_Inf.Reset_horas | 192.168.4.43:4660 | 6:0X:340 | Read+Write | Always
MSA_UT_Bombas_ACS_P_Inf_1.Alarma_variador | 192.168.4.43:4660 | 6:0X:229 | Read+Write | Always
MSA_UT_Bombas_ACS_P_Inf_1.Estado | 192.168.4.43:4660 | 6:0X:219 | Read+Write | Always
MSA_UT_Bombas_ACS_P_Inf_1.Fallo | 192.168.4.43:4660 | 6:0X:341 | Read+Write | Always
MSA_UT_Bombas_ACS_P_Inf_1.Horas_funcionam | 192.168.4.43:4660 | 6:3X:760 | Read+Write | Always
MSA_UT_Bombas_ACS_P_Inf_1.Orden | 192.168.4.43:4660 | 6:0X:279 | Read+Write | Always
MSA_UT_Bombas_ACS_P_Inf_2.Alarma_variador | 192.168.4.43:4660 | 6:0X:231 | Read+Write | Always
MSA_UT_Bombas_ACS_P_Inf_2.Estado | 192.168.4.43:4660 | 6:0X:220 | Read+Write | Always
MSA_UT_Bombas_ACS_P_Inf_2.Fallo | 192.168.4.43:4660 | 6:0X:342 | Read+Write | Always
MSA_UT_Bombas_ACS_P_Inf_2.Horas_funcionam | 192.168.4.43:4660 | 6:3X:716 | Read+Write | Always
MSA_UT_Bombas_ACS_P_Inf_2.Orden | 192.168.4.43:4660 | 6:0X:280 | Read+Write | Always
MSA_UT_Bombas_ACS_PB.Horario_A | 192.168.4.43:4660 | 6:3X:805T80 | Read+Write | Always
MSA_UT_Bombas_ACS_PB.Horario_estado | 192.168.4.43:4660 | 6:0X:345 | Read+Write | Always
MSA_UT_Bombas_ACS_PB.Manual_horario | 192.168.4.43:4660 | 6:0X:346 | Read+Write | Always
MSA_UT_Bombas_ACS_PB.Marcha_paro | 192.168.4.43:4660 | 6:0X:347 | Read+Write | Always
MSA_UT_Bombas_ACS_PB.Reset_horas | 192.168.4.43:4660 | 6:0X:348 | Read+Write | Always
MSA_UT_Bombas_ACS_PB_1.Alarma_variador | 192.168.4.43:4660 | 6:0X:206 | Read+Write | Always
MSA_UT_Bombas_ACS_PB_1.Estado | 192.168.4.43:4660 | 6:0X:217 | Read+Write | Always
MSA_UT_Bombas_ACS_PB_1.Fallo | 192.168.4.43:4660 | 6:0X:349 | Read+Write | Always
MSA_UT_Bombas_ACS_PB_1.Horas_funcionam | 192.168.4.43:4660 | 6:3X:672 | Read+Write | Always
MSA_UT_Bombas_ACS_PB_1.Orden | 192.168.4.43:4660 | 6:0X:277 | Read+Write | Always
MSA_UT_Bombas_ACS_PB_2.Alarma_variador | 192.168.4.43:4660 | 6:0X:207 | Read+Write | Always
MSA_UT_Bombas_ACS_PB_2.Estado | 192.168.4.43:4660 | 6:0X:218 | Read+Write | Always
MSA_UT_Bombas_ACS_PB_2.Fallo | 192.168.4.43:4660 | 6:0X:350 | Read+Write | Always
MSA_UT_Bombas_ACS_PB_2.Horas_funcionam | 192.168.4.43:4660 | 6:3X:628 | Read+Write | Always
MSA_UT_Bombas_ACS_PB_2.Orden | 192.168.4.43:4660 | 6:0X:278 | Read+Write | Always
MSA_UT_Bombas_calor_Fallo | 192.168.4.43:4660 | 5:0X:338 | Read+Write | Always
MSA_UT_Bombas_calor_Interruptor_flujo | 192.168.4.43:4660 | 6:0X:232 | Read+Write | Always
MSA_UT_Bombas_calor_Orden | 192.168.4.43:4660 | 5:0X:275 | Read+Write | Always
MSA_UT_Bombas_Condens_Fallo | 192.168.4.43:4660 | 5:0X:325 | Read+Write | Always
MSA_UT_Bombas_Condens_Orden | 192.168.4.43:4660 | 5:0X:269 | Read+Write | Always
MSA_UT_Bombas_frio_Fallo | 192.168.4.43:4660 | 5:0X:327 | Read+Write | Always
MSA_UT_Bombas_frio_Interruptor_flujo | 192.168.4.43:4660 | 6:0X:230 | Read+Write | Always
MSA_UT_Bombas_frio_Orden | 192.168.4.43:4660 | 5:0X:273 | Read+Write | Always
MSA_UT_Bombas_UTAS.Horario_A | 192.168.4.43:4660 | 6:3X:937T80 | Read+Write | Always
MSA_UT_Bombas_UTAS.Horario_estado | 192.168.4.43:4660 | 6:0X:321 | Read+Write | Always
MSA_UT_Bombas_UTAS.Manual_horario | 192.168.4.43:4660 | 6:0X:322 | Read+Write | Always
MSA_UT_Bombas_UTAS.Marcha_paro | 192.168.4.43:4660 | 6:0X:323 | Read+Write | Always
MSA_UT_Bombas_UTAS.Reset_horas | 192.168.4.43:4660 | 6:0X:324 | Read+Write | Always
MSA_UT_Bombas_UTAS_AC_1.Alarma_variador | 192.168.4.43:4660 | 6:0X:225 | Read+Write | Always
MSA_UT_Bombas_UTAS_AC_1.Estado | 192.168.4.43:4660 | 6:0X:221 | Read+Write | Always
MSA_UT_Bombas_UTAS_AC_1.Fallo | 192.168.4.43:4660 | 6:0X:326 | Read+Write | Always
MSA_UT_Bombas_UTAS_AC_1.Horas_funcionam | 192.168.4.43:4660 | 6:3X:1024 | Read+Write | Always
MSA_UT_Bombas_UTAS_AC_1.Orden | 192.168.4.43:4660 | 6:0X:281 | Read+Write | Always
MSA_UT_Bombas_UTAS_AC_2.Alarma_variador | 192.168.4.43:4660 | 6:0X:226 | Read+Write | Always
MSA_UT_Bombas_UTAS_AC_2.Estado | 192.168.4.43:4660 | 6:0X:222 | Read+Write | Always
MSA_UT_Bombas_UTAS_AC_2.Fallo | 192.168.4.43:4660 | 6:0X:327 | Read+Write | Always
MSA_UT_Bombas_UTAS_AC_2.Horas_funcionam | 192.168.4.43:4660 | 6:3X:980 | Read+Write | Always
MSA_UT_Bombas_UTAS_AC_2.Orden | 192.168.4.43:4660 | 6:0X:282 | Read+Write | Always
MSA_UT_Bombas_UTAS_AF_1.Alarma_variador | 192.168.4.43:4660 | 6:0X:227 | Read+Write | Always
MSA_UT_Bombas_UTAS_AF_1.Estado | 192.168.4.43:4660 | 6:0X:202 | Read+Write | Always
MSA_UT_Bombas_UTAS_AF_1.Fallo | 192.168.4.43:4660 | 6:0X:330 | Read+Write | Always
MSA_UT_Bombas_UTAS_AF_1.Horas_funcionam | 192.168.4.43:4660 | 6:3X:936 | Read+Write | Always
MSA_UT_Bombas_UTAS_AF_1.Orden | 192.168.4.43:4660 | 6:0X:273 | Read+Write | Always
MSA_UT_Bombas_UTAS_AF_2.Alarma_variador | 192.168.4.43:4660 | 6:0X:228 | Read+Write | Always
MSA_UT_Bombas_UTAS_AF_2.Estado | 192.168.4.43:4660 | 6:0X:203 | Read+Write | Always
MSA_UT_Bombas_UTAS_AF_2.Fallo | 192.168.4.43:4660 | 6:0X:331 | Read+Write | Always
MSA_UT_Bombas_UTAS_AF_2.Horas_funcionam | 192.168.4.43:4660 | 6:3X:892 | Read+Write | Always
MSA_UT_Bombas_UTAS_AF_2.Orden | 192.168.4.43:4660 | 6:0X:274 | Read+Write | Always
MSA_UT_Circuito_calor_Presostato_maxima | 192.168.4.43:4660 | 6:0X:238 | Read+Write | Always
MSA_UT_Circuito_calor_Presostato_minima | 192.168.4.43:4660 | 6:0X:239 | Read+Write | Always
MSA_UT_Circuito_Condens_Interruptor_flujo | 192.168.4.43:4660 | 6:0X:208 | Read+Write | Always
MSA_UT_Circuito_Condens_Presostato_maxima | 192.168.4.43:4660 | 6:0X:234 | Read+Write | Always
MSA_UT_Circuito_Condens_Presostato_minima | 192.168.4.43:4660 | 6:0X:235 | Read+Write | Always
MSA_UT_Circuito_frio_Presostato_maxima | 192.168.4.43:4660 | 6:0X:236 | Read+Write | Always
MSA_UT_Circuito_frio_Presostato_minima | 192.168.4.43:4660 | 6:0X:237 | Read+Write | Always
MSA_UT_Cl_ESD.Estado_maquina | 192.168.4.43:4660 | 1:0X:236 | Read+Write | Always
MSA_UT_Cl_ESD.Estado_recuperador | 192.168.4.43:4660 | 1:0X:252 | Read+Write | Always
MSA_UT_Cl_ESD.Estado_vent_imp | 192.168.4.43:4660 | 1:0X:231 | Read+Write | Always
MSA_UT_Cl_ESD.Estado_vent_ret | 192.168.4.43:4660 | 1:0X:232 | Read+Write | Always
MSA_UT_Cl_ESD.Fallo_maquina | 192.168.4.43:4660 | 1:0X:344 | Read+Write | Always
MSA_UT_Cl_ESD.Fallo_recuperador | 192.168.4.43:4660 | 1:0X:343 | Read+Write | Always
MSA_UT_Cl_ESD.Fallo_vent_imp | 192.168.4.43:4660 | 1:0X:341 | Read+Write | Always
MSA_UT_Cl_ESD.Fallo_vent_ret | 192.168.4.43:4660 | 1:0X:342 | Read+Write | Always
MSA_UT_Cl_ESD.Filtro_imp | 192.168.4.43:4660 | 1:0X:207 | Read+Write | Always
MSA_UT_Cl_ESD.Filtro_recuperador | 192.168.4.43:4660 | 1:0X:244 | Read+Write | Always
MSA_UT_Cl_ESD.Filtro_ret | 192.168.4.43:4660 | 1:0X:208 | Read+Write | Always
MSA_UT_Cl_ESD.Horario_A | 192.168.4.43:4660 | 1:3X:849T80 | Read+Write | Always
MSA_UT_Cl_ESD.Horario_estado | 192.168.4.43:4660 | 1:0X:337 | Read+Write | Always
MSA_UT_Cl_ESD.Horas_funcionam | 192.168.4.43:4660 | 1:3X:892 | Read+Write | Always
MSA_UT_Cl_ESD.Manual_horario | 192.168.4.43:4660 | 1:0X:338 | Read+Write | Always
MSA_UT_Cl_ESD.Marcha_paro | 192.168.4.43:4660 | 1:0X:339 | Read+Write | Always
MSA_UT_Cl_ESD.Orden_humectador | 192.168.4.43:4660 | 1:0X:286 | Read+Write | Always
MSA_UT_Cl_ESD.Orden_maquina | 192.168.4.43:4660 | 1:0X:278 | Read+Write | Always
MSA_UT_Cl_ESD.Orden_recuperador | 192.168.4.43:4660 | 1:0X:282 | Read+Write | Always
MSA_UT_Cl_ESD.Orden_vent_imp | 192.168.4.43:4660 | 1:0X:273 | Read+Write | Always
MSA_UT_Cl_ESD.Orden_vent_ret | 192.168.4.43:4660 | 1:0X:274 | Read+Write | Always
MSA_UT_Cl_ESD.Presostato_vent_imp | 192.168.4.43:4660 | 1:0X:223 | Read+Write | Always
MSA_UT_Cl_ESD.Presostato_vent_ret | 192.168.4.43:4660 | 1:0X:224 | Read+Write | Always
MSA_UT_Cl_ESD.Reset_horas | 192.168.4.43:4660 | 1:0X:340 | Read+Write | Always
MSA_UT_Cl_ESE.Estado_maquina | 192.168.4.43:4660 | 1:0X:233 | Read+Write | Always
MSA_UT_Cl_ESE.Estado_recuperador | 192.168.4.43:4660 | 1:0X:249 | Read+Write | Always
MSA_UT_Cl_ESE.Estado_vent_imp | 192.168.4.43:4660 | 1:0X:225 | Read+Write | Always
MSA_UT_Cl_ESE.Estado_vent_ret | 192.168.4.43:4660 | 1:0X:226 | Read+Write | Always
MSA_UT_Cl_ESE.Fallo_maquina | 192.168.4.43:4660 | 1:0X:320 | Read+Write | Always
MSA_UT_Cl_ESE.Fallo_recuperador | 192.168.4.43:4660 | 1:0X:319 | Read+Write | Always
MSA_UT_Cl_ESE.Fallo_vent_imp | 192.168.4.43:4660 | 1:0X:317 | Read+Write | Always
MSA_UT_Cl_ESE.Fallo_vent_ret | 192.168.4.43:4660 | 1:0X:318 | Read+Write | Always
MSA_UT_Cl_ESE.Filtro_imp | 192.168.4.43:4660 | 1:0X:201 | Read+Write | Always
MSA_UT_Cl_ESE.Filtro_recuperador | 192.168.4.43:4660 | 1:0X:241 | Read+Write | Always
MSA_UT_Cl_ESE.Filtro_ret | 192.168.4.43:4660 | 1:0X:202 | Read+Write | Always
MSA_UT_Cl_ESE.Horario_A | 192.168.4.43:4660 | 1:3X:981T80 | Read+Write | Always
MSA_UT_Cl_ESE.Horario_estado | 192.168.4.43:4660 | 1:0X:313 | Read+Write | Always
MSA_UT_Cl_ESE.Horas_funcionam | 192.168.4.43:4660 | 1:3X:1024 | Read+Write | Always
MSA_UT_Cl_ESE.Manual_horario | 192.168.4.43:4660 | 1:0X:314 | Read+Write | Always
MSA_UT_Cl_ESE.Marcha_paro | 192.168.4.43:4660 | 1:0X:315 | Read+Write | Always
MSA_UT_Cl_ESE.Orden_humectador | 192.168.4.43:4660 | 1:0X:283 | Read+Write | Always
MSA_UT_Cl_ESE.Orden_maquina | 192.168.4.43:4660 | 1:0X:275 | Read+Write | Always
MSA_UT_Cl_ESE.Orden_recuperador | 192.168.4.43:4660 | 1:0X:279 | Read+Write | Always
MSA_UT_Cl_ESE.Orden_vent_imp | 192.168.4.43:4660 | 1:0X:265 | Read+Write | Always
MSA_UT_Cl_ESE.Orden_vent_ret | 192.168.4.43:4660 | 1:0X:266 | Read+Write | Always
MSA_UT_Cl_ESE.Presostato_vent_imp | 192.168.4.43:4660 | 1:0X:217 | Read+Write | Always
MSA_UT_Cl_ESE.Presostato_vent_ret | 192.168.4.43:4660 | 1:0X:218 | Read+Write | Always
MSA_UT_Cl_ESE.Reset_horas | 192.168.4.43:4660 | 1:0X:316 | Read+Write | Always
MSA_UT_Cl_MFZCA.Estado_maquina | 192.168.4.43:4660 | 1:0X:235 | Read+Write | Always
MSA_UT_Cl_MFZCA.Estado_recuperador | 192.168.4.43:4660 | 1:0X:251 | Read+Write | Always
MSA_UT_Cl_MFZCA.Estado_vent_imp | 192.168.4.43:4660 | 1:0X:229 | Read+Write | Always
MSA_UT_Cl_MFZCA.Estado_vent_ret | 192.168.4.43:4660 | 1:0X:230 | Read+Write | Always
MSA_UT_Cl_MFZCA.Fallo_maquina | 192.168.4.43:4660 | 1:0X:336 | Read+Write | Always
MSA_UT_Cl_MFZCA.Fallo_recuperador | 192.168.4.43:4660 | 1:0X:335 | Read+Write | Always
MSA_UT_Cl_MFZCA.Fallo_vent_imp | 192.168.4.43:4660 | 1:0X:333 | Read+Write | Always
MSA_UT_Cl_MFZCA.Fallo_vent_ret | 192.168.4.43:4660 | 1:0X:334 | Read+Write | Always
MSA_UT_Cl_MFZCA.Filtro_imp | 192.168.4.43:4660 | 1:0X:205 | Read+Write | Always
MSA_UT_Cl_MFZCA.Filtro_recuperador | 192.168.4.43:4660 | 1:0X:243 | Read+Write | Always
MSA_UT_Cl_MFZCA.Filtro_ret | 192.168.4.43:4660 | 1:0X:206 | Read+Write | Always
MSA_UT_Cl_MFZCA.Horario_A | 192.168.4.43:4660 | 1:3X:893T80 | Read+Write | Always
MSA_UT_Cl_MFZCA.Horario_estado | 192.168.4.43:4660 | 1:0X:329 | Read+Write | Always
MSA_UT_Cl_MFZCA.Horas_funcionam | 192.168.4.43:4660 | 1:3X:936 | Read+Write | Always
MSA_UT_Cl_MFZCA.Manual_horario | 192.168.4.43:4660 | 1:0X:330 | Read+Write | Always
MSA_UT_Cl_MFZCA.Marcha_paro | 192.168.4.43:4660 | 1:0X:331 | Read+Write | Always
MSA_UT_Cl_MFZCA.Orden_humectador | 192.168.4.43:4660 | 1:0X:285 | Read+Write | Always
MSA_UT_Cl_MFZCA.Orden_maquina | 192.168.4.43:4660 | 1:0X:277 | Read+Write | Always
MSA_UT_Cl_MFZCA.Orden_recuperador | 192.168.4.43:4660 | 1:0X:281 | Read+Write | Always
MSA_UT_Cl_MFZCA.Orden_vent_imp | 192.168.4.43:4660 | 1:0X:269 | Read+Write | Always
MSA_UT_Cl_MFZCA.Orden_vent_ret | 192.168.4.43:4660 | 1:0X:270 | Read+Write | Always
MSA_UT_Cl_MFZCA.Presostato_vent_imp | 192.168.4.43:4660 | 1:0X:221 | Read+Write | Always
MSA_UT_Cl_MFZCA.Presostato_vent_ret | 192.168.4.43:4660 | 1:0X:222 | Read+Write | Always
MSA_UT_Cl_MFZCA.Reset_horas | 192.168.4.43:4660 | 1:0X:332 | Read+Write | Always
MSA_UT_Cl_MFZCE.Estado_maquina | 192.168.4.43:4660 | 1:0X:234 | Read+Write | Always
MSA_UT_Cl_MFZCE.Estado_recuperador | 192.168.4.43:4660 | 1:0X:250 | Read+Write | Always
MSA_UT_Cl_MFZCE.Estado_vent_imp | 192.168.4.43:4660 | 1:0X:227 | Read+Write | Always
MSA_UT_Cl_MFZCE.Estado_vent_ret | 192.168.4.43:4660 | 1:0X:228 | Read+Write | Always
MSA_UT_Cl_MFZCE.Fallo_maquina | 192.168.4.43:4660 | 1:0X:328 | Read+Write | Always
MSA_UT_Cl_MFZCE.Fallo_recuperador | 192.168.4.43:4660 | 1:0X:327 | Read+Write | Always
MSA_UT_Cl_MFZCE.Fallo_vent_imp | 192.168.4.43:4660 | 1:0X:325 | Read+Write | Always
MSA_UT_Cl_MFZCE.Fallo_vent_ret | 192.168.4.43:4660 | 1:0X:326 | Read+Write | Always
MSA_UT_Cl_MFZCE.Filtro_imp | 192.168.4.43:4660 | 1:0X:203 | Read+Write | Always
MSA_UT_Cl_MFZCE.Filtro_recuperador | 192.168.4.43:4660 | 1:0X:242 | Read+Write | Always
MSA_UT_Cl_MFZCE.Filtro_ret | 192.168.4.43:4660 | 1:0X:204 | Read+Write | Always
MSA_UT_Cl_MFZCE.Horario_A | 192.168.4.43:4660 | 1:3X:937T80 | Read+Write | Always
MSA_UT_Cl_MFZCE.Horario_estado | 192.168.4.43:4660 | 1:0X:321 | Read+Write | Always
MSA_UT_Cl_MFZCE.Horas_funcionam | 192.168.4.43:4660 | 1:3X:980 | Read+Write | Always
MSA_UT_Cl_MFZCE.Manual_horario | 192.168.4.43:4660 | 1:0X:322 | Read+Write | Always
MSA_UT_Cl_MFZCE.Marcha_paro | 192.168.4.43:4660 | 1:0X:323 | Read+Write | Always
MSA_UT_Cl_MFZCE.Orden_humectador | 192.168.4.43:4660 | 1:0X:284 | Read+Write | Always
MSA_UT_Cl_MFZCE.Orden_maquina | 192.168.4.43:4660 | 1:0X:276 | Read+Write | Always
MSA_UT_Cl_MFZCE.Orden_recuperador | 192.168.4.43:4660 | 1:0X:280 | Read+Write | Always
MSA_UT_Cl_MFZCE.Orden_vent_imp | 192.168.4.43:4660 | 1:0X:267 | Read+Write | Always
MSA_UT_Cl_MFZCE.Orden_vent_ret | 192.168.4.43:4660 | 1:0X:268 | Read+Write | Always
MSA_UT_Cl_MFZCE.Presostato_vent_imp | 192.168.4.43:4660 | 1:0X:219 | Read+Write | Always
MSA_UT_Cl_MFZCE.Presostato_vent_ret | 192.168.4.43:4660 | 1:0X:220 | Read+Write | Always
MSA_UT_Cl_MFZCE.Reset_horas | 192.168.4.43:4660 | 1:0X:324 | Read+Write | Always
MSA_UT_depositos_inercia_AC_Termostato_seg_1 | 192.168.4.43:4660 | 6:0X:242 | Read+Write | Always
MSA_UT_depositos_inercia_AC_Termostato_seg_2 | 192.168.4.43:4660 | 6:0X:243 | Read+Write | Always
MSA_UT_depositos_inercia_AF_Termostato_seg_1 | 192.168.4.43:4660 | 6:0X:240 | Read+Write | Always
MSA_UT_depositos_inercia_AF_Termostato_seg_2 | 192.168.4.43:4660 | 6:0X:241 | Read+Write | Always
MSA_UT_Produccion.Horario_A | 192.168.4.43:4660 | 5:3X:981T80 | Read+Write | Always
MSA_UT_Produccion.Horario_estado | 192.168.4.43:4660 | 5:0X:313 | Read+Write | Always
MSA_UT_Produccion.Manual_horario | 192.168.4.43:4660 | 5:0X:314 | Read+Write | Always
MSA_UT_Produccion.Marcha_paro | 192.168.4.43:4660 | 5:0X:315 | Read+Write | Always
MSA_UT_Produccion.Reset_horas | 192.168.4.43:4660 | 5:0X:316 | Read+Write | Always
MSA_UT_Produccion_Arrancar_maquina | 192.168.4.43:4660 | 5:0X:317 | Read+Write | Always
MSA_UT_Produccion_Estado_maquina | 192.168.4.43:4660 | 6:0X:201 | Read | Always
MSA_UT_Produccion_Orden_maquina | 192.168.4.43:4660 | 6:0X:287 | Read+Write | Always
MSA_UT_UTAS_IV_Bombas_paradas | 192.168.4.43:4660 | 6:0X:329 | Read+Write | Always
MSA_UT_UTAS_IV_Cambiando | 192.168.4.43:4660 | 6:0X:328 | Read+Write | Always
MSA_UT_UTAS_IV_Cambio_Bombas | 192.168.4.43:4660 | 6:0X:325 | Read+Write | Always
MSA_UT_UTAS_IV_Cambio_Valvulas | 192.168.4.43:4660 | 5:0X:334 | Read+Write | Always
MSA_UT_UTAS_IV_Valvulas_en_Posicion | 192.168.4.43:4660 | 5:0X:335 | Read+Write | Always
MSA_UT_valv_UTAS_AC_Imp.Estado_abierta | 192.168.4.43:4660 | 5:0X:229 | Read+Write | Always
MSA_UT_valv_UTAS_AC_Imp.Estado_cerrada | 192.168.4.43:4660 | 5:0X:230 | Read+Write | Always
MSA_UT_valv_UTAS_AC_Imp.Fallo | 192.168.4.43:4660 | 5:0X:330 | Read+Write | Always
MSA_UT_valv_UTAS_AC_Imp.Orden_abrir | 192.168.4.43:4660 | 5:0X:279 | Read+Write | Always
MSA_UT_valv_UTAS_AC_Ret.Estado_abierta | 192.168.4.43:4660 | 5:0X:227 | Read+Write | Always
MSA_UT_valv_UTAS_AC_Ret.Estado_cerrada | 192.168.4.43:4660 | 5:0X:228 | Read+Write | Always
MSA_UT_valv_UTAS_AC_Ret.Fallo | 192.168.4.43:4660 | 5:0X:331 | Read+Write | Always
MSA_UT_valv_UTAS_AC_Ret.Orden_abrir | 192.168.4.43:4660 | 5:0X:280 | Read+Write | Always
MSA_UT_valv_UTAS_AF_Imp.Estado_abierta | 192.168.4.43:4660 | 5:0X:225 | Read+Write | Always
MSA_UT_valv_UTAS_AF_Imp.Estado_cerrada | 192.168.4.43:4660 | 5:0X:226 | Read+Write | Always
MSA_UT_valv_UTAS_AF_Imp.Fallo | 192.168.4.43:4660 | 5:0X:332 | Read+Write | Always
MSA_UT_valv_UTAS_AF_Imp.Orden_abrir | 192.168.4.43:4660 | 5:0X:277 | Read+Write | Always
MSA_UT_valv_UTAS_AF_Ret.Estado_abierta | 192.168.4.43:4660 | 5:0X:223 | Read+Write | Always
MSA_UT_valv_UTAS_AF_Ret.Estado_cerrada | 192.168.4.43:4660 | 5:0X:224 | Read+Write | Always
MSA_UT_valv_UTAS_AF_Ret.Fallo | 192.168.4.43:4660 | 5:0X:333 | Read+Write | Always
MSA_UT_valv_UTAS_AF_Ret.Orden_abrir | 192.168.4.43:4660 | 5:0X:278 | Read+Write | Always
MSA_UT_VM_Condens_1.Estado_abierta | 192.168.4.43:4660 | 5:0X:201 | Read+Write | Always
MSA_UT_VM_Condens_1.Fallo | 192.168.4.43:4660 | 5:0X:321 | Read+Write | Always
MSA_UT_VM_Condens_1.Orden_abrir | 192.168.4.43:4660 | 5:0X:265 | Read+Write | Always
MSA_UT_VM_Condens_2.Estado_abierta | 192.168.4.43:4660 | 5:0X:202 | Read+Write | Always
MSA_UT_VM_Condens_2.Fallo | 192.168.4.43:4660 | 5:0X:322 | Read+Write | Always
MSA_UT_VM_Condens_2.Orden_abrir | 192.168.4.43:4660 | 5:0X:266 | Read+Write | Always
MSA_UT_VM_Condens_3.Estado_abierta | 192.168.4.43:4660 | 5:0X:203 | Read+Write | Always
MSA_UT_VM_Condens_3.Fallo | 192.168.4.43:4660 | 5:0X:323 | Read+Write | Always
MSA_UT_VM_Condens_3.Orden_abrir | 192.168.4.43:4660 | 5:0X:267 | Read+Write | Always
MSA_UT_VM_Condens_4.Estado_abierta | 192.168.4.43:4660 | 5:0X:204 | Read+Write | Always
MSA_UT_VM_Condens_4.Fallo | 192.168.4.43:4660 | 5:0X:324 | Read+Write | Always
MSA_UT_VM_Condens_4.Orden_abrir | 192.168.4.43:4660 | 5:0X:268 | Read+Write | Always
MSA_BM_Extractor_VE_03.Horario_A | 192.168.4.23:4660 | 1:3X:805T80 | Read+Write | Always
MSA_BM_Extractor_VE_03.Horario_estado | 192.168.4.23:4660 | 1:0X:345 | Read | Always
MSA_BM_Extractor_VE_03.Manual_horario | 192.168.4.23:4660 | 1:0X:346 | Read+Write | Always
MSA_BM_Extractor_VE_03.Marcha_paro | 192.168.4.23:4660 | 1:0X:347 | Read+Write | Always
MSA_BM_Extractor_VE_03.Reset_horas | 192.168.4.23:4660 | 1:0X:348 | Read+Write | Always
MSA_BM_Extractor_VE_03.Horas_funcionam | 192.168.4.23:4660 | 1:3X:848 | Read | Always
MSA_BM_Extractor_VE_03.Estado | 192.168.4.23:4660 | 1:0X:237 | Read | Always
MSA_BM_Extractor_VE_03.Orden | 192.168.4.23:4660 | 1:0X:287 | Read | Always
MSA_BM_Extractor_VE_03.Fallo | 192.168.4.23:4660 | 1:0X:350 | Read | Always
MSA_BM_Extractor_VE_04.Horario_A | 192.168.4.23:4660 | 1:3X:761T80 | Read+Write | Always
MSA_BM_Extractor_VE_04.Horario_estado | 192.168.4.23:4660 | 1:0X:353 | Read | Always
MSA_BM_Extractor_VE_04.Manual_horario | 192.168.4.23:4660 | 1:0X:354 | Read+Write | Always
MSA_BM_Extractor_VE_04.Marcha_paro | 192.168.4.23:4660 | 1:0X:355 | Read+Write | Always
MSA_BM_Extractor_VE_04.Reset_horas | 192.168.4.23:4660 | 1:0X:356 | Read+Write | Always
MSA_BM_Extractor_VE_04.Horas_funcionam | 192.168.4.23:4660 | 1:3X:804 | Read | Always
MSA_BM_Extractor_VE_04.Estado | 192.168.4.23:4660 | 1:0X:238 | Read | Always
MSA_BM_Extractor_VE_04.Orden | 192.168.4.23:4660 | 1:0X:288 | Read | Always
MSA_BM_Extractor_VE_04.Fallo | 192.168.4.23:4660 | 1:0X:358 | Read | Always
MSA_BM_Extractor_VE_05.Horario_A | 192.168.4.23:4660 | 1:3X:717T80 | Read+Write | Always
MSA_BM_Extractor_VE_05.Horario_estado | 192.168.4.23:4660 | 1:0X:361 | Read | Always
MSA_BM_Extractor_VE_05.Manual_horario | 192.168.4.23:4660 | 1:0X:362 | Read+Write | Always
MSA_BM_Extractor_VE_05.Marcha_paro | 192.168.4.23:4660 | 1:0X:363 | Read+Write | Always
MSA_BM_Extractor_VE_05.Reset_horas | 192.168.4.23:4660 | 1:0X:364 | Read+Write | Always
MSA_BM_Extractor_VE_05.Horas_funcionam | 192.168.4.23:4660 | 1:3X:760 | Read | Always
MSA_BM_Extractor_VE_05.Estado | 192.168.4.23:4660 | 1:0X:239 | Read | Always
MSA_BM_Extractor_VE_05.Orden | 192.168.4.23:4660 | 1:0X:289 | Read | Always
MSA_BM_Extractor_VE_05.Fallo | 192.168.4.23:4660 | 1:0X:366 | Read | Always
MSA_BM_Extractor_VE_06.Horario_A | 192.168.4.23:4660 | 1:3X:673T80 | Read+Write | Always
MSA_BM_Extractor_VE_06.Horario_estado | 192.168.4.23:4660 | 1:0X:369 | Read | Always
MSA_BM_Extractor_VE_06.Manual_horario | 192.168.4.23:4660 | 1:0X:370 | Read+Write | Always
MSA_BM_Extractor_VE_06.Marcha_paro | 192.168.4.23:4660 | 1:0X:371 | Read+Write | Always
MSA_BM_Extractor_VE_06.Reset_horas | 192.168.4.23:4660 | 1:0X:372 | Read+Write | Always
MSA_BM_Extractor_VE_06.Horas_funcionam | 192.168.4.23:4660 | 1:3X:716 | Read | Always
MSA_BM_Extractor_VE_06.Estado | 192.168.4.23:4660 | 1:0X:240 | Read | Always
MSA_BM_Extractor_VE_06.Orden | 192.168.4.23:4660 | 1:0X:290 | Read | Always
MSA_BM_Extractor_VE_06.Fallo | 192.168.4.23:4660 | 1:0X:374 | Read | Always
MSA_BM_Vent_Extraccion_23_01.Horario_A | 192.168.4.23:4660 | 8:3X:585T80 | Read+Write | Always
MSA_BM_Vent_Extraccion_23_01.Horario_estado | 192.168.4.23:4660 | 8:0X:385 | Read | Always
MSA_BM_Vent_Extraccion_23_01.Manual_horario | 192.168.4.23:4660 | 8:0X:386 | Read+Write | Always
MSA_BM_Vent_Extraccion_23_01.Marcha_paro | 192.168.4.23:4660 | 8:0X:387 | Read+Write | Always
MSA_BM_Vent_Extraccion_23_01.Reset_horas | 192.168.4.23:4660 | 8:0X:388 | Read+Write | Always
MSA_BM_Vent_Extraccion_23_01.Horas_funcionam | 192.168.4.23:4660 | 8:3X:892 | Read | Always
MSA_BM_Vent_Extraccion_23_01.Estado | 192.168.4.23:4660 | 8:0X:224 | Read | Always
MSA_BM_Vent_Extraccion_23_01.Orden | 192.168.4.23:4660 | 8:0X:277 | Read | Always
MSA_BM_Vent_Extraccion_23_01.Fallo | 192.168.4.23:4660 | 8:0X:389 | Read | Always
MSA_BM_Vent_Extraccion_23_02.Horario_A | 192.168.4.23:4660 | 8:3X:541T80 | Read+Write | Always
MSA_BM_Vent_Extraccion_23_02.Horario_estado | 192.168.4.23:4660 | 8:0X:393 | Read | Always
MSA_BM_Vent_Extraccion_23_02.Manual_horario | 192.168.4.23:4660 | 8:0X:394 | Read+Write | Always
MSA_BM_Vent_Extraccion_23_02.Marcha_paro | 192.168.4.23:4660 | 8:0X:395 | Read+Write | Always
MSA_BM_Vent_Extraccion_23_02.Reset_horas | 192.168.4.23:4660 | 8:0X:396 | Read+Write | Always
MSA_BM_Vent_Extraccion_23_02.Horas_funcionam | 192.168.4.23:4660 | 8:3X:848 | Read | Always
MSA_BM_Vent_Extraccion_23_02.Estado | 192.168.4.23:4660 | 8:0X:225 | Read | Always
MSA_BM_Vent_Extraccion_23_02.Orden | 192.168.4.23:4660 | 8:0X:278 | Read | Always
MSA_BM_Vent_Extraccion_23_02.Fallo | 192.168.4.23:4660 | 8:0X:397 | Read | Always
MSA_BM_Vent_Extraccion_23_03.Horario_A | 192.168.4.23:4660 | 8:3X:497T80 | Read+Write | Always
MSA_BM_Vent_Extraccion_23_03.Horario_estado | 192.168.4.23:4660 | 8:0X:401 | Read | Always
MSA_BM_Vent_Extraccion_23_03.Manual_horario | 192.168.4.23:4660 | 8:0X:402 | Read+Write | Always
MSA_BM_Vent_Extraccion_23_03.Marcha_paro | 192.168.4.23:4660 | 8:0X:403 | Read+Write | Always
MSA_BM_Vent_Extraccion_23_03.Reset_horas | 192.168.4.23:4660 | 8:0X:404 | Read+Write | Always
MSA_BM_Vent_Extraccion_23_03.Horas_funcionam | 192.168.4.23:4660 | 8:3X:804 | Read | Always
MSA_BM_Vent_Extraccion_23_03.Estado | 192.168.4.23:4660 | 8:0X:226 | Read | Always
MSA_BM_Vent_Extraccion_23_03.Orden | 192.168.4.23:4660 | 8:0X:279 | Read | Always
MSA_BM_Vent_Extraccion_23_03.Fallo | 192.168.4.23:4660 | 8:0X:405 | Read | Always
MSA_BM_Vent_Extraccion_23_04.Horario_A | 192.168.4.23:4660 | 8:3X:453T80 | Read+Write | Always
MSA_BM_Vent_Extraccion_23_04.Horario_estado | 192.168.4.23:4660 | 8:0X:409 | Read | Always
MSA_BM_Vent_Extraccion_23_04.Manual_horario | 192.168.4.23:4660 | 8:0X:410 | Read+Write | Always
MSA_BM_Vent_Extraccion_23_04.Marcha_paro | 192.168.4.23:4660 | 8:0X:411 | Read+Write | Always
MSA_BM_Vent_Extraccion_23_04.Reset_horas | 192.168.4.23:4660 | 8:0X:412 | Read+Write | Always
MSA_BM_Vent_Extraccion_23_04.Horas_funcionam | 192.168.4.23:4660 | 8:3X:760 | Read | Always
MSA_BM_Vent_Extraccion_23_04.Estado | 192.168.4.23:4660 | 8:0X:227 | Read | Always
MSA_BM_Vent_Extraccion_23_04.Orden | 192.168.4.23:4660 | 8:0X:280 | Read | Always
MSA_BM_Vent_Extraccion_23_04.Fallo | 192.168.4.23:4660 | 8:0X:413 | Read | Always
MSA_BM_Vent_impulsion_23_01.Horario_A | 192.168.4.23:4660 | 8:3X:761T80 | Read+Write | Always
MSA_BM_Vent_impulsion_23_01.Horario_estado | 192.168.4.23:4660 | 8:0X:353 | Read | Always
MSA_BM_Vent_impulsion_23_01.Manual_horario | 192.168.4.23:4660 | 8:0X:354 | Read+Write | Always
MSA_BM_Vent_impulsion_23_01.Marcha_paro | 192.168.4.23:4660 | 8:0X:355 | Read+Write | Always
MSA_BM_Vent_impulsion_23_01.Reset_horas | 192.168.4.23:4660 | 8:0X:356 | Read+Write | Always
MSA_BM_Vent_impulsion_23_01.Horas_funcionam | 192.168.4.23:4660 | 8:3X:716 | Read | Always
MSA_BM_Vent_impulsion_23_01.Estado | 192.168.4.23:4660 | 8:0X:220 | Read | Always
MSA_BM_Vent_impulsion_23_01.Orden | 192.168.4.23:4660 | 8:0X:273 | Read | Always
MSA_BM_Vent_impulsion_23_01.Fallo | 192.168.4.23:4660 | 8:0X:357 | Read | Always
MSA_BM_Vent_impulsion_23_02.Horario_A | 192.168.4.23:4660 | 8:3X:717T80 | Read+Write | Always
MSA_BM_Vent_impulsion_23_02.Horario_estado | 192.168.4.23:4660 | 8:0X:361 | Read | Always
MSA_BM_Vent_impulsion_23_02.Manual_horario | 192.168.4.23:4660 | 8:0X:362 | Read+Write | Always
MSA_BM_Vent_impulsion_23_02.Marcha_paro | 192.168.4.23:4660 | 8:0X:363 | Read+Write | Always
MSA_BM_Vent_impulsion_23_02.Reset_horas | 192.168.4.23:4660 | 8:0X:364 | Read+Write | Always
MSA_BM_Vent_impulsion_23_02.Horas_funcionam | 192.168.4.23:4660 | 8:3X:1024 | Read | Always
MSA_BM_Vent_impulsion_23_02.Estado | 192.168.4.23:4660 | 8:0X:221 | Read | Always
MSA_BM_Vent_impulsion_23_02.Orden | 192.168.4.23:4660 | 8:0X:274 | Read | Always
MSA_BM_Vent_impulsion_23_02.Fallo | 192.168.4.23:4660 | 8:0X:365 | Read | Always
MSA_BM_Vent_impulsion_23_03.Horario_A | 192.168.4.23:4660 | 8:3X:673T80 | Read+Write | Always
MSA_BM_Vent_impulsion_23_03.Horario_estado | 192.168.4.23:4660 | 8:0X:369 | Read | Always
MSA_BM_Vent_impulsion_23_03.Manual_horario | 192.168.4.23:4660 | 8:0X:370 | Read+Write | Always
MSA_BM_Vent_impulsion_23_03.Marcha_paro | 192.168.4.23:4660 | 8:0X:371 | Read+Write | Always
MSA_BM_Vent_impulsion_23_03.Reset_horas | 192.168.4.23:4660 | 8:0X:372 | Read+Write | Always
MSA_BM_Vent_impulsion_23_03.Horas_funcionam | 192.168.4.23:4660 | 8:3X:980 | Read | Always
MSA_BM_Vent_impulsion_23_03.Estado | 192.168.4.23:4660 | 8:0X:222 | Read | Always
MSA_BM_Vent_impulsion_23_03.Orden | 192.168.4.23:4660 | 8:0X:275 | Read | Always
MSA_BM_Vent_impulsion_23_03.Fallo | 192.168.4.23:4660 | 8:0X:373 | Read | Always
MSA_BM_Vent_impulsion_23_04.Horario_A | 192.168.4.23:4660 | 8:3X:629T80 | Read+Write | Always
MSA_BM_Vent_impulsion_23_04.Horario_estado | 192.168.4.23:4660 | 8:0X:377 | Read | Always
MSA_BM_Vent_impulsion_23_04.Manual_horario | 192.168.4.23:4660 | 8:0X:378 | Read+Write | Always
MSA_BM_Vent_impulsion_23_04.Marcha_paro | 192.168.4.23:4660 | 8:0X:379 | Read+Write | Always
MSA_BM_Vent_impulsion_23_04.Reset_horas | 192.168.4.23:4660 | 8:0X:380 | Read+Write | Always
MSA_BM_Vent_impulsion_23_04.Horas_funcionam | 192.168.4.23:4660 | 8:3X:936 | Read | Always
MSA_BM_Vent_impulsion_23_04.Estado | 192.168.4.23:4660 | 8:0X:223 | Read | Always
MSA_BM_Vent_impulsion_23_04.Orden | 192.168.4.23:4660 | 8:0X:276 | Read | Always
MSA_BM_Vent_impulsion_23_04.Fallo | 192.168.4.23:4660 | 8:0X:381 | Read | Always
MSA_BM_Vent_aport_QM11.Horario_A | 192.168.4.23:4660 | 10:3X:365T80 | Read+Write | Always
MSA_BM_Vent_aport_QM11.Horario_estado | 192.168.4.23:4660 | 10:0X:361 | Read | Always
MSA_BM_Vent_aport_QM11.Manual_horario | 192.168.4.23:4660 | 10:0X:362 | Read+Write | Always
MSA_BM_Vent_aport_QM11.Marcha_paro | 192.168.4.23:4660 | 10:0X:363 | Read+Write | Always
MSA_BM_Vent_aport_QM11.Reset_horas | 192.168.4.23:4660 | 10:0X:364 | Read+Write | Always
MSA_BM_Vent_aport_QM11.Horas_funcionam | 192.168.4.23:4660 | 10:3X:760 | Read | Always
MSA_BM_Vent_aport_QM11.Estado | 192.168.4.23:4660 | 10:0X:203 | Read | Always
MSA_BM_Vent_aport_QM11.Orden | 192.168.4.23:4660 | 10:0X:265 | Read | Always
MSA_BM_Vent_aport_QM11.Fallo | 192.168.4.23:4660 | 10:0X:365 | Read | Always
MSA_BT_Extractor_VE_09.Horario_A | 192.168.4.33:4660 | 1:3X:805T80 | Read+Write | Always
MSA_BT_Extractor_VE_09.Horario_estado | 192.168.4.33:4660 | 1:0X:345 | Read | Always
MSA_BT_Extractor_VE_09.Manual_horario | 192.168.4.33:4660 | 1:0X:346 | Read+Write | Always
MSA_BT_Extractor_VE_09.Marcha_paro | 192.168.4.33:4660 | 1:0X:347 | Read+Write | Always
MSA_BT_Extractor_VE_09.Reset_horas | 192.168.4.33:4660 | 1:0X:348 | Read+Write | Always
MSA_BT_Extractor_VE_09.Horas_funcionam | 192.168.4.33:4660 | 1:3X:848 | Read | Always
MSA_BT_Extractor_VE_09.Estado | 192.168.4.33:4660 | 1:0X:237 | Read | Always
MSA_BT_Extractor_VE_09.Orden | 192.168.4.33:4660 | 1:0X:287 | Read | Always
MSA_BT_Extractor_VE_09.Fallo | 192.168.4.33:4660 | 1:0X:350 | Read | Always
MSA_BT_Extractor_VE_10.Horario_A | 192.168.4.33:4660 | 1:3X:761T80 | Read+Write | Always
MSA_BT_Extractor_VE_10.Horario_estado | 192.168.4.33:4660 | 1:0X:353 | Read | Always
MSA_BT_Extractor_VE_10.Manual_horario | 192.168.4.33:4660 | 1:0X:354 | Read+Write | Always
MSA_BT_Extractor_VE_10.Marcha_paro | 192.168.4.33:4660 | 1:0X:355 | Read+Write | Always
MSA_BT_Extractor_VE_10.Reset_horas | 192.168.4.33:4660 | 1:0X:356 | Read+Write | Always
MSA_BT_Extractor_VE_10.Horas_funcionam | 192.168.4.33:4660 | 1:3X:804 | Read | Always
MSA_BT_Extractor_VE_10.Estado | 192.168.4.33:4660 | 1:0X:238 | Read | Always
MSA_BT_Extractor_VE_10.Orden | 192.168.4.33:4660 | 1:0X:288 | Read | Always
MSA_BT_Extractor_VE_10.Fallo | 192.168.4.33:4660 | 1:0X:358 | Read | Always
MSA_BT_Extractor_VE_11.Horario_A | 192.168.4.33:4660 | 1:3X:717T80 | Read+Write | Always
MSA_BT_Extractor_VE_11.Horario_estado | 192.168.4.33:4660 | 1:0X:361 | Read | Always
MSA_BT_Extractor_VE_11.Manual_horario | 192.168.4.33:4660 | 1:0X:362 | Read+Write | Always
MSA_BT_Extractor_VE_11.Marcha_paro | 192.168.4.33:4660 | 1:0X:363 | Read+Write | Always
MSA_BT_Extractor_VE_11.Reset_horas | 192.168.4.33:4660 | 1:0X:364 | Read+Write | Always
MSA_BT_Extractor_VE_11.Horas_funcionam | 192.168.4.33:4660 | 1:3X:760 | Read | Always
MSA_BT_Extractor_VE_11.Estado | 192.168.4.33:4660 | 1:0X:239 | Read | Always
MSA_BT_Extractor_VE_11.Orden | 192.168.4.33:4660 | 1:0X:289 | Read | Always
MSA_BT_Extractor_VE_11.Fallo | 192.168.4.33:4660 | 1:0X:366 | Read | Always
MSA_BT_Extractor_VE_12.Horario_A | 192.168.4.33:4660 | 1:3X:673T80 | Read+Write | Always
MSA_BT_Extractor_VE_12.Horario_estado | 192.168.4.33:4660 | 1:0X:369 | Read | Always
MSA_BT_Extractor_VE_12.Manual_horario | 192.168.4.33:4660 | 1:0X:370 | Read+Write | Always
MSA_BT_Extractor_VE_12.Marcha_paro | 192.168.4.33:4660 | 1:0X:371 | Read+Write | Always
MSA_BT_Extractor_VE_12.Reset_horas | 192.168.4.33:4660 | 1:0X:372 | Read+Write | Always
MSA_BT_Extractor_VE_12.Horas_funcionam | 192.168.4.33:4660 | 1:3X:716 | Read | Always
MSA_BT_Extractor_VE_12.Estado | 192.168.4.33:4660 | 1:0X:240 | Read | Always
MSA_BT_Extractor_VE_12.Orden | 192.168.4.33:4660 | 1:0X:290 | Read | Always
MSA_BT_Extractor_VE_12.Fallo | 192.168.4.33:4660 | 1:0X:374 | Read | Always
MSA_BT_Extrac_locales_tecnicos.Horario_A | 192.168.4.33:4660 | 7:3X:673T80 | Read+Write | Always
MSA_BT_Extrac_locales_tecnicos.Horario_estado | 192.168.4.33:4660 | 7:0X:369 | Read | Always
MSA_BT_Extrac_locales_tecnicos.Manual_horario | 192.168.4.33:4660 | 7:0X:370 | Read+Write | Always
MSA_BT_Extrac_locales_tecnicos.Marcha_paro | 192.168.4.33:4660 | 7:0X:371 | Read+Write | Always
MSA_BT_Extrac_locales_tecnicos.Reset_horas | 192.168.4.33:4660 | 7:0X:372 | Read+Write | Always
MSA_BT_Extrac_locales_tecnicos.Horas_funcionam | 192.168.4.33:4660 | 7:3X:364 | Read | Always
MSA_BT_Extrac_locales_tecnicos.Estado | 192.168.4.33:4660 | 7:0X:220 | Read | Always
MSA_BT_Extrac_locales_tecnicos.Orden | 192.168.4.33:4660 | 7:0X:276 | Read | Always
MSA_BT_Extrac_locales_tecnicos.Fallo | 192.168.4.33:4660 | 7:0X:366 | Read | Always
MSA_BT_Extractor_33_01.Horario_A | 192.168.4.33:4660 | 10:3X:805T80 | Read+Write | Always
MSA_BT_Extractor_33_01.Horario_estado | 192.168.4.33:4660 | 10:0X:345 | Read | Always
MSA_BT_Extractor_33_01.Manual_horario | 192.168.4.33:4660 | 10:0X:346 | Read+Write | Always
MSA_BT_Extractor_33_01.Marcha_paro | 192.168.4.33:4660 | 10:0X:347 | Read+Write | Always
MSA_BT_Extractor_33_01.Reset_horas | 192.168.4.33:4660 | 10:0X:348 | Read+Write | Always
MSA_BT_Extractor_33_01.Horas_funcionam | 192.168.4.33:4660 | 10:3X:848 | Read | Always
MSA_BT_Extractor_33_01.Estado | 192.168.4.33:4660 | 10:0X:206 | Read | Always
MSA_BT_Extractor_33_01.Orden | 192.168.4.33:4660 | 10:0X:269 | Read | Always
MSA_BT_Extractor_33_01.Fallo | 192.168.4.33:4660 | 10:0X:349 | Read | Always
MSA_BT_Extractor_33_02.Horario_A | 192.168.4.33:4660 | 10:3X:761T80 | Read+Write | Always
MSA_BT_Extractor_33_02.Horario_estado | 192.168.4.33:4660 | 10:0X:353 | Read | Always
MSA_BT_Extractor_33_02.Manual_horario | 192.168.4.33:4660 | 10:0X:354 | Read+Write | Always
MSA_BT_Extractor_33_02.Marcha_paro | 192.168.4.33:4660 | 10:0X:355 | Read+Write | Always
MSA_BT_Extractor_33_02.Reset_horas | 192.168.4.33:4660 | 10:0X:356 | Read+Write | Always
MSA_BT_Extractor_33_02.Horas_funcionam | 192.168.4.33:4660 | 10:3X:804 | Read | Always
MSA_BT_Extractor_33_02.Estado | 192.168.4.33:4660 | 10:0X:207 | Read | Always
MSA_BT_Extractor_33_02.Orden | 192.168.4.33:4660 | 10:0X:270 | Read | Always
MSA_BT_Extractor_33_02.Fallo | 192.168.4.33:4660 | 10:0X:357 | Read | Always
MSA_BT_Extractor_33_03.Horario_A | 192.168.4.33:4660 | 10:3X:717T80 | Read+Write | Always
MSA_BT_Extractor_33_03.Horario_estado | 192.168.4.33:4660 | 10:0X:361 | Read | Always
MSA_BT_Extractor_33_03.Manual_horario | 192.168.4.33:4660 | 10:0X:362 | Read+Write | Always
MSA_BT_Extractor_33_03.Marcha_paro | 192.168.4.33:4660 | 10:0X:363 | Read+Write | Always
MSA_BT_Extractor_33_03.Reset_horas | 192.168.4.33:4660 | 10:0X:364 | Read+Write | Always
MSA_BT_Extractor_33_03.Horas_funcionam | 192.168.4.33:4660 | 10:3X:760 | Read | Always
MSA_BT_Extractor_33_03.Estado | 192.168.4.33:4660 | 10:0X:208 | Read | Always
MSA_BT_Extractor_33_03.Orden | 192.168.4.33:4660 | 10:0X:273 | Read | Always
MSA_BT_Extractor_33_03.Fallo | 192.168.4.33:4660 | 10:0X:365 | Read | Always
MSA_BT_Extractor_33_04.Horario_A | 192.168.4.33:4660 | 10:3X:673T80 | Read+Write | Always
MSA_BT_Extractor_33_04.Horario_estado | 192.168.4.33:4660 | 10:0X:369 | Read | Always
MSA_BT_Extractor_33_04.Manual_horario | 192.168.4.33:4660 | 10:0X:370 | Read+Write | Always
MSA_BT_Extractor_33_04.Marcha_paro | 192.168.4.33:4660 | 10:0X:371 | Read+Write | Always
MSA_BT_Extractor_33_04.Reset_horas | 192.168.4.33:4660 | 10:0X:372 | Read+Write | Always
MSA_BT_Extractor_33_04.Horas_funcionam | 192.168.4.33:4660 | 10:3X:716 | Read | Always
MSA_BT_Extractor_33_04.Estado | 192.168.4.33:4660 | 10:0X:217 | Read | Always
MSA_BT_Extractor_33_04.Orden | 192.168.4.33:4660 | 10:0X:274 | Read | Always
MSA_BT_Extractor_33_04.Fallo | 192.168.4.33:4660 | 10:0X:373 | Read | Always
MSA_BT_Vent_aport_33_01.Horario_A | 192.168.4.33:4660 | 10:3X:981T80 | Read+Write | Always
MSA_BT_Vent_aport_33_01.Horario_estado | 192.168.4.33:4660 | 10:0X:313 | Read | Always
MSA_BT_Vent_aport_33_01.Manual_horario | 192.168.4.33:4660 | 10:0X:314 | Read+Write | Always
MSA_BT_Vent_aport_33_01.Marcha_paro | 192.168.4.33:4660 | 10:0X:315 | Read+Write | Always
MSA_BT_Vent_aport_33_01.Reset_horas | 192.168.4.33:4660 | 10:0X:316 | Read+Write | Always
MSA_BT_Vent_aport_33_01.Horas_funcionam | 192.168.4.33:4660 | 10:3X:1024 | Read | Always
MSA_BT_Vent_aport_33_01.Estado | 192.168.4.33:4660 | 10:0X:202 | Read | Always
MSA_BT_Vent_aport_33_01.Orden | 192.168.4.33:4660 | 10:0X:265 | Read | Always
MSA_BT_Vent_aport_33_01.Fallo | 192.168.4.33:4660 | 10:0X:317 | Read | Always
MSA_BT_Vent_aport_33_02.Horario_A | 192.168.4.33:4660 | 10:3X:937T80 | Read+Write | Always
MSA_BT_Vent_aport_33_02.Horario_estado | 192.168.4.33:4660 | 10:0X:321 | Read | Always
MSA_BT_Vent_aport_33_02.Manual_horario | 192.168.4.33:4660 | 10:0X:322 | Read+Write | Always
MSA_BT_Vent_aport_33_02.Marcha_paro | 192.168.4.33:4660 | 10:0X:323 | Read+Write | Always
MSA_BT_Vent_aport_33_02.Reset_horas | 192.168.4.33:4660 | 10:0X:324 | Read+Write | Always
MSA_BT_Vent_aport_33_02.Horas_funcionam | 192.168.4.33:4660 | 10:3X:980 | Read | Always
MSA_BT_Vent_aport_33_02.Estado | 192.168.4.33:4660 | 10:0X:203 | Read | Always
MSA_BT_Vent_aport_33_02.Orden | 192.168.4.33:4660 | 10:0X:266 | Read | Always
MSA_BT_Vent_aport_33_02.Fallo | 192.168.4.33:4660 | 10:0X:325 | Read | Always
MSA_BT_Vent_aport_33_03.Horario_A | 192.168.4.33:4660 | 10:3X:893T80 | Read+Write | Always
MSA_BT_Vent_aport_33_03.Horario_estado | 192.168.4.33:4660 | 10:0X:329 | Read | Always
MSA_BT_Vent_aport_33_03.Manual_horario | 192.168.4.33:4660 | 10:0X:330 | Read+Write | Always
MSA_BT_Vent_aport_33_03.Marcha_paro | 192.168.4.33:4660 | 10:0X:331 | Read+Write | Always
MSA_BT_Vent_aport_33_03.Reset_horas | 192.168.4.33:4660 | 10:0X:332 | Read+Write | Always
MSA_BT_Vent_aport_33_03.Horas_funcionam | 192.168.4.33:4660 | 10:3X:936 | Read | Always
MSA_BT_Vent_aport_33_03.Estado | 192.168.4.33:4660 | 10:0X:204 | Read | Always
MSA_BT_Vent_aport_33_03.Orden | 192.168.4.33:4660 | 10:0X:267 | Read | Always
MSA_BT_Vent_aport_33_03.Fallo | 192.168.4.33:4660 | 10:0X:333 | Read | Always
MSA_BT_Vent_aport_33_04.Horario_A | 192.168.4.33:4660 | 10:3X:849T80 | Read+Write | Always
MSA_BT_Vent_aport_33_04.Horario_estado | 192.168.4.33:4660 | 10:0X:337 | Read | Always
MSA_BT_Vent_aport_33_04.Manual_horario | 192.168.4.33:4660 | 10:0X:338 | Read+Write | Always
MSA_BT_Vent_aport_33_04.Marcha_paro | 192.168.4.33:4660 | 10:0X:339 | Read+Write | Always
MSA_BT_Vent_aport_33_04.Reset_horas | 192.168.4.33:4660 | 10:0X:340 | Read+Write | Always
MSA_BT_Vent_aport_33_04.Horas_funcionam | 192.168.4.33:4660 | 10:3X:892 | Read | Always
MSA_BT_Vent_aport_33_04.Estado | 192.168.4.33:4660 | 10:0X:205 | Read | Always
MSA_BT_Vent_aport_33_04.Orden | 192.168.4.33:4660 | 10:0X:268 | Read | Always
MSA_BT_Vent_aport_33_04.Fallo | 192.168.4.33:4660 | 10:0X:341 | Read | Always
MSA_BT_Vent_imp_S_tecnicas.Horario_A | 192.168.4.33:4660 | 7:3X:717T80 | Read+Write | Always
MSA_BT_Vent_imp_S_tecnicas.Horario_estado | 192.168.4.33:4660 | 7:0X:361 | Read | Always
MSA_BT_Vent_imp_S_tecnicas.Manual_horario | 192.168.4.33:4660 | 7:0X:362 | Read+Write | Always
MSA_BT_Vent_imp_S_tecnicas.Marcha_paro | 192.168.4.33:4660 | 7:0X:363 | Read+Write | Always
MSA_BT_Vent_imp_S_tecnicas.Reset_horas | 192.168.4.33:4660 | 7:0X:364 | Read+Write | Always
MSA_BT_Vent_imp_S_tecnicas.Horas_funcionam | 192.168.4.33:4660 | 7:3X:408 | Read | Always
MSA_BT_Vent_imp_S_tecnicas.Estado | 192.168.4.33:4660 | 7:0X:219 | Read | Always
MSA_BT_Vent_imp_S_tecnicas.Orden | 192.168.4.33:4660 | 7:0X:275 | Read | Always
MSA_BT_Vent_imp_S_tecnicas.Fallo | 192.168.4.33:4660 | 7:0X:365 | Read | Always
MSA_UT_Extractor_VE_15.Horario_A | 192.168.4.43:4660 | 1:3X:805T80 | Read+Write | Always
MSA_UT_Extractor_VE_15.Horario_estado | 192.168.4.43:4660 | 1:0X:345 | Read | Always
MSA_UT_Extractor_VE_15.Manual_horario | 192.168.4.43:4660 | 1:0X:346 | Read+Write | Always
MSA_UT_Extractor_VE_15.Marcha_paro | 192.168.4.43:4660 | 1:0X:347 | Read+Write | Always
MSA_UT_Extractor_VE_15.Reset_horas | 192.168.4.43:4660 | 1:0X:348 | Read+Write | Always
MSA_UT_Extractor_VE_15.Horas_funcionam | 192.168.4.43:4660 | 1:3X:848 | Read | Always
MSA_UT_Extractor_VE_15.Estado | 192.168.4.43:4660 | 1:0X:237 | Read | Always
MSA_UT_Extractor_VE_15.Orden | 192.168.4.43:4660 | 1:0X:287 | Read | Always
MSA_UT_Extractor_VE_15.Fallo | 192.168.4.43:4660 | 1:0X:350 | Read | Always
MSA_UT_Extractor_VE_16.Horario_A | 192.168.4.43:4660 | 1:3X:761T80 | Read+Write | Always
MSA_UT_Extractor_VE_16.Horario_estado | 192.168.4.43:4660 | 1:0X:353 | Read | Always
MSA_UT_Extractor_VE_16.Manual_horario | 192.168.4.43:4660 | 1:0X:354 | Read+Write | Always
MSA_UT_Extractor_VE_16.Marcha_paro | 192.168.4.43:4660 | 1:0X:355 | Read+Write | Always
MSA_UT_Extractor_VE_16.Reset_horas | 192.168.4.43:4660 | 1:0X:356 | Read+Write | Always
MSA_UT_Extractor_VE_16.Horas_funcionam | 192.168.4.43:4660 | 1:3X:804 | Read | Always
MSA_UT_Extractor_VE_16.Estado | 192.168.4.43:4660 | 1:0X:238 | Read | Always
MSA_UT_Extractor_VE_16.Orden | 192.168.4.43:4660 | 1:0X:288 | Read | Always
MSA_UT_Extractor_VE_16.Fallo | 192.168.4.43:4660 | 1:0X:358 | Read | Always
MSA_UT_Extractor_VE_17.Horario_A | 192.168.4.43:4660 | 1:3X:717T80 | Read+Write | Always
MSA_UT_Extractor_VE_17.Horario_estado | 192.168.4.43:4660 | 1:0X:361 | Read | Always
MSA_UT_Extractor_VE_17.Manual_horario | 192.168.4.43:4660 | 1:0X:362 | Read+Write | Always
MSA_UT_Extractor_VE_17.Marcha_paro | 192.168.4.43:4660 | 1:0X:363 | Read+Write | Always
MSA_UT_Extractor_VE_17.Reset_horas | 192.168.4.43:4660 | 1:0X:364 | Read+Write | Always
MSA_UT_Extractor_VE_17.Horas_funcionam | 192.168.4.43:4660 | 1:3X:760 | Read | Always
MSA_UT_Extractor_VE_17.Estado | 192.168.4.43:4660 | 1:0X:239 | Read | Always
MSA_UT_Extractor_VE_17.Orden | 192.168.4.43:4660 | 1:0X:289 | Read | Always
MSA_UT_Extractor_VE_17.Fallo | 192.168.4.43:4660 | 1:0X:366 | Read | Always
MSA_UT_Extractor_VE_18.Horario_A | 192.168.4.43:4660 | 1:3X:673T80 | Read+Write | Always
MSA_UT_Extractor_VE_18.Horario_estado | 192.168.4.43:4660 | 1:0X:369 | Read | Always
MSA_UT_Extractor_VE_18.Manual_horario | 192.168.4.43:4660 | 1:0X:370 | Read+Write | Always
MSA_UT_Extractor_VE_18.Marcha_paro | 192.168.4.43:4660 | 1:0X:371 | Read+Write | Always
MSA_UT_Extractor_VE_18.Reset_horas | 192.168.4.43:4660 | 1:0X:372 | Read+Write | Always
MSA_UT_Extractor_VE_18.Horas_funcionam | 192.168.4.43:4660 | 1:3X:716 | Read | Always
MSA_UT_Extractor_VE_18.Estado | 192.168.4.43:4660 | 1:0X:240 | Read | Always
MSA_UT_Extractor_VE_18.Orden | 192.168.4.43:4660 | 1:0X:290 | Read | Always
MSA_UT_Extractor_VE_18.Fallo | 192.168.4.43:4660 | 1:0X:374 | Read | Always
MSA_UT_Extractor_UT_42_01.Horario_A | 192.168.4.43:4660 | 7:3X:805T80 | Read+Write | Always
MSA_UT_Extractor_UT_42_01.Horario_estado | 192.168.4.43:4660 | 7:0X:345 | Read | Always
MSA_UT_Extractor_UT_42_01.Manual_horario | 192.168.4.43:4660 | 7:0X:346 | Read+Write | Always
MSA_UT_Extractor_UT_42_01.Marcha_paro | 192.168.4.43:4660 | 7:0X:347 | Read+Write | Always
MSA_UT_Extractor_UT_42_01.Reset_horas | 192.168.4.43:4660 | 7:0X:348 | Read+Write | Always
MSA_UT_Extractor_UT_42_01.Horas_funcionam | 192.168.4.43:4660 | 7:3X:1024 | Read | Always
MSA_UT_Extractor_UT_42_01.Estado | 192.168.4.43:4660 | 7:0X:205 | Read | Always
MSA_UT_Extractor_UT_42_01.Orden | 192.168.4.43:4660 | 7:0X:269 | Read | Always
MSA_UT_Extractor_UT_42_01.Fallo | 192.168.4.43:4660 | 7:0X:349 | Read | Always
MSA_UT_Extractor_UT_42_02.Horario_A | 192.168.4.43:4660 | 7:3X:761T80 | Read+Write | Always
MSA_UT_Extractor_UT_42_02.Horario_estado | 192.168.4.43:4660 | 7:0X:353 | Read | Always
MSA_UT_Extractor_UT_42_02.Manual_horario | 192.168.4.43:4660 | 7:0X:354 | Read+Write | Always
MSA_UT_Extractor_UT_42_02.Marcha_paro | 192.168.4.43:4660 | 7:0X:355 | Read+Write | Always
MSA_UT_Extractor_UT_42_02.Reset_horas | 192.168.4.43:4660 | 7:0X:356 | Read+Write | Always
MSA_UT_Extractor_UT_42_02.Horas_funcionam | 192.168.4.43:4660 | 7:3X:980 | Read | Always
MSA_UT_Extractor_UT_42_02.Estado | 192.168.4.43:4660 | 7:0X:206 | Read | Always
MSA_UT_Extractor_UT_42_02.Orden | 192.168.4.43:4660 | 7:0X:270 | Read | Always
MSA_UT_Extractor_UT_42_02.Fallo | 192.168.4.43:4660 | 7:0X:357 | Read | Always
MSA_UT_Extractor_UT_42_03.Horario_A | 192.168.4.43:4660 | 7:3X:717T80 | Read+Write | Always
MSA_UT_Extractor_UT_42_03.Horario_estado | 192.168.4.43:4660 | 7:0X:361 | Read | Always
MSA_UT_Extractor_UT_42_03.Manual_horario | 192.168.4.43:4660 | 7:0X:362 | Read+Write | Always
MSA_UT_Extractor_UT_42_03.Marcha_paro | 192.168.4.43:4660 | 7:0X:363 | Read+Write | Always
MSA_UT_Extractor_UT_42_03.Reset_horas | 192.168.4.43:4660 | 7:0X:364 | Read+Write | Always
MSA_UT_Extractor_UT_42_03.Horas_funcionam | 192.168.4.43:4660 | 7:3X:936 | Read | Always
MSA_UT_Extractor_UT_42_03.Estado | 192.168.4.43:4660 | 7:0X:217 | Read | Always
MSA_UT_Extractor_UT_42_03.Orden | 192.168.4.43:4660 | 7:0X:273 | Read | Always
MSA_UT_Extractor_UT_42_03.Fallo | 192.168.4.43:4660 | 7:0X:365 | Read | Always
MSA_UT_Extractor_UT_42_04.Horario_A | 192.168.4.43:4660 | 7:3X:673T80 | Read+Write | Always
MSA_UT_Extractor_UT_42_04.Horario_estado | 192.168.4.43:4660 | 7:0X:369 | Read | Always
MSA_UT_Extractor_UT_42_04.Manual_horario | 192.168.4.43:4660 | 7:0X:370 | Read+Write | Always
MSA_UT_Extractor_UT_42_04.Marcha_paro | 192.168.4.43:4660 | 7:0X:371 | Read+Write | Always
MSA_UT_Extractor_UT_42_04.Reset_horas | 192.168.4.43:4660 | 7:0X:372 | Read+Write | Always
MSA_UT_Extractor_UT_42_04.Horas_funcionam | 192.168.4.43:4660 | 7:3X:892 | Read | Always
MSA_UT_Extractor_UT_42_04.Estado | 192.168.4.43:4660 | 7:0X:218 | Read | Always
MSA_UT_Extractor_UT_42_04.Orden | 192.168.4.43:4660 | 7:0X:274 | Read | Always
MSA_UT_Extractor_UT_42_04.Fallo | 192.168.4.43:4660 | 7:0X:373 | Read | Always
MSA_UT_Extractor_UTU_42_01.Horario_A | 192.168.4.43:4660 | 7:3X:629T80 | Read+Write | Always
MSA_UT_Extractor_UTU_42_01.Horario_estado | 192.168.4.43:4660 | 7:0X:377 | Read | Always
MSA_UT_Extractor_UTU_42_01.Manual_horario | 192.168.4.43:4660 | 7:0X:378 | Read+Write | Always
MSA_UT_Extractor_UTU_42_01.Marcha_paro | 192.168.4.43:4660 | 7:0X:379 | Read+Write | Always
MSA_UT_Extractor_UTU_42_01.Reset_horas | 192.168.4.43:4660 | 7:0X:380 | Read+Write | Always
MSA_UT_Extractor_UTU_42_01.Horas_funcionam | 192.168.4.43:4660 | 7:3X:848 | Read | Always
MSA_UT_Extractor_UTU_42_01.Estado | 192.168.4.43:4660 | 7:0X:219 | Read | Always
MSA_UT_Extractor_UTU_42_01.Orden | 192.168.4.43:4660 | 7:0X:275 | Read | Always
MSA_UT_Extractor_UTU_42_01.Fallo | 192.168.4.43:4660 | 7:0X:381 | Read | Always
MSA_UT_Extractor_UTU_42_02.Horario_A | 192.168.4.43:4660 | 7:3X:585T80 | Read+Write | Always
MSA_UT_Extractor_UTU_42_02.Horario_estado | 192.168.4.43:4660 | 7:0X:385 | Read | Always
MSA_UT_Extractor_UTU_42_02.Manual_horario | 192.168.4.43:4660 | 7:0X:386 | Read+Write | Always
MSA_UT_Extractor_UTU_42_02.Marcha_paro | 192.168.4.43:4660 | 7:0X:387 | Read+Write | Always
MSA_UT_Extractor_UTU_42_02.Reset_horas | 192.168.4.43:4660 | 7:0X:388 | Read+Write | Always
MSA_UT_Extractor_UTU_42_02.Horas_funcionam | 192.168.4.43:4660 | 7:3X:804 | Read | Always
MSA_UT_Extractor_UTU_42_02.Estado | 192.168.4.43:4660 | 7:0X:220 | Read | Always
MSA_UT_Extractor_UTU_42_02.Orden | 192.168.4.43:4660 | 7:0X:276 | Read | Always
MSA_UT_Extractor_UTU_42_02.Fallo | 192.168.4.43:4660 | 7:0X:389 | Read | Always
MSA_UT_Extractor_UTU_42_03.Horario_A | 192.168.4.43:4660 | 7:3X:541T80 | Read+Write | Always
MSA_UT_Extractor_UTU_42_03.Horario_estado | 192.168.4.43:4660 | 7:0X:393 | Read | Always
MSA_UT_Extractor_UTU_42_03.Manual_horario | 192.168.4.43:4660 | 7:0X:394 | Read+Write | Always
MSA_UT_Extractor_UTU_42_03.Marcha_paro | 192.168.4.43:4660 | 7:0X:395 | Read+Write | Always
MSA_UT_Extractor_UTU_42_03.Reset_horas | 192.168.4.43:4660 | 7:0X:396 | Read+Write | Always
MSA_UT_Extractor_UTU_42_03.Horas_funcionam | 192.168.4.43:4660 | 7:3X:760 | Read | Always
MSA_UT_Extractor_UTU_42_03.Estado | 192.168.4.43:4660 | 7:0X:221 | Read | Always
MSA_UT_Extractor_UTU_42_03.Orden | 192.168.4.43:4660 | 7:0X:277 | Read | Always
MSA_UT_Extractor_UTU_42_03.Fallo | 192.168.4.43:4660 | 7:0X:397 | Read | Always
MSA_UT_Extractor_UTU_42_04.Horario_A | 192.168.4.43:4660 | 7:3X:497T80 | Read+Write | Always
MSA_UT_Extractor_UTU_42_04.Horario_estado | 192.168.4.43:4660 | 7:0X:401 | Read | Always
MSA_UT_Extractor_UTU_42_04.Manual_horario | 192.168.4.43:4660 | 7:0X:402 | Read+Write | Always
MSA_UT_Extractor_UTU_42_04.Marcha_paro | 192.168.4.43:4660 | 7:0X:403 | Read+Write | Always
MSA_UT_Extractor_UTU_42_04.Reset_horas | 192.168.4.43:4660 | 7:0X:404 | Read+Write | Always
MSA_UT_Extractor_UTU_42_04.Horas_funcionam | 192.168.4.43:4660 | 7:3X:716 | Read | Always
MSA_UT_Extractor_UTU_42_04.Estado | 192.168.4.43:4660 | 7:0X:222 | Read | Always
MSA_UT_Extractor_UTU_42_04.Orden | 192.168.4.43:4660 | 7:0X:278 | Read | Always
MSA_UT_Extractor_UTU_42_04.Fallo | 192.168.4.43:4660 | 7:0X:405 | Read | Always
MSA_UT_Extractor_locales_tecnicos.Horario_A | 192.168.4.43:4660 | 7:3X:409T80 | Read+Write | Always
MSA_UT_Extractor_locales_tecnicos.Horario_estado | 192.168.4.43:4660 | 7:0X:417 | Read | Always
MSA_UT_Extractor_locales_tecnicos.Manual_horario | 192.168.4.43:4660 | 7:0X:418 | Read+Write | Always
MSA_UT_Extractor_locales_tecnicos.Marcha_paro | 192.168.4.43:4660 | 7:0X:419 | Read+Write | Always
MSA_UT_Extractor_locales_tecnicos.Reset_horas | 192.168.4.43:4660 | 7:0X:420 | Read+Write | Always
MSA_UT_Extractor_locales_tecnicos.Horas_funcionam | 192.168.4.43:4660 | 7:3X:628 | Read | Always
MSA_UT_Extractor_locales_tecnicos.Estado | 192.168.4.43:4660 | 7:0X:224 | Read | Always
MSA_UT_Extractor_locales_tecnicos.Orden | 192.168.4.43:4660 | 7:0X:280 | Read | Always
MSA_UT_Extractor_locales_tecnicos.Fallo | 192.168.4.43:4660 | 7:0X:421 | Read | Always
MSA_UT_Extractor_Servicios.Horario_A | 192.168.4.43:4660 | 9:3X:805T80 | Read+Write | Always
MSA_UT_Extractor_Servicios.Horario_estado | 192.168.4.43:4660 | 9:0X:345 | Read | Always
MSA_UT_Extractor_Servicios.Manual_horario | 192.168.4.43:4660 | 9:0X:346 | Read+Write | Always
MSA_UT_Extractor_Servicios.Marcha_paro | 192.168.4.43:4660 | 9:0X:347 | Read+Write | Always
MSA_UT_Extractor_Servicios.Reset_horas | 192.168.4.43:4660 | 9:0X:348 | Read+Write | Always
MSA_UT_Extractor_Servicios.Horas_funcionam | 192.168.4.43:4660 | 9:3X:848 | Read | Always
MSA_UT_Extractor_Servicios.Estado | 192.168.4.43:4660 | 9:0X:205 | Read | Always
MSA_UT_Extractor_Servicios.Orden | 192.168.4.43:4660 | 9:0X:269 | Read | Always
MSA_UT_Extractor_Servicios.Fallo | 192.168.4.43:4660 | 9:0X:349 | Read | Always
MSA_UT_Extractor_Complem.Horario_A | 192.168.4.43:4660 | 9:3X:761T80 | Read+Write | Always
MSA_UT_Extractor_Complem.Horario_estado | 192.168.4.43:4660 | 9:0X:353 | Read | Always
MSA_UT_Extractor_Complem.Manual_horario | 192.168.4.43:4660 | 9:0X:354 | Read+Write | Always
MSA_UT_Extractor_Complem.Marcha_paro | 192.168.4.43:4660 | 9:0X:355 | Read+Write | Always
MSA_UT_Extractor_Complem.Reset_horas | 192.168.4.43:4660 | 9:0X:356 | Read+Write | Always
MSA_UT_Extractor_Complem.Horas_funcionam | 192.168.4.43:4660 | 9:3X:804 | Read | Always
MSA_UT_Extractor_Complem.Estado | 192.168.4.43:4660 | 9:0X:206 | Read | Always
MSA_UT_Extractor_Complem.Orden | 192.168.4.43:4660 | 9:0X:270 | Read | Always
MSA_UT_Extractor_Complem.Fallo | 192.168.4.43:4660 | 9:0X:357 | Read | Always
MSA_UT_Ventil_imp_locales_tecnicos.Horario_A | 192.168.4.43:4660 | 7:3X:453T80 | Read+Write | Always
MSA_UT_Ventil_imp_locales_tecnicos.Horario_estado | 192.168.4.43:4660 | 7:0X:409 | Read | Always
MSA_UT_Ventil_imp_locales_tecnicos.Manual_horario | 192.168.4.43:4660 | 7:0X:410 | Read+Write | Always
MSA_UT_Ventil_imp_locales_tecnicos.Marcha_paro | 192.168.4.43:4660 | 7:0X:411 | Read+Write | Always
MSA_UT_Ventil_imp_locales_tecnicos.Reset_horas | 192.168.4.43:4660 | 7:0X:412 | Read+Write | Always
MSA_UT_Ventil_imp_locales_tecnicos.Horas_funcionam | 192.168.4.43:4660 | 7:3X:672 | Read | Always
MSA_UT_Ventil_imp_locales_tecnicos.Estado | 192.168.4.43:4660 | 7:0X:223 | Read | Always
MSA_UT_Ventil_imp_locales_tecnicos.Orden | 192.168.4.43:4660 | 7:0X:279 | Read | Always
MSA_UT_Ventil_imp_locales_tecnicos.Fallo | 192.168.4.43:4660 | 7:0X:413 | Read | Always
MSA_UT_Ventil_impuls_43_01.Horario_A | 192.168.4.43:4660 | 9:3X:981T80 | Read+Write | Always
MSA_UT_Ventil_impuls_43_01.Horario_estado | 192.168.4.43:4660 | 9:0X:313 | Read | Always
MSA_UT_Ventil_impuls_43_01.Manual_horario | 192.168.4.43:4660 | 9:0X:314 | Read+Write | Always
MSA_UT_Ventil_impuls_43_01.Marcha_paro | 192.168.4.43:4660 | 9:0X:315 | Read+Write | Always
MSA_UT_Ventil_impuls_43_01.Reset_horas | 192.168.4.43:4660 | 9:0X:316 | Read+Write | Always
MSA_UT_Ventil_impuls_43_01.Horas_funcionam | 192.168.4.43:4660 | 9:3X:1024 | Read | Always
MSA_UT_Ventil_impuls_43_01.Estado | 192.168.4.43:4660 | 9:0X:201 | Read | Always
MSA_UT_Ventil_impuls_43_01.Orden | 192.168.4.43:4660 | 9:0X:265 | Read | Always
MSA_UT_Ventil_impuls_43_01.Fallo | 192.168.4.43:4660 | 9:0X:317 | Read | Always
MSA_UT_Ventil_impuls_43_02.Horario_A | 192.168.4.43:4660 | 9:3X:937T80 | Read+Write | Always
MSA_UT_Ventil_impuls_43_02.Horario_estado | 192.168.4.43:4660 | 9:0X:321 | Read | Always
MSA_UT_Ventil_impuls_43_02.Manual_horario | 192.168.4.43:4660 | 9:0X:322 | Read+Write | Always
MSA_UT_Ventil_impuls_43_02.Marcha_paro | 192.168.4.43:4660 | 9:0X:323 | Read+Write | Always
MSA_UT_Ventil_impuls_43_02.Reset_horas | 192.168.4.43:4660 | 9:0X:324 | Read+Write | Always
MSA_UT_Ventil_impuls_43_02.Horas_funcionam | 192.168.4.43:4660 | 9:3X:980 | Read | Always
MSA_UT_Ventil_impuls_43_02.Estado | 192.168.4.43:4660 | 9:0X:202 | Read | Always
MSA_UT_Ventil_impuls_43_02.Orden | 192.168.4.43:4660 | 9:0X:266 | Read | Always
MSA_UT_Ventil_impuls_43_02.Fallo | 192.168.4.43:4660 | 9:0X:325 | Read | Always
MSA_UT_Ventil_impuls_43_03.Horario_A | 192.168.4.43:4660 | 9:3X:893T80 | Read+Write | Always
MSA_UT_Ventil_impuls_43_03.Horario_estado | 192.168.4.43:4660 | 9:0X:329 | Read | Always
MSA_UT_Ventil_impuls_43_03.Manual_horario | 192.168.4.43:4660 | 9:0X:330 | Read+Write | Always
MSA_UT_Ventil_impuls_43_03.Marcha_paro | 192.168.4.43:4660 | 9:0X:331 | Read+Write | Always
MSA_UT_Ventil_impuls_43_03.Reset_horas | 192.168.4.43:4660 | 9:0X:332 | Read+Write | Always
MSA_UT_Ventil_impuls_43_03.Horas_funcionam | 192.168.4.43:4660 | 9:3X:936 | Read | Always
MSA_UT_Ventil_impuls_43_03.Estado | 192.168.4.43:4660 | 9:0X:203 | Read | Always
MSA_UT_Ventil_impuls_43_03.Orden | 192.168.4.43:4660 | 9:0X:267 | Read | Always
MSA_UT_Ventil_impuls_43_03.Fallo | 192.168.4.43:4660 | 9:0X:333 | Read | Always
MSA_UT_Ventil_impuls_43_04.Horario_A | 192.168.4.43:4660 | 9:3X:849T80 | Read+Write | Always
MSA_UT_Ventil_impuls_43_04.Horario_estado | 192.168.4.43:4660 | 9:0X:337 | Read | Always
MSA_UT_Ventil_impuls_43_04.Manual_horario | 192.168.4.43:4660 | 9:0X:338 | Read+Write | Always
MSA_UT_Ventil_impuls_43_04.Marcha_paro | 192.168.4.43:4660 | 9:0X:339 | Read+Write | Always
MSA_UT_Ventil_impuls_43_04.Reset_horas | 192.168.4.43:4660 | 9:0X:340 | Read+Write | Always
MSA_UT_Ventil_impuls_43_04.Horas_funcionam | 192.168.4.43:4660 | 9:3X:892 | Read | Always
MSA_UT_Ventil_impuls_43_04.Estado | 192.168.4.43:4660 | 9:0X:204 | Read | Always
MSA_UT_Ventil_impuls_43_04.Orden | 192.168.4.43:4660 | 9:0X:268 | Read | Always
MSA_UT_Ventil_impuls_43_04.Fallo | 192.168.4.43:4660 | 9:0X:341 | Read | Always
MSA_UT_Ventil_impuls_43_01_UTU.Horario_A | 192.168.4.43:4660 | 10:3X:981T80 | Read+Write | Always
MSA_UT_Ventil_impuls_43_01_UTU.Horario_estado | 192.168.4.43:4660 | 10:0X:313 | Read | Always
MSA_UT_Ventil_impuls_43_01_UTU.Manual_horario | 192.168.4.43:4660 | 10:0X:314 | Read+Write | Always
MSA_UT_Ventil_impuls_43_01_UTU.Marcha_paro | 192.168.4.43:4660 | 10:0X:315 | Read+Write | Always
MSA_UT_Ventil_impuls_43_01_UTU.Reset_horas | 192.168.4.43:4660 | 10:0X:316 | Read+Write | Always
MSA_UT_Ventil_impuls_43_01_UTU.Horas_funcionam | 192.168.4.43:4660 | 10:3X:760 | Read | Always
MSA_UT_Ventil_impuls_43_01_UTU.Estado | 192.168.4.43:4660 | 10:0X:201 | Read | Always
MSA_UT_Ventil_impuls_43_01_UTU.Orden | 192.168.4.43:4660 | 10:0X:265 | Read | Always
MSA_UT_Ventil_impuls_43_01_UTU.Fallo | 192.168.4.43:4660 | 10:0X:317 | Read | Always
MSA_UT_Ventil_impuls_43_02_UTU.Horario_A | 192.168.4.43:4660 | 10:3X:937T80 | Read+Write | Always
MSA_UT_Ventil_impuls_43_02_UTU.Horario_estado | 192.168.4.43:4660 | 10:0X:321 | Read | Always
MSA_UT_Ventil_impuls_43_02_UTU.Manual_horario | 192.168.4.43:4660 | 10:0X:322 | Read+Write | Always
MSA_UT_Ventil_impuls_43_02_UTU.Marcha_paro | 192.168.4.43:4660 | 10:0X:323 | Read+Write | Always
MSA_UT_Ventil_impuls_43_02_UTU.Reset_horas | 192.168.4.43:4660 | 10:0X:324 | Read+Write | Always
MSA_UT_Ventil_impuls_43_02_UTU.Horas_funcionam | 192.168.4.43:4660 | 10:3X:716 | Read | Always
MSA_UT_Ventil_impuls_43_02_UTU.Estado | 192.168.4.43:4660 | 10:0X:202 | Read | Always
MSA_UT_Ventil_impuls_43_02_UTU.Orden | 192.168.4.43:4660 | 10:0X:266 | Read | Always
MSA_UT_Ventil_impuls_43_02_UTU.Fallo | 192.168.4.43:4660 | 10:0X:325 | Read | Always
MSA_UT_Ventil_impuls_43_03_UTU.Horario_A | 192.168.4.43:4660 | 10:3X:893T80 | Read+Write | Always
MSA_UT_Ventil_impuls_43_03_UTU.Horario_estado | 192.168.4.43:4660 | 10:0X:329 | Read | Always
MSA_UT_Ventil_impuls_43_03_UTU.Manual_horario | 192.168.4.43:4660 | 10:0X:330 | Read+Write | Always
MSA_UT_Ventil_impuls_43_03_UTU.Marcha_paro | 192.168.4.43:4660 | 10:0X:331 | Read+Write | Always
MSA_UT_Ventil_impuls_43_03_UTU.Reset_horas | 192.168.4.43:4660 | 10:0X:332 | Read+Write | Always
MSA_UT_Ventil_impuls_43_03_UTU.Horas_funcionam | 192.168.4.43:4660 | 10:3X:672 | Read | Always
MSA_UT_Ventil_impuls_43_03_UTU.Estado | 192.168.4.43:4660 | 10:0X:203 | Read | Always
MSA_UT_Ventil_impuls_43_03_UTU.Orden | 192.168.4.43:4660 | 10:0X:267 | Read | Always
MSA_UT_Ventil_impuls_43_03_UTU.Fallo | 192.168.4.43:4660 | 10:0X:333 | Read | Always
MSA_UT_Ventil_impuls_43_04_UTU.Horario_A | 192.168.4.43:4660 | 10:3X:849T80 | Read+Write | Always
MSA_UT_Ventil_impuls_43_04_UTU.Horario_estado | 192.168.4.43:4660 | 10:0X:337 | Read | Always
MSA_UT_Ventil_impuls_43_04_UTU.Manual_horario | 192.168.4.43:4660 | 10:0X:338 | Read+Write | Always
MSA_UT_Ventil_impuls_43_04_UTU.Marcha_paro | 192.168.4.43:4660 | 10:0X:339 | Read+Write | Always
MSA_UT_Ventil_impuls_43_04_UTU.Reset_horas | 192.168.4.43:4660 | 10:0X:340 | Read+Write | Always
MSA_UT_Ventil_impuls_43_04_UTU.Horas_funcionam | 192.168.4.43:4660 | 10:3X:628 | Read | Always
MSA_UT_Ventil_impuls_43_04_UTU.Estado | 192.168.4.43:4660 | 10:0X:204 | Read | Always
MSA_UT_Ventil_impuls_43_04_UTU.Orden | 192.168.4.43:4660 | 10:0X:268 | Read | Always
MSA_UT_Ventil_impuls_43_04_UTU.Fallo | 192.168.4.43:4660 | 10:0X:341 | Read | Always
MSA_UM_Extractor_VI_03.Horario_A | 192.168.4.53:4660 | 1:3X:805T80 | Read+Write | Always
MSA_UM_Extractor_VI_03.Horario_estado | 192.168.4.53:4660 | 1:0X:345 | Read | Always
MSA_UM_Extractor_VI_03.Manual_horario | 192.168.4.53:4660 | 1:0X:346 | Read+Write | Always
MSA_UM_Extractor_VI_03.Marcha_paro | 192.168.4.53:4660 | 1:0X:347 | Read+Write | Always
MSA_UM_Extractor_VI_03.Reset_horas | 192.168.4.53:4660 | 1:0X:348 | Read+Write | Always
MSA_UM_Extractor_VI_03.Horas_funcionam | 192.168.4.53:4660 | 1:3X:848 | Read | Always
MSA_UM_Extractor_VI_03.Estado | 192.168.4.53:4660 | 1:0X:237 | Read | Always
MSA_UM_Extractor_VI_03.Orden | 192.168.4.53:4660 | 1:0X:287 | Read | Always
MSA_UM_Extractor_VI_03.Fallo | 192.168.4.53:4660 | 1:0X:349 | Read | Always
MSA_UM_Extractor_VE_19.Horario_A | 192.168.4.53:4660 | 1:3X:761T80 | Read+Write | Always
MSA_UM_Extractor_VE_19.Horario_estado | 192.168.4.53:4660 | 1:0X:353 | Read | Always
MSA_UM_Extractor_VE_19.Manual_horario | 192.168.4.53:4660 | 1:0X:354 | Read+Write | Always
MSA_UM_Extractor_VE_19.Marcha_paro | 192.168.4.53:4660 | 1:0X:355 | Read+Write | Always
MSA_UM_Extractor_VE_19.Reset_horas | 192.168.4.53:4660 | 1:0X:356 | Read+Write | Always
MSA_UM_Extractor_VE_19.Horas_funcionam | 192.168.4.53:4660 | 1:3X:804 | Read | Always
MSA_UM_Extractor_VE_19.Estado | 192.168.4.53:4660 | 1:0X:238 | Read | Always
MSA_UM_Extractor_VE_19.Orden | 192.168.4.53:4660 | 1:0X:288 | Read | Always
MSA_UM_Extractor_VE_19.Fallo | 192.168.4.53:4660 | 1:0X:357 | Read | Always
MSA_UM_Extractor_VE_20.Horario_A | 192.168.4.53:4660 | 1:3X:717T80 | Read+Write | Always
MSA_UM_Extractor_VE_20.Horario_estado | 192.168.4.53:4660 | 1:0X:361 | Read | Always
MSA_UM_Extractor_VE_20.Manual_horario | 192.168.4.53:4660 | 1:0X:362 | Read+Write | Always
MSA_UM_Extractor_VE_20.Marcha_paro | 192.168.4.53:4660 | 1:0X:363 | Read+Write | Always
MSA_UM_Extractor_VE_20.Reset_horas | 192.168.4.53:4660 | 1:0X:364 | Read+Write | Always
MSA_UM_Extractor_VE_20.Horas_funcionam | 192.168.4.53:4660 | 1:3X:760 | Read | Always
MSA_UM_Extractor_VE_20.Estado | 192.168.4.53:4660 | 1:0X:239 | Read | Always
MSA_UM_Extractor_VE_20.Orden | 192.168.4.53:4660 | 1:0X:289 | Read | Always
MSA_UM_Extractor_VE_20.Fallo | 192.168.4.53:4660 | 1:0X:365 | Read | Always
MSA_UM_Extractor_Reserva_QM50.Horario_A | 192.168.4.53:4660 | 1:3X:673T80 | Read+Write | Always
MSA_UM_Extractor_Reserva_QM50.Horario_estado | 192.168.4.53:4660 | 1:0X:369 | Read | Always
MSA_UM_Extractor_Reserva_QM50.Manual_horario | 192.168.4.53:4660 | 1:0X:370 | Read+Write | Always
MSA_UM_Extractor_Reserva_QM50.Marcha_paro | 192.168.4.53:4660 | 1:0X:371 | Read+Write | Always
MSA_UM_Extractor_Reserva_QM50.Reset_horas | 192.168.4.53:4660 | 1:0X:372 | Read+Write | Always
MSA_UM_Extractor_Reserva_QM50.Horas_funcionam | 192.168.4.53:4660 | 1:3X:716 | Read | Always
MSA_UM_Extractor_Reserva_QM50.Estado | 192.168.4.53:4660 | 1:0X:240 | Read | Always
MSA_UM_Extractor_Reserva_QM50.Orden | 192.168.4.53:4660 | 1:0X:290 | Read | Always
MSA_UM_Extractor_Reserva_QM50.Fallo | 192.168.4.53:4660 | 1:0X:373 | Read | Always
MSA_UM_Extrac_Cuadros_clima.Horario_A | 192.168.4.53:4660 | 2:3X:321T80 | Read+Write | Always
MSA_UM_Extrac_Cuadros_clima.Horario_estado | 192.168.4.53:4660 | 2:0X:433 | Read | Always
MSA_UM_Extrac_Cuadros_clima.Manual_horario | 192.168.4.53:4660 | 2:0X:434 | Read+Write | Always
MSA_UM_Extrac_Cuadros_clima.Marcha_paro | 192.168.4.53:4660 | 2:0X:435 | Read+Write | Always
MSA_UM_Extrac_Cuadros_clima.Reset_horas | 192.168.4.53:4660 | 2:0X:436 | Read+Write | Always
MSA_UM_Extrac_Cuadros_clima.Horas_funcionam | 192.168.4.53:4660 | 2:3X:1024 | Read | Always
MSA_UM_Extrac_Cuadros_clima.Estado | 192.168.4.53:4660 | 2:0X:223 | Read | Always
MSA_UM_Extrac_Cuadros_clima.Orden | 192.168.4.53:4660 | 2:0X:281 | Read | Always
MSA_UM_Extrac_Cuadros_clima.Fallo | 192.168.4.53:4660 | 2:0X:437 | Read | Always
MSA_UM_Vent_Desenf_VPS1.Horario_estado | 192.168.4.53:4660 | 6:0X:337 | Read | Always
MSA_UM_Vent_Desenf_VPS1.Manual_horario | 192.168.4.53:4660 | 6:0X:338 | Read+Write | Always
MSA_UM_Vent_Desenf_VPS1.Marcha_paro | 192.168.4.53:4660 | 6:0X:339 | Read+Write | Always
MSA_UM_Vent_Desenf_VPS1.Reset_horas | 192.168.4.53:4660 | 6:0X:340 | Read+Write | Always
MSA_UM_Vent_Desenf_VPS1.Horas_funcionam | 192.168.4.53:4660 | 6:3X:584 | Read | Always
MSA_UM_Vent_Desenf_VPS1.Estado | 192.168.4.53:4660 | 6:0X:203 | Read | Always
MSA_UM_Vent_Desenf_VPS1.Orden | 192.168.4.53:4660 | 6:0X:267 | Read | Always
MSA_UM_Vent_Desenf_VPS1.Fallo | 192.168.4.53:4660 | 6:0X:341 | Read | Always
MSA_UM_Vent_Desenf_VPS2.Horario_A | 192.168.4.53:4660 | 6:3X:805T80 | Read+Write | Always
MSA_UM_Vent_Desenf_VPS2.Horario_estado | 192.168.4.53:4660 | 6:0X:345 | Read | Always
MSA_UM_Vent_Desenf_VPS2.Manual_horario | 192.168.4.53:4660 | 6:0X:346 | Read+Write | Always
MSA_UM_Vent_Desenf_VPS2.Marcha_paro | 192.168.4.53:4660 | 6:0X:347 | Read+Write | Always
MSA_UM_Vent_Desenf_VPS2.Reset_horas | 192.168.4.53:4660 | 6:0X:348 | Read+Write | Always
MSA_UM_Vent_Desenf_VPS2.Horas_funcionam | 192.168.4.53:4660 | 6:3X:540 | Read | Always
MSA_UM_Vent_Desenf_VPS2.Estado | 192.168.4.53:4660 | 6:0X:204 | Read | Always
MSA_UM_Vent_Desenf_VPS2.Orden | 192.168.4.53:4660 | 6:0X:268 | Read | Always
MSA_UM_Vent_Desenf_VPS2.Fallo | 192.168.4.53:4660 | 6:0X:349 | Read | Always
MSA_UM_Vent_Desenf_Reserva.Horario_A | 192.168.4.53:4660 | 6:3X:761T80 | Read+Write | Always
MSA_UM_Vent_Desenf_Reserva.Horario_estado | 192.168.4.53:4660 | 6:0X:353 | Read | Always
MSA_UM_Vent_Desenf_Reserva.Manual_horario | 192.168.4.53:4660 | 6:0X:354 | Read+Write | Always
MSA_UM_Vent_Desenf_Reserva.Marcha_paro | 192.168.4.53:4660 | 6:0X:355 | Read+Write | Always
MSA_UM_Vent_Desenf_Reserva.Reset_horas | 192.168.4.53:4660 | 6:0X:356 | Read+Write | Always
MSA_UM_Vent_Desenf_Reserva.Horas_funcionam | 192.168.4.53:4660 | 6:3X:496 | Read | Always
MSA_UM_Vent_Desenf_Reserva.Estado | 192.168.4.53:4660 | 6:0X:205 | Read | Always
MSA_UM_Vent_Desenf_Reserva.Orden | 192.168.4.53:4660 | 6:0X:269 | Read | Always
MSA_UM_Vent_Desenf_Reserva.Fallo | 192.168.4.53:4660 | 6:0X:357 | Read | Always
MSA_UM_Recup_Esp_Multifunc.Horario_A | 192.168.4.53:4660 | 6:3X:673T80 | Read+Write | Always
MSA_UM_Recup_Esp_Multifunc.Horario_estado | 192.168.4.53:4660 | 6:0X:369 | Read | Always
MSA_UM_Recup_Esp_Multifunc.Manual_horario | 192.168.4.53:4660 | 6:0X:370 | Read+Write | Always
MSA_UM_Recup_Esp_Multifunc.Marcha_paro | 192.168.4.53:4660 | 6:0X:371 | Read+Write | Always
MSA_UM_Recup_Esp_Multifunc.Reset_horas | 192.168.4.53:4660 | 6:0X:372 | Read+Write | Always
MSA_UM_Recup_Esp_Multifunc.Horas_funcionam | 192.168.4.53:4660 | 6:3X:936 | Read | Always
MSA_UM_Recup_Esp_Multifunc.Estado | 192.168.4.53:4660 | 6:0X:217 | Read | Always
MSA_UM_Recup_Esp_Multifunc.Orden | 192.168.4.53:4660 | 6:0X:273 | Read | Always
MSA_UM_Recup_Esp_Multifunc.Fallo | 192.168.4.53:4660 | 6:0X:373 | Read | Always
MSA_UM_Ventil_imp_VE_PS1.Horario_A | 192.168.4.53:4660 | 6:3X:585T80 | Read+Write | Always
MSA_UM_Ventil_imp_VE_PS1.Horario_estado | 192.168.4.53:4660 | 6:0X:385 | Read | Always
MSA_UM_Ventil_imp_VE_PS1.Manual_horario | 192.168.4.53:4660 | 6:0X:386 | Read+Write | Always
MSA_UM_Ventil_imp_VE_PS1.Marcha_paro | 192.168.4.53:4660 | 6:0X:387 | Read+Write | Always
MSA_UM_Ventil_imp_VE_PS1.Reset_horas | 192.168.4.53:4660 | 6:0X:388 | Read+Write | Always
MSA_UM_Ventil_imp_VE_PS1.Horas_funcionam | 192.168.4.53:4660 | 6:3X:848 | Read | Always
MSA_UM_Ventil_imp_VE_PS1.Estado | 192.168.4.53:4660 | 6:0X:219 | Read | Always
MSA_UM_Ventil_imp_VE_PS1.Orden | 192.168.4.53:4660 | 6:0X:275 | Read | Always
MSA_UM_Ventil_imp_VE_PS1.Fallo | 192.168.4.53:4660 | 6:0X:389 | Read | Always
MSA_UM_Extractor_VE_PS1.Horario_A | 192.168.4.53:4660 | 6:3X:541T80 | Read+Write | Always
MSA_UM_Extractor_VE_PS1.Horario_estado | 192.168.4.53:4660 | 6:0X:393 | Read | Always
MSA_UM_Extractor_VE_PS1.Manual_horario | 192.168.4.53:4660 | 6:0X:394 | Read+Write | Always
MSA_UM_Extractor_VE_PS1.Marcha_paro | 192.168.4.53:4660 | 6:0X:395 | Read+Write | Always
MSA_UM_Extractor_VE_PS1.Reset_horas | 192.168.4.53:4660 | 6:0X:396 | Read+Write | Always
MSA_UM_Extractor_VE_PS1.Horas_funcionam | 192.168.4.53:4660 | 6:3X:804 | Read | Always
MSA_UM_Extractor_VE_PS1.Estado | 192.168.4.53:4660 | 6:0X:220 | Read | Always
MSA_UM_Extractor_VE_PS1.Orden | 192.168.4.53:4660 | 6:0X:276 | Read | Always
MSA_UM_Extractor_VE_PS1.Fallo | 192.168.4.53:4660 | 6:0X:397 | Read | Always
MSA_UM_Extractor_Servicios.Horario_A | 192.168.4.53:4660 | 6:3X:497T80 | Read+Write | Always
MSA_UM_Extractor_Servicios.Horario_estado | 192.168.4.53:4660 | 6:0X:401 | Read | Always
MSA_UM_Extractor_Servicios.Manual_horario | 192.168.4.53:4660 | 6:0X:402 | Read+Write | Always
MSA_UM_Extractor_Servicios.Marcha_paro | 192.168.4.53:4660 | 6:0X:403 | Read+Write | Always
MSA_UM_Extractor_Servicios.Reset_horas | 192.168.4.53:4660 | 6:0X:404 | Read+Write | Always
MSA_UM_Extractor_Servicios.Horas_funcionam | 192.168.4.53:4660 | 6:3X:760 | Read | Always
MSA_UM_Extractor_Servicios.Estado | 192.168.4.53:4660 | 6:0X:221 | Read | Always
MSA_UM_Extractor_Servicios.Orden | 192.168.4.53:4660 | 6:0X:277 | Read | Always
MSA_UM_Extractor_Servicios.Fallo | 192.168.4.53:4660 | 6:0X:405 | Read | Always
MSA_UM_Extrac_Aseos_2.Horario_A | 192.168.4.53:4660 | 6:3X:409T80 | Read+Write | Always
MSA_UM_Extrac_Aseos_2.Horario_estado | 192.168.4.53:4660 | 6:0X:417 | Read | Always
MSA_UM_Extrac_Aseos_2.Manual_horario | 192.168.4.53:4660 | 6:0X:418 | Read+Write | Always
MSA_UM_Extrac_Aseos_2.Marcha_paro | 192.168.4.53:4660 | 6:0X:419 | Read+Write | Always
MSA_UM_Extrac_Aseos_2.Reset_horas | 192.168.4.53:4660 | 6:0X:420 | Read+Write | Always
MSA_UM_Extrac_Aseos_2.Horas_funcionam | 192.168.4.53:4660 | 6:3X:672 | Read | Always
MSA_UM_Extrac_Aseos_2.Estado | 192.168.4.53:4660 | 6:0X:223 | Read | Always
MSA_UM_Extrac_Aseos_2.Orden | 192.168.4.53:4660 | 6:0X:279 | Read | Always
MSA_UM_Extrac_Aseos_2.Fallo | 192.168.4.53:4660 | 6:0X:421 | Read | Always
MSA_UM_Extractor_53_01_UMM.Horario_A | 192.168.4.53:4660 | 9:3X:805T80 | Read+Write | Always
MSA_UM_Extractor_53_01_UMM.Horario_estado | 192.168.4.53:4660 | 9:0X:345 | Read | Always
MSA_UM_Extractor_53_01_UMM.Manual_horario | 192.168.4.53:4660 | 9:0X:346 | Read+Write | Always
MSA_UM_Extractor_53_01_UMM.Marcha_paro | 192.168.4.53:4660 | 9:0X:347 | Read+Write | Always
MSA_UM_Extractor_53_01_UMM.Reset_horas | 192.168.4.53:4660 | 9:0X:348 | Read+Write | Always
MSA_UM_Extractor_53_01_UMM.Horas_funcionam | 192.168.4.53:4660 | 9:3X:848 | Read | Always
MSA_UM_Extractor_53_01_UMM.Estado | 192.168.4.53:4660 | 9:0X:205 | Read | Always
MSA_UM_Extractor_53_01_UMM.Orden | 192.168.4.53:4660 | 9:0X:269 | Read | Always
MSA_UM_Extractor_53_01_UMM.Fallo | 192.168.4.53:4660 | 9:0X:349 | Read | Always
MSA_UM_Extractor_53_02_UMM.Horario_A | 192.168.4.53:4660 | 9:3X:761T80 | Read+Write | Always
MSA_UM_Extractor_53_02_UMM.Horario_estado | 192.168.4.53:4660 | 9:0X:353 | Read | Always
MSA_UM_Extractor_53_02_UMM.Manual_horario | 192.168.4.53:4660 | 9:0X:354 | Read+Write | Always
MSA_UM_Extractor_53_02_UMM.Marcha_paro | 192.168.4.53:4660 | 9:0X:355 | Read+Write | Always
MSA_UM_Extractor_53_02_UMM.Reset_horas | 192.168.4.53:4660 | 9:0X:356 | Read+Write | Always
MSA_UM_Extractor_53_02_UMM.Horas_funcionam | 192.168.4.53:4660 | 9:3X:804 | Read | Always
MSA_UM_Extractor_53_02_UMM.Estado | 192.168.4.53:4660 | 9:0X:206 | Read | Always
MSA_UM_Extractor_53_02_UMM.Orden | 192.168.4.53:4660 | 9:0X:270 | Read | Always
MSA_UM_Extractor_53_02_UMM.Fallo | 192.168.4.53:4660 | 9:0X:357 | Read | Always
MSA_UM_Ventil_impuls_53_01_UMU.Horario_A | 192.168.4.53:4660 | 9:3X:981T80 | Read+Write | Always
MSA_UM_Ventil_impuls_53_01_UMU.Horario_estado | 192.168.4.53:4660 | 9:0X:313 | Read | Always
MSA_UM_Ventil_impuls_53_01_UMU.Manual_horario | 192.168.4.53:4660 | 9:0X:314 | Read+Write | Always
MSA_UM_Ventil_impuls_53_01_UMU.Marcha_paro | 192.168.4.53:4660 | 9:0X:315 | Read+Write | Always
MSA_UM_Ventil_impuls_53_01_UMU.Reset_horas | 192.168.4.53:4660 | 9:0X:316 | Read+Write | Always
MSA_UM_Ventil_impuls_53_01_UMU.Horas_funcionam | 192.168.4.53:4660 | 9:3X:1024 | Read | Always
MSA_UM_Ventil_impuls_53_01_UMU.Estado | 192.168.4.53:4660 | 9:0X:201 | Read | Always
MSA_UM_Ventil_impuls_53_01_UMU.Orden | 192.168.4.53:4660 | 9:0X:265 | Read | Always
MSA_UM_Ventil_impuls_53_01_UMU.Fallo | 192.168.4.53:4660 | 9:0X:317 | Read | Always
MSA_UM_Ventil_impuls_53_02_UMU.Horario_A | 192.168.4.53:4660 | 9:3X:937T80 | Read+Write | Always
MSA_UM_Ventil_impuls_53_02_UMU.Horario_estado | 192.168.4.53:4660 | 9:0X:321 | Read | Always
MSA_UM_Ventil_impuls_53_02_UMU.Manual_horario | 192.168.4.53:4660 | 9:0X:322 | Read+Write | Always
MSA_UM_Ventil_impuls_53_02_UMU.Marcha_paro | 192.168.4.53:4660 | 9:0X:323 | Read+Write | Always
MSA_UM_Ventil_impuls_53_02_UMU.Reset_horas | 192.168.4.53:4660 | 9:0X:324 | Read+Write | Always
MSA_UM_Ventil_impuls_53_02_UMU.Horas_funcionam | 192.168.4.53:4660 | 9:3X:980 | Read | Always
MSA_UM_Ventil_impuls_53_02_UMU.Estado | 192.168.4.53:4660 | 9:0X:202 | Read | Always
MSA_UM_Ventil_impuls_53_02_UMU.Orden | 192.168.4.53:4660 | 9:0X:266 | Read | Always
MSA_UM_Ventil_impuls_53_02_UMU.Fallo | 192.168.4.53:4660 | 9:0X:325 | Read | Always
MSA_UM_Extractor_53_01_UMU.Horario_A | 192.168.4.53:4660 | 9:3X:893T80 | Read+Write | Always
MSA_UM_Extractor_53_01_UMU.Horario_estado | 192.168.4.53:4660 | 9:0X:329 | Read | Always
MSA_UM_Extractor_53_01_UMU.Manual_horario | 192.168.4.53:4660 | 9:0X:330 | Read+Write | Always
MSA_UM_Extractor_53_01_UMU.Marcha_paro | 192.168.4.53:4660 | 9:0X:331 | Read+Write | Always
MSA_UM_Extractor_53_01_UMU.Reset_horas | 192.168.4.53:4660 | 9:0X:332 | Read+Write | Always
MSA_UM_Extractor_53_01_UMU.Horas_funcionam | 192.168.4.53:4660 | 9:3X:936 | Read | Always
MSA_UM_Extractor_53_01_UMU.Estado | 192.168.4.53:4660 | 9:0X:203 | Read | Always
MSA_UM_Extractor_53_01_UMU.Orden | 192.168.4.53:4660 | 9:0X:267 | Read | Always
MSA_UM_Extractor_53_01_UMU.Fallo | 192.168.4.53:4660 | 9:0X:333 | Read | Always
MSA_UM_Extractor_53_02_UMU.Horario_A | 192.168.4.53:4660 | 9:3X:849T80 | Read+Write | Always
MSA_UM_Extractor_53_02_UMU.Horario_estado | 192.168.4.53:4660 | 9:0X:337 | Read | Always
MSA_UM_Extractor_53_02_UMU.Manual_horario | 192.168.4.53:4660 | 9:0X:338 | Read+Write | Always
MSA_UM_Extractor_53_02_UMU.Marcha_paro | 192.168.4.53:4660 | 9:0X:339 | Read+Write | Always
MSA_UM_Extractor_53_02_UMU.Reset_horas | 192.168.4.53:4660 | 9:0X:340 | Read+Write | Always
MSA_UM_Extractor_53_02_UMU.Horas_funcionam | 192.168.4.53:4660 | 9:3X:892 | Read | Always
MSA_UM_Extractor_53_02_UMU.Estado | 192.168.4.53:4660 | 9:0X:204 | Read | Always
MSA_UM_Extractor_53_02_UMU.Orden | 192.168.4.53:4660 | 9:0X:268 | Read | Always
MSA_UM_Extractor_53_02_UMU.Fallo | 192.168.4.53:4660 | 9:0X:341 | Read | Always
MSA_UM_Vent_Desenf_VPS1.Horario_A | 192.168.4.53:4660 | 6:3X:849T80 | Read+Write | Always
MSA_BM_Vent_Sobrepres_Romans_Escalera.Horario_A | 192.168.4.23:4660 | 1:3X:629T80 | Read+Write | Always
MSA_BM_Vent_Sobrepres_Romans_Escalera.Horario_estado | 192.168.4.23:4660 | 1:0X:377 | Read | Always
MSA_BM_Vent_Sobrepres_Romans_Escalera.Manual_horario | 192.168.4.23:4660 | 1:0X:378 | Read+Write | Always
MSA_BM_Vent_Sobrepres_Romans_Escalera.Marcha_paro | 192.168.4.23:4660 | 1:0X:379 | Read+Write | Always
MSA_BM_Vent_Sobrepres_Romans_Escalera.Reset_horas | 192.168.4.23:4660 | 1:0X:380 | Read+Write | Always
MSA_BM_Vent_Sobrepres_Romans_Escalera.Horas_funcionam | 192.168.4.23:4660 | 1:3X:672 | Read | Always
MSA_BM_Vent_Sobrepres_Romans_Escalera.Orden | 192.168.4.23:4660 | 1:0X:291 | Read | Always
MSA_BM_Vent_Sobrepres_Romans_Vestibulo.Horario_A | 192.168.4.23:4660 | 1:3X:585T80 | Read+Write | Always
MSA_BM_Vent_Sobrepres_Romans_Vestibulo.Horario_estado | 192.168.4.23:4660 | 1:0X:385 | Read | Always
MSA_BM_Vent_Sobrepres_Romans_Vestibulo.Manual_horario | 192.168.4.23:4660 | 1:0X:386 | Read+Write | Always
MSA_BM_Vent_Sobrepres_Romans_Vestibulo.Marcha_paro | 192.168.4.23:4660 | 1:0X:387 | Read+Write | Always
MSA_BM_Vent_Sobrepres_Romans_Vestibulo.Reset_horas | 192.168.4.23:4660 | 1:0X:388 | Read+Write | Always
MSA_BM_Vent_Sobrepres_Romans_Vestibulo.Horas_funcionam | 192.168.4.23:4660 | 1:3X:628 | Read | Always
MSA_BM_Vent_Sobrepres_Romans_Vestibulo.Orden | 192.168.4.23:4660 | 1:0X:292 | Read | Always
MSA_BM_Vent_Sobrepres_N1_ME_Escalera.Horario_A | 192.168.4.23:4660 | 5:3X:717T80 | Read+Write | Always
MSA_BM_Vent_Sobrepres_N1_ME_Escalera.Horario_estado | 192.168.4.23:4660 | 5:0X:361 | Read | Always
MSA_BM_Vent_Sobrepres_N1_ME_Escalera.Manual_horario | 192.168.4.23:4660 | 5:0X:362 | Read+Write | Always
MSA_BM_Vent_Sobrepres_N1_ME_Escalera.Marcha_paro | 192.168.4.23:4660 | 5:0X:363 | Read+Write | Always
MSA_BM_Vent_Sobrepres_N1_ME_Escalera.Reset_horas | 192.168.4.23:4660 | 5:0X:364 | Read+Write | Always
MSA_BM_Vent_Sobrepres_N1_ME_Escalera.Horas_funcionam | 192.168.4.23:4660 | 5:3X:496 | Read | Always
MSA_BM_Vent_Sobrepres_N1_ME_Escalera.Orden | 192.168.4.23:4660 | 5:0X:265 | Read | Always
MSA_BM_Vent_Sobrepres_N1_FV_Escalera.Horario_A | 192.168.4.23:4660 | 5:3X:674T80 | Read+Write | Always
MSA_BM_Vent_Sobrepres_N1_FV_Escalera.Horario_estado | 192.168.4.23:4660 | 5:0X:377 | Read | Always
MSA_BM_Vent_Sobrepres_N1_FV_Escalera.Manual_horario | 192.168.4.23:4660 | 5:0X:378 | Read+Write | Always
MSA_BM_Vent_Sobrepres_N1_FV_Escalera.Marcha_paro | 192.168.4.23:4660 | 5:0X:379 | Read+Write | Always
MSA_BM_Vent_Sobrepres_N1_FV_Escalera.Reset_horas | 192.168.4.23:4660 | 5:0X:380 | Read+Write | Always
MSA_BM_Vent_Sobrepres_N1_FV_Escalera.Horas_funcionam | 192.168.4.23:4660 | 5:3X:452 | Read | Always
MSA_BM_Vent_Sobrepres_N1_FV_Escalera.Orden | 192.168.4.23:4660 | 5:0X:266 | Read | Always
MSA_BM_Vent_Sobrepres_N1_MV_Escalera.Horario_A | 192.168.4.23:4660 | 5:3X:630T80 | Read+Write | Always
MSA_BM_Vent_Sobrepres_N1_MV_Escalera.Horario_estado | 192.168.4.23:4660 | 5:0X:385 | Read | Always
MSA_BM_Vent_Sobrepres_N1_MV_Escalera.Manual_horario | 192.168.4.23:4660 | 5:0X:386 | Read+Write | Always
MSA_BM_Vent_Sobrepres_N1_MV_Escalera.Marcha_paro | 192.168.4.23:4660 | 5:0X:387 | Read+Write | Always
MSA_BM_Vent_Sobrepres_N1_MV_Escalera.Reset_horas | 192.168.4.23:4660 | 5:0X:388 | Read+Write | Always
MSA_BM_Vent_Sobrepres_N1_MV_Escalera.Horas_funcionam | 192.168.4.23:4660 | 5:3X:408 | Read | Always
MSA_BM_Vent_Sobrepres_N1_MV_Escalera.Orden | 192.168.4.23:4660 | 5:0X:267 | Read | Always
MSA_BM_Vent_Sobrepres_N1_FE_Escalera.Horario_A | 192.168.4.23:4660 | 5:3X:585T80 | Read+Write | Always
MSA_BM_Vent_Sobrepres_N1_FE_Escalera.Horario_estado | 192.168.4.23:4660 | 5:0X:393 | Read | Always
MSA_BM_Vent_Sobrepres_N1_FE_Escalera.Manual_horario | 192.168.4.23:4660 | 5:0X:394 | Read+Write | Always
MSA_BM_Vent_Sobrepres_N1_FE_Escalera.Marcha_paro | 192.168.4.23:4660 | 5:0X:395 | Read+Write | Always
MSA_BM_Vent_Sobrepres_N1_FE_Escalera.Reset_horas | 192.168.4.23:4660 | 5:0X:396 | Read+Write | Always
MSA_BM_Vent_Sobrepres_N1_FE_Escalera.Horas_funcionam | 192.168.4.23:4660 | 5:3X:364 | Read | Always
MSA_BM_Vent_Sobrepres_N1_FE_Escalera.Orden | 192.168.4.23:4660 | 5:0X:268 | Read | Always
MSA_BT_Vent_Sobrepres_Esc_Central_N2.Horario_A | 192.168.4.33:4660 | 1:3X:629T80 | Read+Write | Always
MSA_BT_Vent_Sobrepres_Esc_Central_N2.Horario_estado | 192.168.4.33:4660 | 1:0X:377 | Read | Always
MSA_BT_Vent_Sobrepres_Esc_Central_N2.Manual_horario | 192.168.4.33:4660 | 1:0X:378 | Read+Write | Always
MSA_BT_Vent_Sobrepres_Esc_Central_N2.Marcha_paro | 192.168.4.33:4660 | 1:0X:379 | Read+Write | Always
MSA_BT_Vent_Sobrepres_Esc_Central_N2.Reset_horas | 192.168.4.33:4660 | 1:0X:380 | Read+Write | Always
MSA_BT_Vent_Sobrepres_Esc_Central_N2.Horas_funcionam | 192.168.4.33:4660 | 1:3X:672 | Read | Always
MSA_BT_Vent_Sobrepres_Esc_Central_N2.Orden | 192.168.4.33:4660 | 1:0X:293 | Read | Always
MSA_BT_Vent_Sobrepres_Esc_Central_N3.Horario_A | 192.168.4.33:4660 | 1:3X:585T80 | Read+Write | Always
MSA_BT_Vent_Sobrepres_Esc_Central_N3.Horario_estado | 192.168.4.33:4660 | 1:0X:385 | Read | Always
MSA_BT_Vent_Sobrepres_Esc_Central_N3.Manual_horario | 192.168.4.33:4660 | 1:0X:386 | Read+Write | Always
MSA_BT_Vent_Sobrepres_Esc_Central_N3.Marcha_paro | 192.168.4.33:4660 | 1:0X:387 | Read+Write | Always
MSA_BT_Vent_Sobrepres_Esc_Central_N3.Reset_horas | 192.168.4.33:4660 | 1:0X:388 | Read+Write | Always
MSA_BT_Vent_Sobrepres_Esc_Central_N3.Horas_funcionam | 192.168.4.33:4660 | 1:3X:628 | Read | Always
MSA_BT_Vent_Sobrepres_Esc_Central_N3.Orden | 192.168.4.33:4660 | 1:0X:294 | Read | Always
MSA_BT_Vent_Sobrepres_Escalera_N2_FE.Horario_A | 192.168.4.33:4660 | 6:3X:585T80 | Read+Write | Always
MSA_BT_Vent_Sobrepres_Escalera_N2_FE.Horario_estado | 192.168.4.33:4660 | 6:0X:385 | Read | Always
MSA_BT_Vent_Sobrepres_Escalera_N2_FE.Manual_horario | 192.168.4.33:4660 | 6:0X:386 | Read+Write | Always
MSA_BT_Vent_Sobrepres_Escalera_N2_FE.Marcha_paro | 192.168.4.33:4660 | 6:0X:387 | Read+Write | Always
MSA_BT_Vent_Sobrepres_Escalera_N2_FE.Reset_horas | 192.168.4.33:4660 | 6:0X:388 | Read+Write | Always
MSA_BT_Vent_Sobrepres_Escalera_N2_FE.Horas_funcionam | 192.168.4.33:4660 | 6:3X:408 | Read | Always
MSA_BT_Vent_Sobrepres_Escalera_N2_FE.Orden | 192.168.4.33:4660 | 6:0X:265 | Read | Always
MSA_BT_Vent_SobrepresEscalera_N2_FV.Horario_A | 192.168.4.33:4660 | 6:3X:629T80 | Read+Write | Always
MSA_BT_Vent_SobrepresEscalera_N2_FV.Horario_estado | 192.168.4.33:4660 | 6:0X:377 | Read | Always
MSA_BT_Vent_SobrepresEscalera_N2_FV.Manual_horario | 192.168.4.33:4660 | 6:0X:378 | Read+Write | Always
MSA_BT_Vent_SobrepresEscalera_N2_FV.Marcha_paro | 192.168.4.33:4660 | 6:0X:379 | Read+Write | Always
MSA_BT_Vent_SobrepresEscalera_N2_FV.Reset_horas | 192.168.4.33:4660 | 6:0X:380 | Read+Write | Always
MSA_BT_Vent_SobrepresEscalera_N2_FV.Horas_funcionam | 192.168.4.33:4660 | 6:3X:364 | Read | Always
MSA_BT_Vent_SobrepresEscalera_N2_FV.Orden | 192.168.4.33:4660 | 6:0X:266 | Read | Always
MSA_UT_Vent_Sobrepres_Escalera_N3_ME.Horario_A | 192.168.4.43:4660 | 6:3X:717T80 | Read+Write | Always
MSA_UT_Vent_Sobrepres_Escalera_N3_ME.Horario_estado | 192.168.4.43:4660 | 6:0X:361 | Read | Always
MSA_UT_Vent_Sobrepres_Escalera_N3_ME.Manual_horario | 192.168.4.43:4660 | 6:0X:362 | Read+Write | Always
MSA_UT_Vent_Sobrepres_Escalera_N3_ME.Marcha_paro | 192.168.4.43:4660 | 6:0X:363 | Read+Write | Always
MSA_UT_Vent_Sobrepres_Escalera_N3_ME.Reset_horas | 192.168.4.43:4660 | 6:0X:364 | Read+Write | Always
MSA_UT_Vent_Sobrepres_Escalera_N3_ME.Horas_funcionam | 192.168.4.43:4660 | 6:3X:496 | Read | Always
MSA_UT_Vent_Sobrepres_Escalera_N3_ME.Orden | 192.168.4.43:4660 | 6:0X:265 | Read | Always
MSA_UT_Vent_Sobrepres_Escalera_N3_FV.Horario_A | 192.168.4.43:4660 | 6:3X:673T80 | Read+Write | Always
MSA_UT_Vent_Sobrepres_Escalera_N3_FV.Horario_estado | 192.168.4.43:4660 | 6:0X:369 | Read | Always
MSA_UT_Vent_Sobrepres_Escalera_N3_FV.Manual_horario | 192.168.4.43:4660 | 6:0X:370 | Read+Write | Always
MSA_UT_Vent_Sobrepres_Escalera_N3_FV.Marcha_paro | 192.168.4.43:4660 | 6:0X:371 | Read+Write | Always
MSA_UT_Vent_Sobrepres_Escalera_N3_FV.Reset_horas | 192.168.4.43:4660 | 6:0X:372 | Read+Write | Always
MSA_UT_Vent_Sobrepres_Escalera_N3_FV.Horas_funcionam | 192.168.4.43:4660 | 6:3X:452 | Read | Always
MSA_UT_Vent_Sobrepres_Escalera_N3_FV.Orden | 192.168.4.43:4660 | 6:0X:266 | Read | Always
MSA_UT_Vent_Sobrepres_Escalera_N3_FE.Horario_A | 192.168.4.43:4660 | 6:3X:585T80 | Read+Write | Always
MSA_UT_Vent_Sobrepres_Escalera_N3_FE.Horario_estado | 192.168.4.43:4660 | 6:0X:385 | Read | Always
MSA_UT_Vent_Sobrepres_Escalera_N3_FE.Manual_horario | 192.168.4.43:4660 | 6:0X:386 | Read+Write | Always
MSA_UT_Vent_Sobrepres_Escalera_N3_FE.Marcha_paro | 192.168.4.43:4660 | 6:0X:387 | Read+Write | Always
MSA_UT_Vent_Sobrepres_Escalera_N3_FE.Reset_horas | 192.168.4.43:4660 | 6:0X:388 | Read+Write | Always
MSA_UT_Vent_Sobrepres_Escalera_N3_FE.Horas_funcionam | 192.168.4.43:4660 | 6:3X:408 | Read | Always
MSA_UT_Vent_Sobrepres_Escalera_N3_FE.Orden | 192.168.4.43:4660 | 6:0X:267 | Read | Always
MSA_UT_Vent_Sobrepres_Escalera_N3_MV.Horario_A | 192.168.4.43:4660 | 6:3X:629T80 | Read+Write | Always
MSA_UT_Vent_Sobrepres_Escalera_N3_MV.Horario_estado | 192.168.4.43:4660 | 6:0X:377 | Read | Always
MSA_UT_Vent_Sobrepres_Escalera_N3_MV.Manual_horario | 192.168.4.43:4660 | 6:0X:378 | Read+Write | Always
MSA_UT_Vent_Sobrepres_Escalera_N3_MV.Marcha_paro | 192.168.4.43:4660 | 6:0X:379 | Read+Write | Always
MSA_UT_Vent_Sobrepres_Escalera_N3_MV.Reset_horas | 192.168.4.43:4660 | 6:0X:380 | Read+Write | Always
MSA_UT_Vent_Sobrepres_Escalera_N3_MV.Horas_funcionam | 192.168.4.43:4660 | 6:3X:364 | Read | Always
MSA_UT_Vent_Sobrepres_Escalera_N3_MV.Orden | 192.168.4.43:4660 | 6:0X:268 | Read | Always
MSA_UM_Vent_Sobrepres_Escalera_Oficinas.Horario_A | 192.168.4.53:4660 | 5:3X:585T80 | Read+Write | Always
MSA_UM_Vent_Sobrepres_Escalera_Oficinas.Horario_estado | 192.168.4.53:4660 | 5:0X:385 | Read | Always
MSA_UM_Vent_Sobrepres_Escalera_Oficinas.Manual_horario | 192.168.4.53:4660 | 5:0X:386 | Read+Write | Always
MSA_UM_Vent_Sobrepres_Escalera_Oficinas.Marcha_paro | 192.168.4.53:4660 | 5:0X:387 | Read+Write | Always
MSA_UM_Vent_Sobrepres_Escalera_Oficinas.Reset_horas | 192.168.4.53:4660 | 5:0X:388 | Read+Write | Always
MSA_UM_Vent_Sobrepres_Escalera_Oficinas.Horas_funcionam | 192.168.4.53:4660 | 5:3X:452 | Read | Always
MSA_UM_Vent_Sobrepres_Escalera_Oficinas.Orden | 192.168.4.53:4660 | 5:0X:265 | Read | Always
MSA_UM_Vent_Sobrepres_Vestib_Oficinas.Horario_A | 192.168.4.53:4660 | 5:3X:541T80 | Read+Write | Always
MSA_UM_Vent_Sobrepres_Vestib_Oficinas.Horario_estado | 192.168.4.53:4660 | 5:0X:393 | Read | Always
MSA_UM_Vent_Sobrepres_Vestib_Oficinas.Manual_horario | 192.168.4.53:4660 | 5:0X:394 | Read+Write | Always
MSA_UM_Vent_Sobrepres_Vestib_Oficinas.Marcha_paro | 192.168.4.53:4660 | 5:0X:395 | Read+Write | Always
MSA_UM_Vent_Sobrepres_Vestib_Oficinas.Reset_horas | 192.168.4.53:4660 | 5:0X:396 | Read+Write | Always
MSA_UM_Vent_Sobrepres_Vestib_Oficinas.Horas_funcionam | 192.168.4.53:4660 | 5:3X:408 | Read | Always
MSA_UM_Vent_Sobrepres_Vestib_Oficinas.Orden | 192.168.4.53:4660 | 5:0X:266 | Read | Always
MSA_BM_Desenfumaje_VPS1_1.Horario_A | 192.168.4.23:4660 | 6:3X:893T80 | Read+Write | Always
MSA_BM_Desenfumaje_VPS1_1.Horario_estado | 192.168.4.23:4660 | 6:0X:329 | Read | Always
MSA_BM_Desenfumaje_VPS1_1.Manual_horario | 192.168.4.23:4660 | 6:0X:330 | Read+Write | Always
MSA_BM_Desenfumaje_VPS1_1.Marcha_paro | 192.168.4.23:4660 | 6:0X:331 | Read+Write | Always
MSA_BM_Desenfumaje_VPS1_1.Reset_horas | 192.168.4.23:4660 | 6:0X:332 | Read+Write | Always
MSA_BM_Desenfumaje_VPS1_1.Estado | 192.168.4.23:4660 | 6:0X:204 | Read | Always
MSA_BM_Desenfumaje_VPS1_1.Orden | 192.168.4.23:4660 | 6:0X:267 | Read | Always
MSA_BM_Desenfumaje_VPS1_1.Fallo | 192.168.4.23:4660 | 6:0X:333 | Read | Always
MSA_BM_Desenfumaje_VPS1_2.Horario_A | 192.168.4.23:4660 | 6:3X:849T80 | Read+Write | Always
MSA_BM_Desenfumaje_VPS1_2.Horario_estado | 192.168.4.23:4660 | 6:0X:337 | Read | Always
MSA_BM_Desenfumaje_VPS1_2.Manual_horario | 192.168.4.23:4660 | 6:0X:338 | Read+Write | Always
MSA_BM_Desenfumaje_VPS1_2.Marcha_paro | 192.168.4.23:4660 | 6:0X:339 | Read+Write | Always
MSA_BM_Desenfumaje_VPS1_2.Reset_horas | 192.168.4.23:4660 | 6:0X:340 | Read+Write | Always
MSA_BM_Desenfumaje_VPS1_2.Estado | 192.168.4.23:4660 | 6:0X:205 | Read | Always
MSA_BM_Desenfumaje_VPS1_2.Orden | 192.168.4.23:4660 | 6:0X:268 | Read | Always
MSA_BM_Desenfumaje_VPS1_2.Fallo | 192.168.4.23:4660 | 6:0X:341 | Read | Always
MSA_BT_Clima_vestuario_1.Horario_A | 192.168.4.33:4660 | 9:3X:981T80 | Read+Write | Always
MSA_BT_Clima_vestuario_1.Horario_estado | 192.168.4.33:4660 | 9:0X:313 | Read | Always
MSA_BT_Clima_vestuario_1.Manual_horario | 192.168.4.33:4660 | 9:0X:314 | Read+Write | Always
MSA_BT_Clima_vestuario_1.Marcha_paro | 192.168.4.33:4660 | 9:0X:315 | Read+Write | Always
MSA_BT_Clima_vestuario_1.Reset_horas | 192.168.4.33:4660 | 9:0X:316 | Read+Write | Always
MSA_BT_Clima_vestuario_1.Horas_funcionam | 192.168.4.33:4660 | 9:3X:1024 | Read | Always
MSA_BT_Clima_vestuario_1.Filtro_sucio_impulsion | 192.168.4.33:4660 | 9:0X:205 | Read | Always
MSA_BT_Clima_vestuario_1.Estado_vent_imp | 192.168.4.33:4660 | 9:0X:201 | Read | Always
MSA_BT_Clima_vestuario_1.Orden_vent_imp | 192.168.4.33:4660 | 9:0X:265 | Read | Always
MSA_BT_Clima_vestuario_1.Fallo_vent_imp | 192.168.4.33:4660 | 9:0X:317 | Read | Always
MSA_BT_Clima_vestuario_1.Estado_vent_ret | 192.168.4.33:4660 | 9:0X:202 | Read | Always
MSA_BT_Clima_vestuario_1.Orden_vent_ret | 192.168.4.33:4660 | 9:0X:266 | Read | Always
MSA_BT_Clima_vestuario_1.Fallo_vent_ret | 192.168.4.33:4660 | 9:0X:318 | Read | Always
MSA_BT_Clima_vestuario_1.Filtro_sucio_retorno | 192.168.4.33:4660 | 9:0X:217 | Read | Always
MSA_BT_Clima_vestuario_1.Filtro_sucio_recuperador | 192.168.4.33:4660 | 9:0X:219 | Read | Always
MSA_BT_Clima_vestuario_1.Presostato_ventil_impulsion | 192.168.4.33:4660 | 9:0X:221 | Read | Always
MSA_BT_Clima_vestuario_1.Presostato_ventil_retorno | 192.168.4.33:4660 | 9:0X:223 | Read | Always
MSA_BT_Clima_vestuario_2.Horario_A | 192.168.4.33:4660 | 9:3X:937T80 | Read+Write | Always
MSA_BT_Clima_vestuario_2.Horario_estado | 192.168.4.33:4660 | 9:0X:321 | Read | Always
MSA_BT_Clima_vestuario_2.Manual_horario | 192.168.4.33:4660 | 9:0X:322 | Read+Write | Always
MSA_BT_Clima_vestuario_2.Marcha_paro | 192.168.4.33:4660 | 9:0X:323 | Read+Write | Always
MSA_BT_Clima_vestuario_2.Reset_horas | 192.168.4.33:4660 | 9:0X:324 | Read+Write | Always
MSA_BT_Clima_vestuario_2.Horas_funcionam | 192.168.4.33:4660 | 9:3X:980 | Read | Always
MSA_BT_Clima_vestuario_2.Filtro_sucio_impulsion | 192.168.4.33:4660 | 9:0X:206 | Read | Always
MSA_BT_Clima_vestuario_2.Estado_vent_imp | 192.168.4.33:4660 | 9:0X:203 | Read | Always
MSA_BT_Clima_vestuario_2.Orden_vent_imp | 192.168.4.33:4660 | 9:0X:267 | Read | Always
MSA_BT_Clima_vestuario_2.Fallo_vent_imp | 192.168.4.33:4660 | 9:0X:325 | Read | Always
MSA_BT_Clima_vestuario_2.Estado_vent_ret | 192.168.4.33:4660 | 9:0X:204 | Read | Always
MSA_BT_Clima_vestuario_2.Orden_vent_ret | 192.168.4.33:4660 | 9:0X:268 | Read | Always
MSA_BT_Clima_vestuario_2.Fallo_vent_ret | 192.168.4.33:4660 | 9:0X:326 | Read | Always
MSA_BT_Clima_vestuario_2.Filtro_sucio_retorno | 192.168.4.33:4660 | 9:0X:218 | Read | Always
MSA_BT_Clima_vestuario_2.Filtro_sucio_recuperador | 192.168.4.33:4660 | 9:0X:220 | Read | Always
MSA_BT_Clima_vestuario_2.Presostato_ventil_impulsion | 192.168.4.33:4660 | 9:0X:222 | Read | Always
MSA_BT_Clima_vestuario_2.Presostato_ventil_retorno | 192.168.4.33:4660 | 9:0X:224 | Read | Always
MSA_BT_Clima_vestuario_1_Estado_recuperador | 192.168.4.33:4660 | 10:0X:230 | Read | Always
MSA_BT_Clima_vestuario_1_Orden_recuperador | 192.168.4.33:4660 | 10:0X:279 | Read+Write | Always
MSA_BT_Clima_vestuario_1_Fallo_recuperador | 192.168.4.33:4660 | 10:0X:409 | Read | Always
MSA_BT_Clima_vestuario_2_Estado_recuperador | 192.168.4.33:4660 | 10:0X:231 | Read | Always
MSA_BT_Clima_vestuario_2_Orden_recuperador | 192.168.4.33:4660 | 10:0X:280 | Read+Write | Always
MSA_BT_Clima_vestuario_2_Fallo_recuperador | 192.168.4.33:4660 | 10:0X:410 | Read | Always
MSA_BM_Cortina_Acceso_Testa.Alarma_protecc | 192.168.4.23:4660 | 2:0X:222 | Read | Always
MSA_BM_Cortina_Acceso_Testa.Estado_Selector_Pref_No_Pref | 192.168.4.23:4660 | 2:0X:223 | Read | Always
MSA_BM_Cortina_Acceso_Testa.Estado_contactor | 192.168.4.23:4660 | 2:0X:224 | Read | Always
MSA_BM_Cortina_Acceso_Lateral.Alarma_protecc | 192.168.4.23:4660 | 2:0X:225 | Read | Always
MSA_BM_Cortina_Acceso_Lateral.Estado_Selector_Pref_No_Pref | 192.168.4.23:4660 | 2:0X:226 | Read | Always
MSA_BM_Cortina_Acceso_Lateral.Estado_contactor | 192.168.4.23:4660 | 2:0X:227 | Read | Always
MSA_BM_Cortina_Acceso_calle.Alarma_protecc | 192.168.4.23:4660 | 2:0X:228 | Read | Always
MSA_BM_Cortina_Acceso_calle.Estado_Selector_Pref_No_Pref | 192.168.4.23:4660 | 2:0X:229 | Read | Always
MSA_BM_Cortina_Acceso_calle.Estado_contactor | 192.168.4.23:4660 | 2:0X:230 | Read | Always
MSA_BM_Cortina_Acceso_4.Alarma_protecc | 192.168.4.23:4660 | 2:0X:245 | Read | Always
MSA_BM_Cortina_Acceso_4.Estado_Selector_Pref_No_Pref | 192.168.4.23:4660 | 2:0X:246 | Read | Always
MSA_BM_Cortina_Acceso_4.Estado_contactor | 192.168.4.23:4660 | 2:0X:247 | Read | Always
MSA_BT_cortina_acceso_calle.Alarma_protecc | 192.168.4.33:4660 | 2:0X:228 | Read | Always
MSA_BT_cortina_acceso_calle.Estado_Selector_Pref_No_Pref | 192.168.4.33:4660 | 2:0X:229 | Read | Always
MSA_BT_cortina_acceso_calle.Estado_contactor | 192.168.4.33:4660 | 2:0X:230 | Read | Always
MSA_BT_cortina_acceso_lateral.Alarma_protecc | 192.168.4.33:4660 | 2:0X:225 | Read | Always
MSA_BT_cortina_acceso_lateral.Estado_Selector_Pref_No_Pref | 192.168.4.33:4660 | 2:0X:226 | Read | Always
MSA_BT_cortina_acceso_lateral.Estado_contactor | 192.168.4.33:4660 | 2:0X:227 | Read | Always
MSA_BT_cortina_acceso_testa.Alarma_protecc | 192.168.4.33:4660 | 2:0X:222 | Read | Always
MSA_BT_cortina_acceso_testa.Estado_Selector_Pref_No_Pref | 192.168.4.33:4660 | 2:0X:223 | Read | Always
MSA_BT_cortina_acceso_testa.Estado_contactor | 192.168.4.33:4660 | 2:0X:224 | Read | Always
MSA_UT_Cortina_Acceso_04.Alarma_protecc | 192.168.4.43:4660 | 1:0X:245 | Read | Always
MSA_UT_Cortina_Acceso_04.Estado_Selector_Pref_No_Pref | 192.168.4.43:4660 | 1:0X:246 | Read | Always
MSA_UT_Cortina_Acceso_04.Estado_contactor | 192.168.4.43:4660 | 1:0X:247 | Read | Always
MSA_UT_Cortina_acceso_testa.Alarma_protecc | 192.168.4.43:4660 | 3:0X:223 | Read | Always
MSA_UT_Cortina_acceso_testa.Estado_Selector_Pref_No_Pref | 192.168.4.43:4660 | 3:0X:224 | Read | Always
MSA_UT_Cortina_acceso_testa.Estado_contactor | 192.168.4.43:4660 | 3:0X:225 | Read | Always
MSA_UT_Cortina_puerta_lateral.Alarma_protecc | 192.168.4.43:4660 | 3:0X:226 | Read | Always
MSA_UT_Cortina_puerta_lateral.Estado_Selector_Pref_No_Pref | 192.168.4.43:4660 | 3:0X:227 | Read | Always
MSA_UT_Cortina_puerta_lateral.Estado_contactor | 192.168.4.43:4660 | 3:0X:228 | Read | Always
MSA_UT_Cortina_puerta_calle.Alarma_protecc | 192.168.4.43:4660 | 3:0X:229 | Read | Always
MSA_UT_Cortina_puerta_calle.Estado_Selector_Pref_No_Pref | 192.168.4.43:4660 | 3:0X:230 | Read | Always
MSA_UT_Cortina_puerta_calle.Estado_contactor | 192.168.4.43:4660 | 3:0X:231 | Read | Always
MSA_UM_Cortina_Acceso_4.Alarma_protecc | 192.168.4.53:4660 | 1:0X:245 | Read | Always
MSA_UM_Cortina_Acceso_4.Estado_Selector_Pref_No_Pref | 192.168.4.53:4660 | 1:0X:246 | Read | Always
MSA_UM_Cortina_Acceso_4.Estado_contactor | 192.168.4.53:4660 | 1:0X:247 | Read | Always
MSA_UM_Cortina_acceso_testa.Alarma_protecc | 192.168.4.53:4660 | 3:0X:221 | Read | Always
MSA_UM_Cortina_acceso_testa.Estado_Selector_Pref_No_Pref | 192.168.4.53:4660 | 3:0X:222 | Read | Always
MSA_UM_Cortina_acceso_testa.Estado_contactor | 192.168.4.53:4660 | 3:0X:223 | Read | Always
MSA_UM_Cortina_acceso_lateral.Alarma_protecc | 192.168.4.53:4660 | 3:0X:224 | Read | Always
MSA_UM_Cortina_acceso_lateral.Estado_Selector_Pref_No_Pref | 192.168.4.53:4660 | 3:0X:225 | Read | Always
MSA_UM_Cortina_acceso_lateral.Estado_contactor | 192.168.4.53:4660 | 3:0X:226 | Read | Always
MSA_UM_Cortina_Acceso_calle.Alarma_protecc | 192.168.4.53:4660 | 3:0X:227 | Read | Always
MSA_UM_Cortina_Acceso_calle.Estado_Selector_Pref_No_Pref | 192.168.4.53:4660 | 3:0X:228 | Read | Always
MSA_UM_Cortina_Acceso_calle.Estado_contactor | 192.168.4.53:4660 | 3:0X:229 | Read | Always
MSA_BT_Ventil_desenfumaje_VPS_1_02.Horario_A | 192.168.4.33:4660 | 7:3X:541T80 | Read+Write | Screen
MSA_BT_Ventil_desenfumaje_VPS_1_02.Horario_estado | 192.168.4.33:4660 | 7:0X:393 | Read | Screen
MSA_BT_Ventil_desenfumaje_VPS_1_02.Manual_horario | 192.168.4.33:4660 | 7:0X:394 | Read+Write | Screen
MSA_BT_Ventil_desenfumaje_VPS_1_03.Horario_A | 192.168.4.33:4660 | 7:3X:585T80 | Read+Write | Screen
MSA_BT_Ventil_desenfumaje_VPS_1_03.Horario_estado | 192.168.4.33:4660 | 7:0X:385 | Read | Screen
MSA_UT_Alumb_K_Reserva.Horario_A | 192.168.4.43:4660 | 6:3X:453T80 | Read+Write | Always
MSA_UT_Alumb_K_Reserva.Horario_estado | 192.168.4.43:4660 | 6:0X:409 | Read | Always
MSA_UT_Alumb_K_Reserva.Manual_horario | 192.168.4.43:4660 | 6:0X:410 | Read+Write | Always
MSA_UT_Alumb_K_Reserva.Marcha_paro | 192.168.4.43:4660 | 6:0X:411 | Read+Write | Always
MSA_UT_Alumb_K_Reserva.Orden | 192.168.4.43:4660 | 6:0X:285 | Read | Always
MSA_BT_Enchufes_Pergolas_QMC31.Horario_A | 192.168.4.33:4660 | 7:3X:629T80 | Read+Write | Always
MSA_BT_Enchufes_Pergolas_QMC31.Horario_estado | 192.168.4.33:4660 | 7:0X:377 | Read | Always
MSA_BT_Enchufes_Pergolas_QMC31.Manual_horario | 192.168.4.33:4660 | 7:0X:378 | Read+Write | Always
MSA_BT_Enchufes_Pergolas_QMC31.Marcha_paro | 192.168.4.33:4660 | 7:0X:379 | Read+Write | Always
MSA_BT_Enchufes_Pergolas_QMC31.Estado | 192.168.4.33:4660 | 7:0X:232 | Read | Always
MSA_BT_Enchufes_Pergolas_QMC31.Orden | 192.168.4.33:4660 | 7:0X:280 | Read | Always
MSA_BT_Enchufes_Pergolas_QMC31.Fallo | 192.168.4.33:4660 | 7:0X:381 | Read | Always
MSA_BM_Cambio_IV_Toberas_Mercat | 192.168.4.23:4660 | 2:0X:280 | Read+Write | Always
MSA_BT_Cambio_IV_Toberas_Mercat | 192.168.4.33:4660 | 1:0X:296 | Read+Write | Always
MSA_UT_Cambio_IV_Toberas_Mercat | 192.168.4.43:4660 | 1:0X:296 | Read+Write | Always
MSA_UM_Cambio_IV_Toberas_Mercat | 192.168.4.53:4660 | 1:0X:296 | Read+Write | Always
MSA_BM_Estado_Aliment_QM22 | 192.168.4.23:4660 | 1:0X:248 | Read | Always
MSA_BM_Estado_alumb_general | 192.168.4.23:4660 | 2:0X:231 | Read | Always
MSA_BM_Est_interrup_gral | 192.168.4.23:4660 | 3:0X:207 | Read | Always
MSA_BM_Est_alim_CE_Inferiores | 192.168.4.23:4660 | 3:0X:208 | Read | Always
MSA_BM_Ascensor_BM01_Est_proteccion | 192.168.4.23:4660 | 3:0X:217 | Read | Always
MSA_BM_Ascensor_BM02_Est_proteccion | 192.168.4.23:4660 | 3:0X:218 | Read | Always
MSA_BM_Montacargas_BM_01_Estado_proteccion | 192.168.4.23:4660 | 3:0X:219 | Read | Always
MSA_BM_Montacargas_BM_01_Estado_Pref_NoPref | 192.168.4.23:4660 | 3:0X:220 | Read | Always
MSA_BM_Montacargas_BM_01_Estado_contactor | 192.168.4.23:4660 | 3:0X:221 | Read | Always
MSA_BM_Montacargas_BM_02_Estado_proteccion | 192.168.4.23:4660 | 3:0X:222 | Read | Always
MSA_BM_Montacargas_BM_02_Estado_Pref_NoPref | 192.168.4.23:4660 | 3:0X:223 | Read | Always
MSA_BM_Montacargas_BM_02_Estado_contactor | 192.168.4.23:4660 | 3:0X:224 | Read | Always
MSA_BM_Escalera_Estado_1 | 192.168.4.23:4660 | 3:0X:225 | Read | Always
MSA_BM_Escalera_Estado_2 | 192.168.4.23:4660 | 3:0X:226 | Read | Always
MSA_BM_Clima_Estado_proteccion | 192.168.4.23:4660 | 3:0X:227 | Read | Always
MSA_BM_Clima_Estado_Pref_NoPref | 192.168.4.23:4660 | 3:0X:228 | Read | Always
MSA_BM_Clima_Estado_contactor | 192.168.4.23:4660 | 3:0X:229 | Read | Always
MSA_BM_Enchufes_Gral_Estado_proteccion | 192.168.4.23:4660 | 3:0X:230 | Read | Always
MSA_BM_Enchufes_Gral_Estado_Pref_NoPref | 192.168.4.23:4660 | 3:0X:231 | Read | Always
MSA_BM_Enchufes_Gral_Estado_contactor | 192.168.4.23:4660 | 3:0X:232 | Read | Always
MSA_BM_QM21_Estado_interruptor_gral | 192.168.4.23:4660 | 6:0X:201 | Read | Always
MSA_BM_Linea_eventos_Estado_proteccion | 192.168.4.23:4660 | 6:0X:206 | Read | Always
MSA_BM_Linea_eventos_Estado_Pref_NoPref | 192.168.4.23:4660 | 6:0X:207 | Read | Always
MSA_BM_Linea_eventos_Estado_contactor | 192.168.4.23:4660 | 6:0X:208 | Read | Always
MSA_BM_QM17_climatizacion_Estado_Pref_NoPref | 192.168.4.23:4660 | 6:0X:217 | Read | Always
MSA_BM_QM17_climatizacion_Estado_contactor | 192.168.4.23:4660 | 6:0X:218 | Read | Always
MSA_BM_QM17_Estado_proteccion | 192.168.4.23:4660 | 6:0X:229 | Read | Always
MSA_BM_QM17_Estado_Pref_NoPref | 192.168.4.23:4660 | 6:0X:230 | Read | Always
MSA_BM_QM17_Estado_contactor | 192.168.4.23:4660 | 6:0X:231 | Read | Always
MSA_BM_Climatizacion_Estado_proteccion | 192.168.4.23:4660 | 7:0X:203 | Read | Always
MSA_BM_Climatizacion_Estado_Pref_NoPref | 192.168.4.23:4660 | 7:0X:201 | Read | Always
MSA_BM_Climatizacion_Estado_contactor | 192.168.4.23:4660 | 7:0X:202 | Read | Always
MSA_BM_Estado_interr_general_QM22 | 192.168.4.23:4660 | 7:0X:204 | Read | Always
MSA_BM_Estado_interr_general_QM12 | 192.168.4.23:4660 | 7:0X:205 | Read | Always
MSA_BM_Estado_interr_general_QM17 | 192.168.4.23:4660 | 7:0X:206 | Read | Always
MSA_BM_clima_23_Estado_protecciones | 192.168.4.23:4660 | 8:0X:201 | Read | Always
MSA_BM_clima_23_Selector_Pref_No_pref | 192.168.4.23:4660 | 8:0X:202 | Read | Always
MSA_BM_clima_23_Estado_contactor | 192.168.4.23:4660 | 8:0X:203 | Read | Always
MSA_BM_Estado_int_gral_QM23 | 192.168.4.23:4660 | 8:0X:217 | Read | Always
MSA_BM_Estado_int_gral_QM231_Clima | 192.168.4.23:4660 | 8:0X:218 | Read | Always
MSA_BM_Estado_int_gral_QM231_Enchufes | 192.168.4.23:4660 | 8:0X:219 | Read | Always
MSA_BM_Estado_int_gral_Alumb | 192.168.4.23:4660 | 8:0X:228 | Read | Always
MSA_BM_Enchufes_Estado_protecciones | 192.168.4.23:4660 | 8:0X:229 | Read | Always
MSA_BM_Enchufes_Selector_Pref_No_pref | 192.168.4.23:4660 | 8:0X:230 | Read | Always
MSA_BM_Enchufes_Estado_contactor | 192.168.4.23:4660 | 8:0X:231 | Read | Always
MSA_BM_Tomas_Corriente_Estado_protecciones | 192.168.4.23:4660 | 9:0X:201 | Read | Always
MSA_BM_Tomas_Corriente_Selector_Pref_No_pref | 192.168.4.23:4660 | 9:0X:202 | Read | Always
MSA_BM_Tomas_Corriente_Estado_contactor | 192.168.4.23:4660 | 9:0X:203 | Read | Always
MSA_BM_Estado_interrup_QM24 | 192.168.4.23:4660 | 10:0X:201 | Read | Always
MSA_BM_Estado_interrup_QM11 | 192.168.4.23:4660 | 10:0X:202 | Read | Always
MSA_BT_Enchufes_servicios.Horario_A | 192.168.4.33:4660 | 7:3X:937T80 | Read+Write | Always
MSA_BT_Enchufes_servicios.Horario_estado | 192.168.4.33:4660 | 7:0X:321 | Read | Always
MSA_BT_Enchufes_servicios.Manual_horario | 192.168.4.33:4660 | 7:0X:322 | Read+Write | Always
MSA_BT_Enchufes_servicios.Marcha_paro | 192.168.4.33:4660 | 7:0X:323 | Read+Write | Always
MSA_BT_Enchufes_servicios_Reset_horas | 192.168.4.33:4660 | 7:0X:324 | Read+Write | Always
MSA_BT_Enchufes_servicios.Estado | 192.168.4.33:4660 | 7:0X:203 | Read | Always
MSA_BT_Enchufes_servicios.Orden | 192.168.4.33:4660 | 7:0X:266 | Read | Always
MSA_BT_Enchufes_servicios.Fallo | 192.168.4.33:4660 | 7:0X:325 | Read | Always
MSA_BT_Estado_interruptor_Gral | 192.168.4.33:4660 | 3:0X:207 | Read | Always
MSA_BT_Estado_cuadros_interiores | 192.168.4.33:4660 | 3:0X:208 | Read | Always
MSA_BT_Ascensor_101_Estado_protecciones | 192.168.4.33:4660 | 3:0X:217 | Read | Always
MSA_BT_Ascensor_102_Estado_protecciones | 192.168.4.33:4660 | 3:0X:218 | Read | Always
MSA_BT_Montacargas_01_1_Estado_proteccion | 192.168.4.33:4660 | 3:0X:219 | Read | Always
MSA_BT_Montacargas_01_1_Estado_Pref_NoPref | 192.168.4.33:4660 | 3:0X:220 | Read | Always
MSA_BT_Montacargas_01_1_Estado_contactor | 192.168.4.33:4660 | 3:0X:221 | Read | Always
MSA_BT_Montacargas_01_2_Estado_proteccion | 192.168.4.33:4660 | 3:0X:222 | Read | Always
MSA_BT_Montacargas_01_2_Estado_Pref_NoPref | 192.168.4.33:4660 | 3:0X:223 | Read | Always
MSA_BT_Montacargas_01_2_Estado_contactor | 192.168.4.33:4660 | 3:0X:224 | Read | Always
MSA_BT_Clima_30_Estado_proteccion | 192.168.4.33:4660 | 3:0X:225 | Read | Always
MSA_BT_Clima_30_Estado_Pref_NoPref | 192.168.4.33:4660 | 3:0X:226 | Read | Always
MSA_BT_Clima_30_Estado_contactor | 192.168.4.33:4660 | 3:0X:227 | Read | Always
MSA_BT_30_Enchufes_Estado_proteccion | 192.168.4.33:4660 | 3:0X:228 | Read | Always
MSA_BT_30_Enchufes_Estado_Pref_NoPref | 192.168.4.33:4660 | 3:0X:229 | Read | Always
MSA_BT_30_Enchufes_Estado_contactor | 192.168.4.33:4660 | 3:0X:230 | Read | Always
MSA_BT_Montacargas_01_3_Estado_proteccion | 192.168.4.33:4660 | 4:0X:201 | Read | Always
MSA_BT_Montacargas_01_3_Estado_Pref_NoPref | 192.168.4.33:4660 | 4:0X:202 | Read | Always
MSA_BT_Montacargas_01_3_Estado_contactor | 192.168.4.33:4660 | 4:0X:203 | Read | Always
MSA_BT_QM31_Estado_interr_gral | 192.168.4.33:4660 | 7:0X:201 | Read | Always
MSA_BT_Estado_lineas_concepto | 192.168.4.33:4660 | 7:0X:207 | Read | Always
MSA_BT_Clima_31_Estado_proteccion | 192.168.4.33:4660 | 7:0X:223 | Read | Always
MSA_BT_Clima_31_Estado_Pref_NoPref | 192.168.4.33:4660 | 7:0X:221 | Read | Always
MSA_BT_Clima_31_Estado_contactor | 192.168.4.33:4660 | 7:0X:222 | Read | Always
MSA_BT_Estado_linea_1 | 192.168.4.33:4660 | 7:0X:208 | Read | Always
MSA_BT_SAI_Estado_linea_2 | 192.168.4.33:4660 | 7:0X:224 | Read | Always
MSA_BT_SAI_Estado_Bypass | 192.168.4.33:4660 | 7:0X:225 | Read | Always
MSA_BT_SAI_Estado | 192.168.4.33:4660 | 7:0X:226 | Read | Always
MSA_BT_Estado_locales_tecnicos | 192.168.4.33:4660 | 7:0X:227 | Read | Always
MSA_BT_Estado_interr_linea_Concepte | 192.168.4.33:4660 | 7:0X:228 | Read | Always
MSA_BT_linea_eventos_Estado_proteccion | 192.168.4.33:4660 | 7:0X:229 | Read | Always
MSA_BT_linea_eventos_Estado_Pref_NoPref | 192.168.4.33:4660 | 7:0X:230 | Read | Always
MSA_BT_linea_eventos_Estado_contactor | 192.168.4.33:4660 | 7:0X:231 | Read | Always
MSA_BT_Estado_interr_general_Qm33 | 192.168.4.33:4660 | 10:0X:201 | Read | Always
MSA_BT_Clima_Estado_Protecc | 192.168.4.33:4660 | 10:0X:218 | Read | Always
MSA_BT_Clima_Pref_No_Pref | 192.168.4.33:4660 | 10:0X:219 | Read | Always
MSA_BT_Clima_Estado_contactor | 192.168.4.33:4660 | 10:0X:220 | Read | Always
MSA_BT_33_Enchufes_Estado_Protecc | 192.168.4.33:4660 | 10:0X:226 | Read | Always
MSA_BT_33_Enchufes_Pref_No_Pref | 192.168.4.33:4660 | 10:0X:227 | Read | Always
MSA_BT_33_Enchufes_Estado_contactor | 192.168.4.33:4660 | 10:0X:228 | Read | Always
MSA_BT_Estado_interr_general_Qm34 | 192.168.4.33:4660 | 10:0X:229 | Read | Always
MSA_UT_Estado_alimentacion_QM42 | 192.168.4.43:4660 | 1:0X:248 | Read | Always
MSA_UT_Estado_interrup_gral | 192.168.4.43:4660 | 2:0X:223 | Read | Always
MSA_UT_Estado_alim_cuadro_inferior | 192.168.4.43:4660 | 2:0X:224 | Read | Always
MSA_UT_ascensor_Estado_1 | 192.168.4.43:4660 | 2:0X:225 | Read | Always
MSA_UT_ascensor_Estado_2 | 192.168.4.43:4660 | 2:0X:226 | Read | Always
MSA_UT_montacargas_2_01_Estado_proteccion | 192.168.4.43:4660 | 2:0X:227 | Read | Always
MSA_UT_montacargas_2_01_Estado_Pref_NoPref | 192.168.4.43:4660 | 2:0X:228 | Read | Always
MSA_UT_montacargas_2_01_Estado_contactor | 192.168.4.43:4660 | 2:0X:229 | Read | Always
MSA_UT_montacargas_2_02_Estado_proteccion | 192.168.4.43:4660 | 2:0X:230 | Read | Always
MSA_UT_montacargas_2_02_Estado_Pref_NoPref | 192.168.4.43:4660 | 2:0X:231 | Read | Always
MSA_UT_montacargas_2_02_Estado_contactor | 192.168.4.43:4660 | 2:0X:232 | Read | Always
MSA_UT_Estado_escalera_1 | 192.168.4.43:4660 | 3:0X:207 | Read | Always
MSA_UT_Estado_escalera_2 | 192.168.4.43:4660 | 3:0X:208 | Read | Always
MSA_UT_montacargas_03_1_Estado_proteccion | 192.168.4.43:4660 | 3:0X:217 | Read | Always
MSA_UT_montacargas_03_1_Estado_Pref_NoPref | 192.168.4.43:4660 | 3:0X:218 | Read | Always
MSA_UT_montacargas_03_1_Estado_contactor | 192.168.4.43:4660 | 3:0X:219 | Read | Always
MSA_UT_montacargas_03_2_Estado_proteccion | 192.168.4.43:4660 | 3:0X:220 | Read | Always
MSA_UT_montacargas_03_2_Estado_Pref_NoPref | 192.168.4.43:4660 | 3:0X:221 | Read | Always
MSA_UT_montacargas_03_2_Estado_contactor | 192.168.4.43:4660 | 3:0X:222 | Read | Always
MSA_UT_Clima_40_Estado_proteccion | 192.168.4.43:4660 | 4:0X:205 | Read | Always
MSA_UT_Clima_40_Estado_Pref_NoPref | 192.168.4.43:4660 | 4:0X:206 | Read | Always
MSA_UT_Clima_40_Estado_contactor | 192.168.4.43:4660 | 4:0X:207 | Read | Always
MSA_UT_Estado_interr_gral_QM41 | 192.168.4.43:4660 | 7:0X:207 | Read | Always
MSA_UT_Estado_interr_gral_QM42 | 192.168.4.43:4660 | 7:0X:208 | Read | Always
MSA_UT_linea_eventos_Estado_proteccion | 192.168.4.43:4660 | 7:0X:225 | Read | Always
MSA_UT_linea_eventos_Estado_Pref_NoPref | 192.168.4.43:4660 | 7:0X:226 | Read | Always
MSA_UT_linea_eventos_Estado_contactor | 192.168.4.43:4660 | 7:0X:227 | Read | Always
MSA_UT_clima_41_Estado_Pref_NoPref | 192.168.4.43:4660 | 7:0X:228 | Read | Always
MSA_UT_clima_41_Estado_contactor | 192.168.4.43:4660 | 7:0X:229 | Read | Always
MSA_UT_clima_41_Estado_contactor | 192.168.4.43:4660 | 7:0X:230 | Read | Always
MSA_UT_Estado_int_gral_Sub_principal | 192.168.4.43:4660 | 7:0X:231 | Read | Always
MSA_UT_Estado_int_gral_Sub_complem | 192.168.4.43:4660 | 7:0X:232 | Read | Always
MSA_UT_41_Climatizacion_Estado_1 | 192.168.4.43:4660 | 8:0X:207 | Read | Always
MSA_UT_41_Climatizacion_Estado_2 | 192.168.4.43:4660 | 8:0X:208 | Read | Always
MSA_UT_Estado_interr_general_QM43 | 192.168.4.43:4660 | 10:0X:207 | Read | Always
MSA_UT_43_Climatizacion_Estado_proteccion | 192.168.4.43:4660 | 11:0X:203 | Read | Always
MSA_UT_43_Climatizacion_Estado_Pref_NoPref | 192.168.4.43:4660 | 11:0X:204 | Read | Always
MSA_UT_43_Climatizacion_Estado_contactor | 192.168.4.43:4660 | 11:0X:205 | Read | Always
MSA_UT_43_Enchufes_Estado_proteccion | 192.168.4.43:4660 | 11:0X:206 | Read | Always
MSA_UT_43_Enchufes_Estado_Pref_NoPref | 192.168.4.43:4660 | 11:0X:207 | Read | Always
MSA_UT_43_Enchufes_Estado_contactor | 192.168.4.43:4660 | 11:0X:208 | Read | Always
MSA_UM_Estado_Aliment_QM22 | 192.168.4.53:4660 | 1:0X:248 | Read | Always
MSA_UM_50_climatizacion_Estado_proteccion | 192.168.4.53:4660 | 2:0X:224 | Read | Always
MSA_UM_50_climatizacion_Estado_Pref_NoPref | 192.168.4.53:4660 | 2:0X:225 | Read | Always
MSA_UM_50_climatizacion_Estado_contactor | 192.168.4.53:4660 | 2:0X:226 | Read | Always
MSA_UM_Estado_Alumb_general | 192.168.4.53:4660 | 2:0X:227 | Read | Always
MSA_UM_Estado_int_general | 192.168.4.53:4660 | 3:0X:207 | Read | Always
MSA_UM_Estado_alim_cuadros_inf | 192.168.4.53:4660 | 3:0X:208 | Read | Always
MSA_UM_montacargas_Estado_proteccion | 192.168.4.53:4660 | 3:0X:217 | Read | Always
MSA_UM_montacargas_Estado_Pref_NoPref | 192.168.4.53:4660 | 3:0X:218 | Read | Always
MSA_UM_montacargas_Estado_contactor | 192.168.4.53:4660 | 3:0X:219 | Read | Always
MSA_UM_ascensor_Estado_UM_01 | 192.168.4.53:4660 | 3:0X:220 | Read | Always
MSA_UM_50_Enchufes_Estado_proteccion | 192.168.4.53:4660 | 3:0X:230 | Read | Always
MSA_UM_50_Enchufes_Estado_Pref_NoPref | 192.168.4.53:4660 | 3:0X:231 | Read | Always
MSA_UM_50_Enchufes_Estado_contactor | 192.168.4.53:4660 | 3:0X:232 | Read | Always
MSA_UM_Estado_linea_eventos_Estado_proteccion | 192.168.4.53:4660 | 6:0X:225 | Read | Always
MSA_UM_Estado_linea_eventos_Estado_Pref_NoPref | 192.168.4.53:4660 | 6:0X:226 | Read | Always
MSA_UM_Estado_linea_eventos_Estado_contactor | 192.168.4.53:4660 | 6:0X:227 | Read | Always
MSA_UM_51_Espais_us_Multifuncional_Estado_proteccion | 192.168.4.53:4660 | 6:0X:233 | Read | Always
MSA_UM_51_Espais_us_Multifuncional_Estado_Pref_NoPref | 192.168.4.53:4660 | 6:0X:234 | Read | Always
MSA_UM_51_Espais_us_Multifuncional_Estado_contactor | 192.168.4.53:4660 | 6:0X:235 | Read | Always
MSA_UT_Estado_int_gral_alumb_QM14 | 192.168.4.53:4660 | 7:0X:204 | Read | Always
MSA_UT_Circ_Clima_general_QM14_Estado_proteccion | 192.168.4.53:4660 | 7:0X:205 | Read | Always
MSA_UT_Circ_Clima_general_QM14_Estado_Pref_NoPref | 192.168.4.53:4660 | 7:0X:206 | Read | Always
MSA_UT_Circ_Clima_general_QM14_Estado_contactor | 192.168.4.53:4660 | 7:0X:207 | Read | Always
MSA_UT_Estado_int_gral_clima_QM14 | 192.168.4.53:4660 | 7:0X:208 | Read | Always
MSA_UT_Circ_Tomas_Corriente_QM14_Estado_proteccion | 192.168.4.53:4660 | 7:0X:217 | Read | Always
MSA_UT_Circ_Tomas_Corriente_QM14_Estado_Pref_NoPref | 192.168.4.53:4660 | 7:0X:218 | Read | Always
MSA_UT_Circ_Tomas_Corriente_QM14_Estado_contactor | 192.168.4.53:4660 | 7:0X:219 | Read | Always
MSA_UT_Est_int_gral_alumb_Emerg | 192.168.4.53:4660 | 7:0X:220 | Read | Always
MSA_UT_Estado_int_gral_clima_QM15 | 192.168.4.53:4660 | 7:0X:221 | Read | Always
MSA_UT_Circ_Clima_general_QM15_Estado_proteccion | 192.168.4.53:4660 | 7:0X:222 | Read | Always
MSA_UT_Circ_Clima_general_QM15_Estado_Pref_NoPref | 192.168.4.53:4660 | 7:0X:223 | Read | Always
MSA_UT_Circ_Clima_general_QM15_Estado_contactor | 192.168.4.53:4660 | 7:0X:224 | Read | Always
MSA_UT_Circ_Tomas_Corriente_QM15_Estado_proteccion | 192.168.4.53:4660 | 7:0X:225 | Read | Always
MSA_UT_Circ_Tomas_Corriente_QM15_Estado_Pref_NoPref | 192.168.4.53:4660 | 7:0X:226 | Read | Always
MSA_UT_Circ_Tomas_Corriente_QM15_Estado_contactor | 192.168.4.53:4660 | 7:0X:227 | Read | Always
MSA_UT_Estado_int_gral_alumb_zona_QM15 | 192.168.4.53:4660 | 7:0X:228 | Read | Always
MSA_UT_Estado_int_gral_enchufes_QM14 | 192.168.4.53:4660 | 7:0X:229 | Read | Always
MSA_UT_Estado_int_gral_enchufes_QM15 | 192.168.4.53:4660 | 7:0X:230 | Read | Always
MSA_UT_Estado_lineas_Generales_QM53 | 192.168.4.53:4660 | 9:0X:207 | Read | Always
MSA_UT_Estado_Linea_concepto | 192.168.4.53:4660 | 9:0X:208 | Read | Always
MSA_UM_Climatizacion_Estado_proteccion | 192.168.4.53:4660 | 11:0X:202 | Read | Always
MSA_UM_Climatizacion_Estado_Pref_NoPref | 192.168.4.53:4660 | 11:0X:203 | Read | Always
MSA_UM_Climatizacion_Estado_contactor | 192.168.4.53:4660 | 11:0X:204 | Read | Always
MSA_UM_Enchufes_Estado_proteccion | 192.168.4.53:4660 | 11:0X:205 | Read | Always
MSA_UM_Enchufes_Estado_Pref_NoPref | 192.168.4.53:4660 | 11:0X:206 | Read | Always
MSA_UM_Enchufes_Estado_contactor | 192.168.4.53:4660 | 11:0X:207 | Read | Always
MSA_UT_Enchufes_40_Estado_proteccion | 192.168.4.43:4660 | 4:0X:202 | Read+Write | Always
MSA_UT_Enchufes_40_Estado_Pref_NoPref | 192.168.4.43:4660 | 4:0X:203 | Read+Write | Always
MSA_UT_Enchufes_40_Estado_contactor | 192.168.4.43:4660 | 4:0X:204 | Read+Write | Always
MSA_UT_clima_41_Estado_proteccion | 192.168.4.43:4660 | 7:0X:230 | Read+Write | Always
MSA_UT_41_Climatizacion_Estado_3 | 192.168.4.43:4660 | 8:0X:217 | Read+Write | Always
BM_Temperatura_display_escritura | 192.168.4.27:4660 | 10:4X:1SX | Write | Always | 10000000
BM_HR_display_escritura | 192.168.4.27:4660 | 10:4X:2SX | Write | Always | 10000000
ZC1_Temperatura_display_escritura | 192.168.4.27:4660 | 20:4X:1SX | Write | Always | 10000000
ZC1_HR_display_escritura | 192.168.4.27:4660 | 20:4X:2SX | Write | Always | 10000000
BT_Temperatura_display_escritura | 192.168.4.37:4660 | 10:4X:1SX | Write | Always | 10000000
BT_HR_display_escritura | 192.168.4.37:4660 | 10:4X:2SX | Write | Always | 10000000
UT_Temperatura_display_escritura | 192.168.4.47:4660 | 10:4X:1SX | Write | Always | 10000000
UT_HR_display_escritura | 192.168.4.47:4660 | 10:4X:2SX | Write | Always | 10000000
ZC2_Temperatura_display_escritura | 192.168.4.47:4660 | 20:4X:1SX | Write | Always | 10000000
ZC2_HR_display_escritura | 192.168.4.47:4660 | 20:4X:2SX | Write | Always | 10000000
UM_Temperatura_display_escritura | 192.168.4.57:4660 | 10:4X:1SX | Write | Always | 10000000
UM_HR_display_escritura | 192.168.4.57:4660 | 10:4X:2SX | Write | Always | 10000000
MSA_Analizador_QM11_General_normal.Tension_Fase_1_N | 192.168.4.22:4660 | 3:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM11_General_normal.Tension_Fase_2_N | 192.168.4.22:4660 | 3:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM11_General_normal.Tension_Fase_3_N | 192.168.4.22:4660 | 3:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM11_General_normal.Intensidad_Fase_1 | 192.168.4.22:4660 | 3:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM11_General_normal.Intensidad_Fase_2 | 192.168.4.22:4660 | 3:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM11_General_normal.Intensidad_Fase_3 | 192.168.4.22:4660 | 3:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM11_General_normal.Intensidad_Neutro | 192.168.4.22:4660 | 3:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM11_General_normal.Potencia_activa_Fase_1 | 192.168.4.22:4660 | 3:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM11_General_normal.Potencia_activa_Fase_2 | 192.168.4.22:4660 | 3:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM11_General_normal.Potencia_activa_Fase_3 | 192.168.4.22:4660 | 3:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM11_General_normal.Potencia_reactiva_Fase_1 | 192.168.4.22:4660 | 3:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM11_General_normal.Potencia_reactiva_Fase_2 | 192.168.4.22:4660 | 3:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM11_General_normal.Potencia_reactiva_Fase_3 | 192.168.4.22:4660 | 3:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM11_General_normal.Frecuencia | 192.168.4.22:4660 | 3:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM11_General_normal.Energia_activa | 192.168.4.22:4660 | 3:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM11_General_normal.Energia_reactiva_inductiva | 192.168.4.22:4660 | 3:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM11_General_normal.Energia_reactiva_capacitiva | 192.168.4.22:4660 | 3:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM11_General_normal.Energia_aparente | 192.168.4.22:4660 | 3:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM11_General_normal.Potencia_activa_trifasica | 192.168.4.22:4660 | 3:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM11_General_normal.Potencia_inductiva_trifasica | 192.168.4.22:4660 | 3:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM11_General_normal.Potencia_capacitiva_trif | 192.168.4.22:4660 | 3:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM11_General_normal.cos_fi_trifasico | 192.168.4.22:4660 | 3:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM11_General_normal.Factor_de_potencia_trif | 192.168.4.22:4660 | 3:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM11_General_normal.Potencia_Aparente | 192.168.4.22:4660 | 3:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM11_General_normal.THD_V_Fase_1 | 192.168.4.22:4660 | 3:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM11_General_normal.THD_V_Fase_2 | 192.168.4.22:4660 | 3:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM11_General_normal.THD_V_Fase_3 | 192.168.4.22:4660 | 3:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM11_General_normal.THD_A_Fase_1 | 192.168.4.22:4660 | 3:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM11_General_normal.THD_A_Fase_2 | 192.168.4.22:4660 | 3:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM11_General_normal.THD_A_Fase_3 | 192.168.4.22:4660 | 3:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM11_General_normal.Tension_Fase_1_2 | 192.168.4.22:4660 | 3:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM11_General_normal.Tension_Fase_2_3 | 192.168.4.22:4660 | 3:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM11_General_normal.Tension_Fase_3_1 | 192.168.4.22:4660 | 3:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM24_General_normal.Tension_Fase_1_N | 192.168.4.22:4660 | 24:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM24_General_normal.Tension_Fase_2_N | 192.168.4.22:4660 | 24:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM24_General_normal.Tension_Fase_3_N | 192.168.4.22:4660 | 24:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM24_General_normal.Intensidad_Fase_1 | 192.168.4.22:4660 | 24:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM24_General_normal.Intensidad_Fase_2 | 192.168.4.22:4660 | 24:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM24_General_normal.Intensidad_Fase_3 | 192.168.4.22:4660 | 24:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM24_General_normal.Intensidad_Neutro | 192.168.4.22:4660 | 24:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM24_General_normal.Potencia_activa_Fase_1 | 192.168.4.22:4660 | 24:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM24_General_normal.Potencia_activa_Fase_2 | 192.168.4.22:4660 | 24:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM24_General_normal.Potencia_activa_Fase_3 | 192.168.4.22:4660 | 24:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM24_General_normal.Potencia_reactiva_Fase_1 | 192.168.4.22:4660 | 24:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM24_General_normal.Potencia_reactiva_Fase_2 | 192.168.4.22:4660 | 24:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM24_General_normal.Potencia_reactiva_Fase_3 | 192.168.4.22:4660 | 24:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM24_General_normal.Frecuencia | 192.168.4.22:4660 | 24:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM24_General_normal.Energia_activa | 192.168.4.22:4660 | 24:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM24_General_normal.Energia_reactiva_inductiva | 192.168.4.22:4660 | 24:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM24_General_normal.Energia_reactiva_capacitiva | 192.168.4.22:4660 | 24:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM24_General_normal.Energia_aparente | 192.168.4.22:4660 | 24:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM24_General_normal.Potencia_activa_trifasica | 192.168.4.22:4660 | 24:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM24_General_normal.Potencia_inductiva_trifasica | 192.168.4.22:4660 | 24:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM24_General_normal.Potencia_capacitiva_trif | 192.168.4.22:4660 | 24:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM24_General_normal.cos_fi_trifasico | 192.168.4.22:4660 | 24:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM24_General_normal.Factor_de_potencia_trif | 192.168.4.22:4660 | 24:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM24_General_normal.Potencia_Aparente | 192.168.4.22:4660 | 24:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM24_General_normal.THD_V_Fase_1 | 192.168.4.22:4660 | 24:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM24_General_normal.THD_V_Fase_2 | 192.168.4.22:4660 | 24:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM24_General_normal.THD_V_Fase_3 | 192.168.4.22:4660 | 24:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM24_General_normal.THD_A_Fase_1 | 192.168.4.22:4660 | 24:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM24_General_normal.THD_A_Fase_2 | 192.168.4.22:4660 | 24:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM24_General_normal.THD_A_Fase_3 | 192.168.4.22:4660 | 24:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM24_General_normal.Tension_Fase_1_2 | 192.168.4.22:4660 | 24:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM24_General_normal.Tension_Fase_2_3 | 192.168.4.22:4660 | 24:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM24_General_normal.Tension_Fase_3_1 | 192.168.4.22:4660 | 24:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM231_General_normal.Tension_Fase_1_N | 192.168.4.22:4660 | 52:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM231_General_normal.Tension_Fase_2_N | 192.168.4.22:4660 | 52:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM231_General_normal.Tension_Fase_3_N | 192.168.4.22:4660 | 52:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM231_General_normal.Intensidad_Fase_1 | 192.168.4.22:4660 | 52:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM231_General_normal.Intensidad_Fase_2 | 192.168.4.22:4660 | 52:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM231_General_normal.Intensidad_Fase_3 | 192.168.4.22:4660 | 52:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM231_General_normal.Intensidad_Neutro | 192.168.4.22:4660 | 52:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM231_General_normal.Potencia_activa_Fase_1 | 192.168.4.22:4660 | 52:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM231_General_normal.Potencia_activa_Fase_2 | 192.168.4.22:4660 | 52:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM231_General_normal.Potencia_activa_Fase_3 | 192.168.4.22:4660 | 52:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM231_General_normal.Potencia_reactiva_Fase_1 | 192.168.4.22:4660 | 52:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM231_General_normal.Potencia_reactiva_Fase_2 | 192.168.4.22:4660 | 52:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM231_General_normal.Potencia_reactiva_Fase_3 | 192.168.4.22:4660 | 52:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM231_General_normal.Frecuencia | 192.168.4.22:4660 | 52:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM231_General_normal.Energia_activa | 192.168.4.22:4660 | 52:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM231_General_normal.Energia_reactiva_inductiva | 192.168.4.22:4660 | 52:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM231_General_normal.Energia_reactiva_capacitiva | 192.168.4.22:4660 | 52:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM231_General_normal.Energia_aparente | 192.168.4.22:4660 | 52:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM231_General_normal.Potencia_activa_trifasica | 192.168.4.22:4660 | 52:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM231_General_normal.Potencia_inductiva_trifasica | 192.168.4.22:4660 | 52:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM231_General_normal.Potencia_capacitiva_trif | 192.168.4.22:4660 | 52:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM231_General_normal.cos_fi_trifasico | 192.168.4.22:4660 | 52:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM231_General_normal.Factor_de_potencia_trif | 192.168.4.22:4660 | 52:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM231_General_normal.Potencia_Aparente | 192.168.4.22:4660 | 52:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM231_General_normal.THD_V_Fase_1 | 192.168.4.22:4660 | 52:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM231_General_normal.THD_V_Fase_2 | 192.168.4.22:4660 | 52:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM231_General_normal.THD_V_Fase_3 | 192.168.4.22:4660 | 52:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM231_General_normal.THD_A_Fase_1 | 192.168.4.22:4660 | 52:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM231_General_normal.THD_A_Fase_2 | 192.168.4.22:4660 | 52:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM231_General_normal.THD_A_Fase_3 | 192.168.4.22:4660 | 52:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM231_General_normal.Tension_Fase_1_2 | 192.168.4.22:4660 | 52:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM231_General_normal.Tension_Fase_2_3 | 192.168.4.22:4660 | 52:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM231_General_normal.Tension_Fase_3_1 | 192.168.4.22:4660 | 52:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM23_General_normal.Tension_Fase_1_N | 192.168.4.22:4660 | 21:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM23_General_normal.Tension_Fase_2_N | 192.168.4.22:4660 | 21:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM23_General_normal.Tension_Fase_3_N | 192.168.4.22:4660 | 21:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM23_General_normal.Intensidad_Fase_1 | 192.168.4.22:4660 | 21:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM23_General_normal.Intensidad_Fase_2 | 192.168.4.22:4660 | 21:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM23_General_normal.Intensidad_Fase_3 | 192.168.4.22:4660 | 21:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM23_General_normal.Intensidad_Neutro | 192.168.4.22:4660 | 21:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM23_General_normal.Potencia_activa_Fase_1 | 192.168.4.22:4660 | 21:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM23_General_normal.Potencia_activa_Fase_2 | 192.168.4.22:4660 | 21:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM23_General_normal.Potencia_activa_Fase_3 | 192.168.4.22:4660 | 21:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM23_General_normal.Potencia_reactiva_Fase_1 | 192.168.4.22:4660 | 21:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM23_General_normal.Potencia_reactiva_Fase_2 | 192.168.4.22:4660 | 21:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM23_General_normal.Potencia_reactiva_Fase_3 | 192.168.4.22:4660 | 21:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM23_General_normal.Frecuencia | 192.168.4.22:4660 | 21:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM23_General_normal.Energia_activa | 192.168.4.22:4660 | 21:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM23_General_normal.Energia_reactiva_inductiva | 192.168.4.22:4660 | 21:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM23_General_normal.Energia_reactiva_capacitiva | 192.168.4.22:4660 | 21:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM23_General_normal.Energia_aparente | 192.168.4.22:4660 | 21:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM23_General_normal.Potencia_activa_trifasica | 192.168.4.22:4660 | 21:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM23_General_normal.Potencia_inductiva_trifasica | 192.168.4.22:4660 | 21:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM23_General_normal.Potencia_capacitiva_trif | 192.168.4.22:4660 | 21:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM23_General_normal.cos_fi_trifasico | 192.168.4.22:4660 | 21:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM23_General_normal.Factor_de_potencia_trif | 192.168.4.22:4660 | 21:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM23_General_normal.Potencia_Aparente | 192.168.4.22:4660 | 21:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM23_General_normal.THD_V_Fase_1 | 192.168.4.22:4660 | 21:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM23_General_normal.THD_V_Fase_2 | 192.168.4.22:4660 | 21:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM23_General_normal.THD_V_Fase_3 | 192.168.4.22:4660 | 21:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM23_General_normal.THD_A_Fase_1 | 192.168.4.22:4660 | 21:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM23_General_normal.THD_A_Fase_2 | 192.168.4.22:4660 | 21:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM23_General_normal.THD_A_Fase_3 | 192.168.4.22:4660 | 21:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM23_General_normal.Tension_Fase_1_2 | 192.168.4.22:4660 | 21:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM23_General_normal.Tension_Fase_2_3 | 192.168.4.22:4660 | 21:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM23_General_normal.Tension_Fase_3_1 | 192.168.4.22:4660 | 21:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM12_General_normal.Tension_Fase_1_N | 192.168.4.22:4660 | 4:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM12_General_normal.Tension_Fase_2_N | 192.168.4.22:4660 | 4:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM12_General_normal.Tension_Fase_3_N | 192.168.4.22:4660 | 4:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM12_General_normal.Intensidad_Fase_1 | 192.168.4.22:4660 | 4:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM12_General_normal.Intensidad_Fase_2 | 192.168.4.22:4660 | 4:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM12_General_normal.Intensidad_Fase_3 | 192.168.4.22:4660 | 4:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM12_General_normal.Intensidad_Neutro | 192.168.4.22:4660 | 4:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM12_General_normal.Potencia_activa_Fase_1 | 192.168.4.22:4660 | 4:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM12_General_normal.Potencia_activa_Fase_2 | 192.168.4.22:4660 | 4:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM12_General_normal.Potencia_activa_Fase_3 | 192.168.4.22:4660 | 4:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM12_General_normal.Potencia_reactiva_Fase_1 | 192.168.4.22:4660 | 4:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM12_General_normal.Potencia_reactiva_Fase_2 | 192.168.4.22:4660 | 4:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM12_General_normal.Potencia_reactiva_Fase_3 | 192.168.4.22:4660 | 4:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM12_General_normal.Frecuencia | 192.168.4.22:4660 | 4:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM12_General_normal.Energia_activa | 192.168.4.22:4660 | 4:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM12_General_normal.Energia_reactiva_inductiva | 192.168.4.22:4660 | 4:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM12_General_normal.Energia_reactiva_capacitiva | 192.168.4.22:4660 | 4:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM12_General_normal.Energia_aparente | 192.168.4.22:4660 | 4:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM12_General_normal.Potencia_activa_trifasica | 192.168.4.22:4660 | 4:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM12_General_normal.Potencia_inductiva_trifasica | 192.168.4.22:4660 | 4:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM12_General_normal.Potencia_capacitiva_trif | 192.168.4.22:4660 | 4:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM12_General_normal.cos_fi_trifasico | 192.168.4.22:4660 | 4:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM12_General_normal.Factor_de_potencia_trif | 192.168.4.22:4660 | 4:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM12_General_normal.Potencia_Aparente | 192.168.4.22:4660 | 4:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM12_General_normal.THD_V_Fase_1 | 192.168.4.22:4660 | 4:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM12_General_normal.THD_V_Fase_2 | 192.168.4.22:4660 | 4:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM12_General_normal.THD_V_Fase_3 | 192.168.4.22:4660 | 4:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM12_General_normal.THD_A_Fase_1 | 192.168.4.22:4660 | 4:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM12_General_normal.THD_A_Fase_2 | 192.168.4.22:4660 | 4:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM12_General_normal.THD_A_Fase_3 | 192.168.4.22:4660 | 4:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM12_General_normal.Tension_Fase_1_2 | 192.168.4.22:4660 | 4:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM12_General_normal.Tension_Fase_2_3 | 192.168.4.22:4660 | 4:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM12_General_normal.Tension_Fase_3_1 | 192.168.4.22:4660 | 4:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM22_General_normal.Tension_Fase_1_N | 192.168.4.22:4660 | 20:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM22_General_normal.Tension_Fase_2_N | 192.168.4.22:4660 | 20:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM22_General_normal.Tension_Fase_3_N | 192.168.4.22:4660 | 20:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM22_General_normal.Intensidad_Fase_1 | 192.168.4.22:4660 | 20:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM22_General_normal.Intensidad_Fase_2 | 192.168.4.22:4660 | 20:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM22_General_normal.Intensidad_Fase_3 | 192.168.4.22:4660 | 20:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM22_General_normal.Intensidad_Neutro | 192.168.4.22:4660 | 20:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM22_General_normal.Potencia_activa_Fase_1 | 192.168.4.22:4660 | 20:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM22_General_normal.Potencia_activa_Fase_2 | 192.168.4.22:4660 | 20:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM22_General_normal.Potencia_activa_Fase_3 | 192.168.4.22:4660 | 20:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM22_General_normal.Potencia_reactiva_Fase_1 | 192.168.4.22:4660 | 20:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM22_General_normal.Potencia_reactiva_Fase_2 | 192.168.4.22:4660 | 20:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM22_General_normal.Potencia_reactiva_Fase_3 | 192.168.4.22:4660 | 20:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM22_General_normal.Frecuencia | 192.168.4.22:4660 | 20:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM22_General_normal.Energia_activa | 192.168.4.22:4660 | 20:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM22_General_normal.Energia_reactiva_inductiva | 192.168.4.22:4660 | 20:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM22_General_normal.Energia_reactiva_capacitiva | 192.168.4.22:4660 | 20:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM22_General_normal.Energia_aparente | 192.168.4.22:4660 | 20:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM22_General_normal.Potencia_activa_trifasica | 192.168.4.22:4660 | 20:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM22_General_normal.Potencia_inductiva_trifasica | 192.168.4.22:4660 | 20:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM22_General_normal.Potencia_capacitiva_trif | 192.168.4.22:4660 | 20:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM22_General_normal.cos_fi_trifasico | 192.168.4.22:4660 | 20:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM22_General_normal.Factor_de_potencia_trif | 192.168.4.22:4660 | 20:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM22_General_normal.Potencia_Aparente | 192.168.4.22:4660 | 20:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM22_General_normal.THD_V_Fase_1 | 192.168.4.22:4660 | 20:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM22_General_normal.THD_V_Fase_2 | 192.168.4.22:4660 | 20:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM22_General_normal.THD_V_Fase_3 | 192.168.4.22:4660 | 20:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM22_General_normal.THD_A_Fase_1 | 192.168.4.22:4660 | 20:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM22_General_normal.THD_A_Fase_2 | 192.168.4.22:4660 | 20:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM22_General_normal.THD_A_Fase_3 | 192.168.4.22:4660 | 20:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM22_General_normal.Tension_Fase_1_2 | 192.168.4.22:4660 | 20:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM22_General_normal.Tension_Fase_2_3 | 192.168.4.22:4660 | 20:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM22_General_normal.Tension_Fase_3_1 | 192.168.4.22:4660 | 20:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM17_General_normal.Tension_Fase_1_N | 192.168.4.22:4660 | 13:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM17_General_normal.Tension_Fase_2_N | 192.168.4.22:4660 | 13:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM17_General_normal.Tension_Fase_3_N | 192.168.4.22:4660 | 13:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM17_General_normal.Intensidad_Fase_1 | 192.168.4.22:4660 | 13:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM17_General_normal.Intensidad_Fase_2 | 192.168.4.22:4660 | 13:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM17_General_normal.Intensidad_Fase_3 | 192.168.4.22:4660 | 13:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM17_General_normal.Intensidad_Neutro | 192.168.4.22:4660 | 13:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM17_General_normal.Potencia_activa_Fase_1 | 192.168.4.22:4660 | 13:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM17_General_normal.Potencia_activa_Fase_2 | 192.168.4.22:4660 | 13:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM17_General_normal.Potencia_activa_Fase_3 | 192.168.4.22:4660 | 13:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM17_General_normal.Potencia_reactiva_Fase_1 | 192.168.4.22:4660 | 13:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM17_General_normal.Potencia_reactiva_Fase_2 | 192.168.4.22:4660 | 13:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM17_General_normal.Potencia_reactiva_Fase_3 | 192.168.4.22:4660 | 13:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM17_General_normal.Frecuencia | 192.168.4.22:4660 | 13:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM17_General_normal.Energia_activa | 192.168.4.22:4660 | 13:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM17_General_normal.Energia_reactiva_inductiva | 192.168.4.22:4660 | 13:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM17_General_normal.Energia_reactiva_capacitiva | 192.168.4.22:4660 | 13:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM17_General_normal.Energia_aparente | 192.168.4.22:4660 | 13:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM17_General_normal.Potencia_activa_trifasica | 192.168.4.22:4660 | 13:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM17_General_normal.Potencia_inductiva_trifasica | 192.168.4.22:4660 | 13:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM17_General_normal.Potencia_capacitiva_trif | 192.168.4.22:4660 | 13:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM17_General_normal.cos_fi_trifasico | 192.168.4.22:4660 | 13:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM17_General_normal.Factor_de_potencia_trif | 192.168.4.22:4660 | 13:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM17_General_normal.Potencia_Aparente | 192.168.4.22:4660 | 13:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM17_General_normal.THD_V_Fase_1 | 192.168.4.22:4660 | 13:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM17_General_normal.THD_V_Fase_2 | 192.168.4.22:4660 | 13:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM17_General_normal.THD_V_Fase_3 | 192.168.4.22:4660 | 13:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM17_General_normal.THD_A_Fase_1 | 192.168.4.22:4660 | 13:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM17_General_normal.THD_A_Fase_2 | 192.168.4.22:4660 | 13:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM17_General_normal.THD_A_Fase_3 | 192.168.4.22:4660 | 13:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM17_General_normal.Tension_Fase_1_2 | 192.168.4.22:4660 | 13:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM17_General_normal.Tension_Fase_2_3 | 192.168.4.22:4660 | 13:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM17_General_normal.Tension_Fase_3_1 | 192.168.4.22:4660 | 13:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM21_General_normal.Tension_Fase_1_N | 192.168.4.22:4660 | 18:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM21_General_normal.Tension_Fase_2_N | 192.168.4.22:4660 | 18:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM21_General_normal.Tension_Fase_3_N | 192.168.4.22:4660 | 18:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM21_General_normal.Intensidad_Fase_1 | 192.168.4.22:4660 | 18:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM21_General_normal.Intensidad_Fase_2 | 192.168.4.22:4660 | 18:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM21_General_normal.Intensidad_Fase_3 | 192.168.4.22:4660 | 18:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM21_General_normal.Intensidad_Neutro | 192.168.4.22:4660 | 18:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM21_General_normal.Potencia_activa_Fase_1 | 192.168.4.22:4660 | 18:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM21_General_normal.Potencia_activa_Fase_2 | 192.168.4.22:4660 | 18:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM21_General_normal.Potencia_activa_Fase_3 | 192.168.4.22:4660 | 18:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM21_General_normal.Potencia_reactiva_Fase_1 | 192.168.4.22:4660 | 18:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM21_General_normal.Potencia_reactiva_Fase_2 | 192.168.4.22:4660 | 18:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM21_General_normal.Potencia_reactiva_Fase_3 | 192.168.4.22:4660 | 18:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM21_General_normal.Frecuencia | 192.168.4.22:4660 | 18:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM21_General_normal.Energia_activa | 192.168.4.22:4660 | 18:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM21_General_normal.Energia_reactiva_inductiva | 192.168.4.22:4660 | 18:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM21_General_normal.Energia_reactiva_capacitiva | 192.168.4.22:4660 | 18:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM21_General_normal.Energia_aparente | 192.168.4.22:4660 | 18:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM21_General_normal.Potencia_activa_trifasica | 192.168.4.22:4660 | 18:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM21_General_normal.Potencia_inductiva_trifasica | 192.168.4.22:4660 | 18:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM21_General_normal.Potencia_capacitiva_trif | 192.168.4.22:4660 | 18:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM21_General_normal.cos_fi_trifasico | 192.168.4.22:4660 | 18:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM21_General_normal.Factor_de_potencia_trif | 192.168.4.22:4660 | 18:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM21_General_normal.Potencia_Aparente | 192.168.4.22:4660 | 18:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM21_General_normal.THD_V_Fase_1 | 192.168.4.22:4660 | 18:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM21_General_normal.THD_V_Fase_2 | 192.168.4.22:4660 | 18:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM21_General_normal.THD_V_Fase_3 | 192.168.4.22:4660 | 18:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM21_General_normal.THD_A_Fase_1 | 192.168.4.22:4660 | 18:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM21_General_normal.THD_A_Fase_2 | 192.168.4.22:4660 | 18:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM21_General_normal.THD_A_Fase_3 | 192.168.4.22:4660 | 18:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM21_General_normal.Tension_Fase_1_2 | 192.168.4.22:4660 | 18:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM21_General_normal.Tension_Fase_2_3 | 192.168.4.22:4660 | 18:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM21_General_normal.Tension_Fase_3_1 | 192.168.4.22:4660 | 18:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM23_Alumbrado.Tension_Fase_1_N | 192.168.4.22:4660 | 22:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM23_Alumbrado.Tension_Fase_2_N | 192.168.4.22:4660 | 22:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM23_Alumbrado.Tension_Fase_3_N | 192.168.4.22:4660 | 22:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM23_Alumbrado.Intensidad_Fase_1 | 192.168.4.22:4660 | 22:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM23_Alumbrado.Intensidad_Fase_2 | 192.168.4.22:4660 | 22:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM23_Alumbrado.Intensidad_Fase_3 | 192.168.4.22:4660 | 22:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM23_Alumbrado.Intensidad_Neutro | 192.168.4.22:4660 | 22:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM23_Alumbrado.Potencia_activa_Fase_1 | 192.168.4.22:4660 | 22:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM23_Alumbrado.Potencia_activa_Fase_2 | 192.168.4.22:4660 | 22:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM23_Alumbrado.Potencia_activa_Fase_3 | 192.168.4.22:4660 | 22:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM23_Alumbrado.Potencia_reactiva_Fase_1 | 192.168.4.22:4660 | 22:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM23_Alumbrado.Potencia_reactiva_Fase_2 | 192.168.4.22:4660 | 22:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM23_Alumbrado.Potencia_reactiva_Fase_3 | 192.168.4.22:4660 | 22:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM23_Alumbrado.Frecuencia | 192.168.4.22:4660 | 22:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM23_Alumbrado.Energia_activa | 192.168.4.22:4660 | 22:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM23_Alumbrado.Energia_reactiva_inductiva | 192.168.4.22:4660 | 22:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM23_Alumbrado.Energia_reactiva_capacitiva | 192.168.4.22:4660 | 22:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM23_Alumbrado.Energia_aparente | 192.168.4.22:4660 | 22:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM23_Alumbrado.Potencia_activa_trifasica | 192.168.4.22:4660 | 22:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM23_Alumbrado.Potencia_inductiva_trifasica | 192.168.4.22:4660 | 22:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM23_Alumbrado.Potencia_capacitiva_trif | 192.168.4.22:4660 | 22:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM23_Alumbrado.cos_fi_trifasico | 192.168.4.22:4660 | 22:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM23_Alumbrado.Factor_de_potencia_trif | 192.168.4.22:4660 | 22:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM23_Alumbrado.Potencia_Aparente | 192.168.4.22:4660 | 22:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM23_Alumbrado.THD_V_Fase_1 | 192.168.4.22:4660 | 22:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM23_Alumbrado.THD_V_Fase_2 | 192.168.4.22:4660 | 22:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM23_Alumbrado.THD_V_Fase_3 | 192.168.4.22:4660 | 22:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM23_Alumbrado.THD_A_Fase_1 | 192.168.4.22:4660 | 22:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM23_Alumbrado.THD_A_Fase_2 | 192.168.4.22:4660 | 22:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM23_Alumbrado.THD_A_Fase_3 | 192.168.4.22:4660 | 22:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM23_Alumbrado.Tension_Fase_1_2 | 192.168.4.22:4660 | 22:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM23_Alumbrado.Tension_Fase_2_3 | 192.168.4.22:4660 | 22:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM23_Alumbrado.Tension_Fase_3_1 | 192.168.4.22:4660 | 22:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM17_Alumbrado.Tension_Fase_1_N | 192.168.4.22:4660 | 14:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM17_Alumbrado.Tension_Fase_2_N | 192.168.4.22:4660 | 14:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM17_Alumbrado.Tension_Fase_3_N | 192.168.4.22:4660 | 14:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM17_Alumbrado.Intensidad_Fase_1 | 192.168.4.22:4660 | 14:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM17_Alumbrado.Intensidad_Fase_2 | 192.168.4.22:4660 | 14:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM17_Alumbrado.Intensidad_Fase_3 | 192.168.4.22:4660 | 14:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM17_Alumbrado.Intensidad_Neutro | 192.168.4.22:4660 | 14:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM17_Alumbrado.Potencia_activa_Fase_1 | 192.168.4.22:4660 | 14:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM17_Alumbrado.Potencia_activa_Fase_2 | 192.168.4.22:4660 | 14:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM17_Alumbrado.Potencia_activa_Fase_3 | 192.168.4.22:4660 | 14:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM17_Alumbrado.Potencia_reactiva_Fase_1 | 192.168.4.22:4660 | 14:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM17_Alumbrado.Potencia_reactiva_Fase_2 | 192.168.4.22:4660 | 14:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM17_Alumbrado.Potencia_reactiva_Fase_3 | 192.168.4.22:4660 | 14:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM17_Alumbrado.Frecuencia | 192.168.4.22:4660 | 14:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM17_Alumbrado.Energia_activa | 192.168.4.22:4660 | 14:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM17_Alumbrado.Energia_reactiva_inductiva | 192.168.4.22:4660 | 14:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM17_Alumbrado.Energia_reactiva_capacitiva | 192.168.4.22:4660 | 14:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM17_Alumbrado.Energia_aparente | 192.168.4.22:4660 | 14:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM17_Alumbrado.Potencia_activa_trifasica | 192.168.4.22:4660 | 14:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM17_Alumbrado.Potencia_inductiva_trifasica | 192.168.4.22:4660 | 14:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM17_Alumbrado.Potencia_capacitiva_trif | 192.168.4.22:4660 | 14:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM17_Alumbrado.cos_fi_trifasico | 192.168.4.22:4660 | 14:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM17_Alumbrado.Factor_de_potencia_trif | 192.168.4.22:4660 | 14:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM17_Alumbrado.Potencia_Aparente | 192.168.4.22:4660 | 14:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM17_Alumbrado.THD_V_Fase_1 | 192.168.4.22:4660 | 14:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM17_Alumbrado.THD_V_Fase_2 | 192.168.4.22:4660 | 14:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM17_Alumbrado.THD_V_Fase_3 | 192.168.4.22:4660 | 14:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM17_Alumbrado.THD_A_Fase_1 | 192.168.4.22:4660 | 14:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM17_Alumbrado.THD_A_Fase_2 | 192.168.4.22:4660 | 14:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM17_Alumbrado.THD_A_Fase_3 | 192.168.4.22:4660 | 14:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM17_Alumbrado.Tension_Fase_1_2 | 192.168.4.22:4660 | 14:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM17_Alumbrado.Tension_Fase_2_3 | 192.168.4.22:4660 | 14:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM17_Alumbrado.Tension_Fase_3_1 | 192.168.4.22:4660 | 14:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM20_Alumbrado.Tension_Fase_1_N | 192.168.4.22:4660 | 16:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM20_Alumbrado.Tension_Fase_2_N | 192.168.4.22:4660 | 16:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM20_Alumbrado.Tension_Fase_3_N | 192.168.4.22:4660 | 16:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM20_Alumbrado.Intensidad_Fase_1 | 192.168.4.22:4660 | 16:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM20_Alumbrado.Intensidad_Fase_2 | 192.168.4.22:4660 | 16:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM20_Alumbrado.Intensidad_Fase_3 | 192.168.4.22:4660 | 16:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM20_Alumbrado.Intensidad_Neutro | 192.168.4.22:4660 | 16:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM20_Alumbrado.Potencia_activa_Fase_1 | 192.168.4.22:4660 | 16:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM20_Alumbrado.Potencia_activa_Fase_2 | 192.168.4.22:4660 | 16:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM20_Alumbrado.Potencia_activa_Fase_3 | 192.168.4.22:4660 | 16:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM20_Alumbrado.Potencia_reactiva_Fase_1 | 192.168.4.22:4660 | 16:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM20_Alumbrado.Potencia_reactiva_Fase_2 | 192.168.4.22:4660 | 16:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM20_Alumbrado.Potencia_reactiva_Fase_3 | 192.168.4.22:4660 | 16:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM20_Alumbrado.Frecuencia | 192.168.4.22:4660 | 16:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM20_Alumbrado.Energia_activa | 192.168.4.22:4660 | 16:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM20_Alumbrado.Energia_reactiva_inductiva | 192.168.4.22:4660 | 16:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM20_Alumbrado.Energia_reactiva_capacitiva | 192.168.4.22:4660 | 16:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM20_Alumbrado.Energia_aparente | 192.168.4.22:4660 | 16:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM20_Alumbrado.Potencia_activa_trifasica | 192.168.4.22:4660 | 16:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM20_Alumbrado.Potencia_inductiva_trifasica | 192.168.4.22:4660 | 16:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM20_Alumbrado.Potencia_capacitiva_trif | 192.168.4.22:4660 | 16:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM20_Alumbrado.cos_fi_trifasico | 192.168.4.22:4660 | 16:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM20_Alumbrado.Factor_de_potencia_trif | 192.168.4.22:4660 | 16:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM20_Alumbrado.Potencia_Aparente | 192.168.4.22:4660 | 16:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM20_Alumbrado.THD_V_Fase_1 | 192.168.4.22:4660 | 16:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM20_Alumbrado.THD_V_Fase_2 | 192.168.4.22:4660 | 16:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM20_Alumbrado.THD_V_Fase_3 | 192.168.4.22:4660 | 16:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM20_Alumbrado.THD_A_Fase_1 | 192.168.4.22:4660 | 16:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM20_Alumbrado.THD_A_Fase_2 | 192.168.4.22:4660 | 16:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM20_Alumbrado.THD_A_Fase_3 | 192.168.4.22:4660 | 16:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM20_Alumbrado.Tension_Fase_1_2 | 192.168.4.22:4660 | 16:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM20_Alumbrado.Tension_Fase_2_3 | 192.168.4.22:4660 | 16:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM20_Alumbrado.Tension_Fase_3_1 | 192.168.4.22:4660 | 16:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM23_Clima_vent.Tension_Fase_1_N | 192.168.4.22:4660 | 23:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM23_Clima_vent.Tension_Fase_2_N | 192.168.4.22:4660 | 23:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM23_Clima_vent.Tension_Fase_3_N | 192.168.4.22:4660 | 23:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM23_Clima_vent.Intensidad_Fase_1 | 192.168.4.22:4660 | 23:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM23_Clima_vent.Intensidad_Fase_2 | 192.168.4.22:4660 | 23:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM23_Clima_vent.Intensidad_Fase_3 | 192.168.4.22:4660 | 23:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM23_Clima_vent.Intensidad_Neutro | 192.168.4.22:4660 | 23:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM23_Clima_vent.Potencia_activa_Fase_1 | 192.168.4.22:4660 | 23:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM23_Clima_vent.Potencia_activa_Fase_2 | 192.168.4.22:4660 | 23:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM23_Clima_vent.Potencia_activa_Fase_3 | 192.168.4.22:4660 | 23:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM23_Clima_vent.Potencia_reactiva_Fase_1 | 192.168.4.22:4660 | 23:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM23_Clima_vent.Potencia_reactiva_Fase_2 | 192.168.4.22:4660 | 23:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM23_Clima_vent.Potencia_reactiva_Fase_3 | 192.168.4.22:4660 | 23:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM23_Clima_vent.Frecuencia | 192.168.4.22:4660 | 23:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM23_Clima_vent.Energia_activa | 192.168.4.22:4660 | 23:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM23_Clima_vent.Energia_reactiva_inductiva | 192.168.4.22:4660 | 23:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM23_Clima_vent.Energia_reactiva_capacitiva | 192.168.4.22:4660 | 23:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM23_Clima_vent.Energia_aparente | 192.168.4.22:4660 | 23:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM23_Clima_vent.Potencia_activa_trifasica | 192.168.4.22:4660 | 23:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM23_Clima_vent.Potencia_inductiva_trifasica | 192.168.4.22:4660 | 23:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM23_Clima_vent.Potencia_capacitiva_trif | 192.168.4.22:4660 | 23:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM23_Clima_vent.cos_fi_trifasico | 192.168.4.22:4660 | 23:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM23_Clima_vent.Factor_de_potencia_trif | 192.168.4.22:4660 | 23:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM23_Clima_vent.Potencia_Aparente | 192.168.4.22:4660 | 23:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM23_Clima_vent.THD_V_Fase_1 | 192.168.4.22:4660 | 23:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM23_Clima_vent.THD_V_Fase_2 | 192.168.4.22:4660 | 23:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM23_Clima_vent.THD_V_Fase_3 | 192.168.4.22:4660 | 23:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM23_Clima_vent.THD_A_Fase_1 | 192.168.4.22:4660 | 23:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM23_Clima_vent.THD_A_Fase_2 | 192.168.4.22:4660 | 23:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM23_Clima_vent.THD_A_Fase_3 | 192.168.4.22:4660 | 23:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM23_Clima_vent.Tension_Fase_1_2 | 192.168.4.22:4660 | 23:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM23_Clima_vent.Tension_Fase_2_3 | 192.168.4.22:4660 | 23:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM23_Clima_vent.Tension_Fase_3_1 | 192.168.4.22:4660 | 23:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM17_Clima_vent.Tension_Fase_1_N | 192.168.4.22:4660 | 15:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM17_Clima_vent.Tension_Fase_2_N | 192.168.4.22:4660 | 15:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM17_Clima_vent.Tension_Fase_3_N | 192.168.4.22:4660 | 15:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM17_Clima_vent.Intensidad_Fase_1 | 192.168.4.22:4660 | 15:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM17_Clima_vent.Intensidad_Fase_2 | 192.168.4.22:4660 | 15:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM17_Clima_vent.Intensidad_Fase_3 | 192.168.4.22:4660 | 15:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM17_Clima_vent.Intensidad_Neutro | 192.168.4.22:4660 | 15:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM17_Clima_vent.Potencia_activa_Fase_1 | 192.168.4.22:4660 | 15:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM17_Clima_vent.Potencia_activa_Fase_2 | 192.168.4.22:4660 | 15:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM17_Clima_vent.Potencia_activa_Fase_3 | 192.168.4.22:4660 | 15:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM17_Clima_vent.Potencia_reactiva_Fase_1 | 192.168.4.22:4660 | 15:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM17_Clima_vent.Potencia_reactiva_Fase_2 | 192.168.4.22:4660 | 15:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM17_Clima_vent.Potencia_reactiva_Fase_3 | 192.168.4.22:4660 | 15:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM17_Clima_vent.Frecuencia | 192.168.4.22:4660 | 15:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM17_Clima_vent.Energia_activa | 192.168.4.22:4660 | 15:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM17_Clima_vent.Energia_reactiva_inductiva | 192.168.4.22:4660 | 15:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM17_Clima_vent.Energia_reactiva_capacitiva | 192.168.4.22:4660 | 15:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM17_Clima_vent.Energia_aparente | 192.168.4.22:4660 | 15:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM17_Clima_vent.Potencia_activa_trifasica | 192.168.4.22:4660 | 15:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM17_Clima_vent.Potencia_inductiva_trifasica | 192.168.4.22:4660 | 15:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM17_Clima_vent.Potencia_capacitiva_trif | 192.168.4.22:4660 | 15:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM17_Clima_vent.cos_fi_trifasico | 192.168.4.22:4660 | 15:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM17_Clima_vent.Factor_de_potencia_trif | 192.168.4.22:4660 | 15:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM17_Clima_vent.Potencia_Aparente | 192.168.4.22:4660 | 15:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM17_Clima_vent.THD_V_Fase_1 | 192.168.4.22:4660 | 15:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM17_Clima_vent.THD_V_Fase_2 | 192.168.4.22:4660 | 15:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM17_Clima_vent.THD_V_Fase_3 | 192.168.4.22:4660 | 15:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM17_Clima_vent.THD_A_Fase_1 | 192.168.4.22:4660 | 15:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM17_Clima_vent.THD_A_Fase_2 | 192.168.4.22:4660 | 15:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM17_Clima_vent.THD_A_Fase_3 | 192.168.4.22:4660 | 15:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM17_Clima_vent.Tension_Fase_1_2 | 192.168.4.22:4660 | 15:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM17_Clima_vent.Tension_Fase_2_3 | 192.168.4.22:4660 | 15:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM17_Clima_vent.Tension_Fase_3_1 | 192.168.4.22:4660 | 15:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM21_Clima_vent.Tension_Fase_1_N | 192.168.4.22:4660 | 19:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM21_Clima_vent.Tension_Fase_2_N | 192.168.4.22:4660 | 19:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM21_Clima_vent.Tension_Fase_3_N | 192.168.4.22:4660 | 19:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM21_Clima_vent.Intensidad_Fase_1 | 192.168.4.22:4660 | 19:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM21_Clima_vent.Intensidad_Fase_2 | 192.168.4.22:4660 | 19:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM21_Clima_vent.Intensidad_Fase_3 | 192.168.4.22:4660 | 19:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM21_Clima_vent.Intensidad_Neutro | 192.168.4.22:4660 | 19:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM21_Clima_vent.Potencia_activa_Fase_1 | 192.168.4.22:4660 | 19:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM21_Clima_vent.Potencia_activa_Fase_2 | 192.168.4.22:4660 | 19:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM21_Clima_vent.Potencia_activa_Fase_3 | 192.168.4.22:4660 | 19:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM21_Clima_vent.Potencia_reactiva_Fase_1 | 192.168.4.22:4660 | 19:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM21_Clima_vent.Potencia_reactiva_Fase_2 | 192.168.4.22:4660 | 19:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM21_Clima_vent.Potencia_reactiva_Fase_3 | 192.168.4.22:4660 | 19:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM21_Clima_vent.Frecuencia | 192.168.4.22:4660 | 19:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM21_Clima_vent.Energia_activa | 192.168.4.22:4660 | 19:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM21_Clima_vent.Energia_reactiva_inductiva | 192.168.4.22:4660 | 19:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM21_Clima_vent.Energia_reactiva_capacitiva | 192.168.4.22:4660 | 19:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM21_Clima_vent.Energia_aparente | 192.168.4.22:4660 | 19:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM21_Clima_vent.Potencia_activa_trifasica | 192.168.4.22:4660 | 19:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM21_Clima_vent.Potencia_inductiva_trifasica | 192.168.4.22:4660 | 19:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM21_Clima_vent.Potencia_capacitiva_trif | 192.168.4.22:4660 | 19:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM21_Clima_vent.cos_fi_trifasico | 192.168.4.22:4660 | 19:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM21_Clima_vent.Factor_de_potencia_trif | 192.168.4.22:4660 | 19:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM21_Clima_vent.Potencia_Aparente | 192.168.4.22:4660 | 19:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM21_Clima_vent.THD_V_Fase_1 | 192.168.4.22:4660 | 19:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM21_Clima_vent.THD_V_Fase_2 | 192.168.4.22:4660 | 19:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM21_Clima_vent.THD_V_Fase_3 | 192.168.4.22:4660 | 19:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM21_Clima_vent.THD_A_Fase_1 | 192.168.4.22:4660 | 19:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM21_Clima_vent.THD_A_Fase_2 | 192.168.4.22:4660 | 19:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM21_Clima_vent.THD_A_Fase_3 | 192.168.4.22:4660 | 19:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM21_Clima_vent.Tension_Fase_1_2 | 192.168.4.22:4660 | 19:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM21_Clima_vent.Tension_Fase_2_3 | 192.168.4.22:4660 | 19:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM21_Clima_vent.Tension_Fase_3_1 | 192.168.4.22:4660 | 19:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM20_Clima_vent.Tension_Fase_1_N | 192.168.4.22:4660 | 17:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM20_Clima_vent.Tension_Fase_2_N | 192.168.4.22:4660 | 17:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM20_Clima_vent.Tension_Fase_3_N | 192.168.4.22:4660 | 17:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM20_Clima_vent.Intensidad_Fase_1 | 192.168.4.22:4660 | 17:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM20_Clima_vent.Intensidad_Fase_2 | 192.168.4.22:4660 | 17:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM20_Clima_vent.Intensidad_Fase_3 | 192.168.4.22:4660 | 17:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM20_Clima_vent.Intensidad_Neutro | 192.168.4.22:4660 | 17:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM20_Clima_vent.Potencia_activa_Fase_1 | 192.168.4.22:4660 | 17:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM20_Clima_vent.Potencia_activa_Fase_2 | 192.168.4.22:4660 | 17:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM20_Clima_vent.Potencia_activa_Fase_3 | 192.168.4.22:4660 | 17:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM20_Clima_vent.Potencia_reactiva_Fase_1 | 192.168.4.22:4660 | 17:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM20_Clima_vent.Potencia_reactiva_Fase_2 | 192.168.4.22:4660 | 17:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM20_Clima_vent.Potencia_reactiva_Fase_3 | 192.168.4.22:4660 | 17:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM20_Clima_vent.Frecuencia | 192.168.4.22:4660 | 17:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM20_Clima_vent.Energia_activa | 192.168.4.22:4660 | 17:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM20_Clima_vent.Energia_reactiva_inductiva | 192.168.4.22:4660 | 17:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM20_Clima_vent.Energia_reactiva_capacitiva | 192.168.4.22:4660 | 17:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM20_Clima_vent.Energia_aparente | 192.168.4.22:4660 | 17:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM20_Clima_vent.Potencia_activa_trifasica | 192.168.4.22:4660 | 17:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM20_Clima_vent.Potencia_inductiva_trifasica | 192.168.4.22:4660 | 17:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM20_Clima_vent.Potencia_capacitiva_trif | 192.168.4.22:4660 | 17:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM20_Clima_vent.cos_fi_trifasico | 192.168.4.22:4660 | 17:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM20_Clima_vent.Factor_de_potencia_trif | 192.168.4.22:4660 | 17:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM20_Clima_vent.Potencia_Aparente | 192.168.4.22:4660 | 17:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM20_Clima_vent.THD_V_Fase_1 | 192.168.4.22:4660 | 17:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM20_Clima_vent.THD_V_Fase_2 | 192.168.4.22:4660 | 17:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM20_Clima_vent.THD_V_Fase_3 | 192.168.4.22:4660 | 17:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM20_Clima_vent.THD_A_Fase_1 | 192.168.4.22:4660 | 17:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM20_Clima_vent.THD_A_Fase_2 | 192.168.4.22:4660 | 17:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM20_Clima_vent.THD_A_Fase_3 | 192.168.4.22:4660 | 17:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM20_Clima_vent.Tension_Fase_1_2 | 192.168.4.22:4660 | 17:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM20_Clima_vent.Tension_Fase_2_3 | 192.168.4.22:4660 | 17:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM20_Clima_vent.Tension_Fase_3_1 | 192.168.4.22:4660 | 17:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM20_Pergolas_Manso.Tension_Fase_1_N | 192.168.4.22:4660 | 53:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM20_Pergolas_Manso.Tension_Fase_2_N | 192.168.4.22:4660 | 53:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM20_Pergolas_Manso.Tension_Fase_3_N | 192.168.4.22:4660 | 53:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM20_Pergolas_Manso.Intensidad_Fase_1 | 192.168.4.22:4660 | 53:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Manso.Intensidad_Fase_2 | 192.168.4.22:4660 | 53:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Manso.Intensidad_Fase_3 | 192.168.4.22:4660 | 53:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Manso.Intensidad_Neutro | 192.168.4.22:4660 | 53:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Manso.Potencia_activa_Fase_1 | 192.168.4.22:4660 | 53:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Manso.Potencia_activa_Fase_2 | 192.168.4.22:4660 | 53:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Manso.Potencia_activa_Fase_3 | 192.168.4.22:4660 | 53:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Manso.Potencia_reactiva_Fase_1 | 192.168.4.22:4660 | 53:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Manso.Potencia_reactiva_Fase_2 | 192.168.4.22:4660 | 53:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Manso.Potencia_reactiva_Fase_3 | 192.168.4.22:4660 | 53:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Manso.Frecuencia | 192.168.4.22:4660 | 53:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM20_Pergolas_Manso.Energia_activa | 192.168.4.22:4660 | 53:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Manso.Energia_reactiva_inductiva | 192.168.4.22:4660 | 53:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Manso.Energia_reactiva_capacitiva | 192.168.4.22:4660 | 53:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Manso.Energia_aparente | 192.168.4.22:4660 | 53:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Manso.Potencia_activa_trifasica | 192.168.4.22:4660 | 53:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Manso.Potencia_inductiva_trifasica | 192.168.4.22:4660 | 53:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Manso.Potencia_capacitiva_trif | 192.168.4.22:4660 | 53:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Manso.cos_fi_trifasico | 192.168.4.22:4660 | 53:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM20_Pergolas_Manso.Factor_de_potencia_trif | 192.168.4.22:4660 | 53:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM20_Pergolas_Manso.Potencia_Aparente | 192.168.4.22:4660 | 53:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Manso.THD_V_Fase_1 | 192.168.4.22:4660 | 53:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM20_Pergolas_Manso.THD_V_Fase_2 | 192.168.4.22:4660 | 53:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM20_Pergolas_Manso.THD_V_Fase_3 | 192.168.4.22:4660 | 53:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM20_Pergolas_Manso.THD_A_Fase_1 | 192.168.4.22:4660 | 53:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM20_Pergolas_Manso.THD_A_Fase_2 | 192.168.4.22:4660 | 53:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM20_Pergolas_Manso.THD_A_Fase_3 | 192.168.4.22:4660 | 53:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM20_Pergolas_Manso.Tension_Fase_1_2 | 192.168.4.22:4660 | 53:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM20_Pergolas_Manso.Tension_Fase_2_3 | 192.168.4.22:4660 | 53:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM20_Pergolas_Manso.Tension_Fase_3_1 | 192.168.4.22:4660 | 53:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM20_Pergolas_Borrell.Tension_Fase_1_N | 192.168.4.22:4660 | 57:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM20_Pergolas_Borrell.Tension_Fase_2_N | 192.168.4.22:4660 | 57:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM20_Pergolas_Borrell.Tension_Fase_3_N | 192.168.4.22:4660 | 57:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM20_Pergolas_Borrell.Intensidad_Fase_1 | 192.168.4.22:4660 | 57:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Borrell.Intensidad_Fase_2 | 192.168.4.22:4660 | 57:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Borrell.Intensidad_Fase_3 | 192.168.4.22:4660 | 57:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Borrell.Intensidad_Neutro | 192.168.4.22:4660 | 57:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Borrell.Potencia_activa_Fase_1 | 192.168.4.22:4660 | 57:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Borrell.Potencia_activa_Fase_2 | 192.168.4.22:4660 | 57:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Borrell.Potencia_activa_Fase_3 | 192.168.4.22:4660 | 57:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Borrell.Potencia_reactiva_Fase_1 | 192.168.4.22:4660 | 57:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Borrell.Potencia_reactiva_Fase_2 | 192.168.4.22:4660 | 57:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Borrell.Potencia_reactiva_Fase_3 | 192.168.4.22:4660 | 57:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Borrell.Frecuencia | 192.168.4.22:4660 | 57:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM20_Pergolas_Borrell.Energia_activa | 192.168.4.22:4660 | 57:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Borrell.Energia_reactiva_inductiva | 192.168.4.22:4660 | 57:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Borrell.Energia_reactiva_capacitiva | 192.168.4.22:4660 | 57:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Borrell.Energia_aparente | 192.168.4.22:4660 | 57:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Borrell.Potencia_activa_trifasica | 192.168.4.22:4660 | 57:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Borrell.Potencia_inductiva_trifasica | 192.168.4.22:4660 | 57:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Borrell.Potencia_capacitiva_trif | 192.168.4.22:4660 | 57:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Borrell.cos_fi_trifasico | 192.168.4.22:4660 | 57:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM20_Pergolas_Borrell.Factor_de_potencia_trif | 192.168.4.22:4660 | 57:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM20_Pergolas_Borrell.Potencia_Aparente | 192.168.4.22:4660 | 57:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM20_Pergolas_Borrell.THD_V_Fase_1 | 192.168.4.22:4660 | 57:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM20_Pergolas_Borrell.THD_V_Fase_2 | 192.168.4.22:4660 | 57:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM20_Pergolas_Borrell.THD_V_Fase_3 | 192.168.4.22:4660 | 57:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM20_Pergolas_Borrell.THD_A_Fase_1 | 192.168.4.22:4660 | 57:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM20_Pergolas_Borrell.THD_A_Fase_2 | 192.168.4.22:4660 | 57:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM20_Pergolas_Borrell.THD_A_Fase_3 | 192.168.4.22:4660 | 57:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM20_Pergolas_Borrell.Tension_Fase_1_2 | 192.168.4.22:4660 | 57:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM20_Pergolas_Borrell.Tension_Fase_2_3 | 192.168.4.22:4660 | 57:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM20_Pergolas_Borrell.Tension_Fase_3_1 | 192.168.4.22:4660 | 57:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM34_General_normal.Tension_Fase_1_N | 192.168.4.32:4660 | 32:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM34_General_normal.Tension_Fase_2_N | 192.168.4.32:4660 | 32:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM34_General_normal.Tension_Fase_3_N | 192.168.4.32:4660 | 32:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM34_General_normal.Intensidad_Fase_1 | 192.168.4.32:4660 | 32:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM34_General_normal.Intensidad_Fase_2 | 192.168.4.32:4660 | 32:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM34_General_normal.Intensidad_Fase_3 | 192.168.4.32:4660 | 32:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM34_General_normal.Intensidad_Neutro | 192.168.4.32:4660 | 32:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM34_General_normal.Potencia_activa_Fase_1 | 192.168.4.32:4660 | 32:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM34_General_normal.Potencia_activa_Fase_2 | 192.168.4.32:4660 | 32:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM34_General_normal.Potencia_activa_Fase_3 | 192.168.4.32:4660 | 32:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM34_General_normal.Potencia_reactiva_Fase_1 | 192.168.4.32:4660 | 32:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM34_General_normal.Potencia_reactiva_Fase_2 | 192.168.4.32:4660 | 32:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM34_General_normal.Potencia_reactiva_Fase_3 | 192.168.4.32:4660 | 32:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM34_General_normal.Frecuencia | 192.168.4.32:4660 | 32:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM34_General_normal.Energia_activa | 192.168.4.32:4660 | 32:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM34_General_normal.Energia_reactiva_inductiva | 192.168.4.32:4660 | 32:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM34_General_normal.Energia_reactiva_capacitiva | 192.168.4.32:4660 | 32:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM34_General_normal.Energia_aparente | 192.168.4.32:4660 | 32:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM34_General_normal.Potencia_activa_trifasica | 192.168.4.32:4660 | 32:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM34_General_normal.Potencia_inductiva_trifasica | 192.168.4.32:4660 | 32:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM34_General_normal.Potencia_capacitiva_trif | 192.168.4.32:4660 | 32:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM34_General_normal.cos_fi_trifasico | 192.168.4.32:4660 | 32:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM34_General_normal.Factor_de_potencia_trif | 192.168.4.32:4660 | 32:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM34_General_normal.Potencia_Aparente | 192.168.4.32:4660 | 32:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM34_General_normal.THD_V_Fase_1 | 192.168.4.32:4660 | 32:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM34_General_normal.THD_V_Fase_2 | 192.168.4.32:4660 | 32:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM34_General_normal.THD_V_Fase_3 | 192.168.4.32:4660 | 32:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM34_General_normal.THD_A_Fase_1 | 192.168.4.32:4660 | 32:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM34_General_normal.THD_A_Fase_2 | 192.168.4.32:4660 | 32:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM34_General_normal.THD_A_Fase_3 | 192.168.4.32:4660 | 32:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM34_General_normal.Tension_Fase_1_2 | 192.168.4.32:4660 | 32:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM34_General_normal.Tension_Fase_2_3 | 192.168.4.32:4660 | 32:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM34_General_normal.Tension_Fase_3_1 | 192.168.4.32:4660 | 32:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM33_General_normal.Tension_Fase_1_N | 192.168.4.32:4660 | 29:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM33_General_normal.Tension_Fase_2_N | 192.168.4.32:4660 | 29:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM33_General_normal.Tension_Fase_3_N | 192.168.4.32:4660 | 29:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM33_General_normal.Intensidad_Fase_1 | 192.168.4.32:4660 | 29:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM33_General_normal.Intensidad_Fase_2 | 192.168.4.32:4660 | 29:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM33_General_normal.Intensidad_Fase_3 | 192.168.4.32:4660 | 29:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM33_General_normal.Intensidad_Neutro | 192.168.4.32:4660 | 29:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM33_General_normal.Potencia_activa_Fase_1 | 192.168.4.32:4660 | 29:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM33_General_normal.Potencia_activa_Fase_2 | 192.168.4.32:4660 | 29:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM33_General_normal.Potencia_activa_Fase_3 | 192.168.4.32:4660 | 29:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM33_General_normal.Potencia_reactiva_Fase_1 | 192.168.4.32:4660 | 29:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM33_General_normal.Potencia_reactiva_Fase_2 | 192.168.4.32:4660 | 29:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM33_General_normal.Potencia_reactiva_Fase_3 | 192.168.4.32:4660 | 29:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM33_General_normal.Frecuencia | 192.168.4.32:4660 | 29:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM33_General_normal.Energia_activa | 192.168.4.32:4660 | 29:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM33_General_normal.Energia_reactiva_inductiva | 192.168.4.32:4660 | 29:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM33_General_normal.Energia_reactiva_capacitiva | 192.168.4.32:4660 | 29:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM33_General_normal.Energia_aparente | 192.168.4.32:4660 | 29:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM33_General_normal.Potencia_activa_trifasica | 192.168.4.32:4660 | 29:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM33_General_normal.Potencia_inductiva_trifasica | 192.168.4.32:4660 | 29:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM33_General_normal.Potencia_capacitiva_trif | 192.168.4.32:4660 | 29:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM33_General_normal.cos_fi_trifasico | 192.168.4.32:4660 | 29:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM33_General_normal.Factor_de_potencia_trif | 192.168.4.32:4660 | 29:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM33_General_normal.Potencia_Aparente | 192.168.4.32:4660 | 29:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM33_General_normal.THD_V_Fase_1 | 192.168.4.32:4660 | 29:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM33_General_normal.THD_V_Fase_2 | 192.168.4.32:4660 | 29:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM33_General_normal.THD_V_Fase_3 | 192.168.4.32:4660 | 29:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM33_General_normal.THD_A_Fase_1 | 192.168.4.32:4660 | 29:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM33_General_normal.THD_A_Fase_2 | 192.168.4.32:4660 | 29:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM33_General_normal.THD_A_Fase_3 | 192.168.4.32:4660 | 29:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM33_General_normal.Tension_Fase_1_2 | 192.168.4.32:4660 | 29:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM33_General_normal.Tension_Fase_2_3 | 192.168.4.32:4660 | 29:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM33_General_normal.Tension_Fase_3_1 | 192.168.4.32:4660 | 29:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM16_General_normal.Tension_Fase_1_N | 192.168.4.32:4660 | 12:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM16_General_normal.Tension_Fase_2_N | 192.168.4.32:4660 | 12:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM16_General_normal.Tension_Fase_3_N | 192.168.4.32:4660 | 12:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM16_General_normal.Intensidad_Fase_1 | 192.168.4.32:4660 | 12:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM16_General_normal.Intensidad_Fase_2 | 192.168.4.32:4660 | 12:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM16_General_normal.Intensidad_Fase_3 | 192.168.4.32:4660 | 12:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM16_General_normal.Intensidad_Neutro | 192.168.4.32:4660 | 12:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM16_General_normal.Potencia_activa_Fase_1 | 192.168.4.32:4660 | 12:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM16_General_normal.Potencia_activa_Fase_2 | 192.168.4.32:4660 | 12:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM16_General_normal.Potencia_activa_Fase_3 | 192.168.4.32:4660 | 12:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM16_General_normal.Potencia_reactiva_Fase_1 | 192.168.4.32:4660 | 12:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM16_General_normal.Potencia_reactiva_Fase_2 | 192.168.4.32:4660 | 12:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM16_General_normal.Potencia_reactiva_Fase_3 | 192.168.4.32:4660 | 12:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM16_General_normal.Frecuencia | 192.168.4.32:4660 | 12:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM16_General_normal.Energia_activa | 192.168.4.32:4660 | 12:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM16_General_normal.Energia_reactiva_inductiva | 192.168.4.32:4660 | 12:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM16_General_normal.Energia_reactiva_capacitiva | 192.168.4.32:4660 | 12:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM16_General_normal.Energia_aparente | 192.168.4.32:4660 | 12:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM16_General_normal.Potencia_activa_trifasica | 192.168.4.32:4660 | 12:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM16_General_normal.Potencia_inductiva_trifasica | 192.168.4.32:4660 | 12:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM16_General_normal.Potencia_capacitiva_trif | 192.168.4.32:4660 | 12:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM16_General_normal.cos_fi_trifasico | 192.168.4.32:4660 | 12:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM16_General_normal.Factor_de_potencia_trif | 192.168.4.32:4660 | 12:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM16_General_normal.Potencia_Aparente | 192.168.4.32:4660 | 12:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM16_General_normal.THD_V_Fase_1 | 192.168.4.32:4660 | 12:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM16_General_normal.THD_V_Fase_2 | 192.168.4.32:4660 | 12:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM16_General_normal.THD_V_Fase_3 | 192.168.4.32:4660 | 12:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM16_General_normal.THD_A_Fase_1 | 192.168.4.32:4660 | 12:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM16_General_normal.THD_A_Fase_2 | 192.168.4.32:4660 | 12:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM16_General_normal.THD_A_Fase_3 | 192.168.4.32:4660 | 12:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM16_General_normal.Tension_Fase_1_2 | 192.168.4.32:4660 | 12:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM16_General_normal.Tension_Fase_2_3 | 192.168.4.32:4660 | 12:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM16_General_normal.Tension_Fase_3_1 | 192.168.4.32:4660 | 12:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM31_General_normal.Tension_Fase_1_N | 192.168.4.32:4660 | 27:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM31_General_normal.Tension_Fase_2_N | 192.168.4.32:4660 | 27:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM31_General_normal.Tension_Fase_3_N | 192.168.4.32:4660 | 27:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM31_General_normal.Intensidad_Fase_1 | 192.168.4.32:4660 | 27:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM31_General_normal.Intensidad_Fase_2 | 192.168.4.32:4660 | 27:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM31_General_normal.Intensidad_Fase_3 | 192.168.4.32:4660 | 27:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM31_General_normal.Intensidad_Neutro | 192.168.4.32:4660 | 27:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM31_General_normal.Potencia_activa_Fase_1 | 192.168.4.32:4660 | 27:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM31_General_normal.Potencia_activa_Fase_2 | 192.168.4.32:4660 | 27:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM31_General_normal.Potencia_activa_Fase_3 | 192.168.4.32:4660 | 27:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM31_General_normal.Potencia_reactiva_Fase_1 | 192.168.4.32:4660 | 27:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM31_General_normal.Potencia_reactiva_Fase_2 | 192.168.4.32:4660 | 27:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM31_General_normal.Potencia_reactiva_Fase_3 | 192.168.4.32:4660 | 27:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM31_General_normal.Frecuencia | 192.168.4.32:4660 | 27:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM31_General_normal.Energia_activa | 192.168.4.32:4660 | 27:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM31_General_normal.Energia_reactiva_inductiva | 192.168.4.32:4660 | 27:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM31_General_normal.Energia_reactiva_capacitiva | 192.168.4.32:4660 | 27:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM31_General_normal.Energia_aparente | 192.168.4.32:4660 | 27:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM31_General_normal.Potencia_activa_trifasica | 192.168.4.32:4660 | 27:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM31_General_normal.Potencia_inductiva_trifasica | 192.168.4.32:4660 | 27:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM31_General_normal.Potencia_capacitiva_trif | 192.168.4.32:4660 | 27:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM31_General_normal.cos_fi_trifasico | 192.168.4.32:4660 | 27:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM31_General_normal.Factor_de_potencia_trif | 192.168.4.32:4660 | 27:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM31_General_normal.Potencia_Aparente | 192.168.4.32:4660 | 27:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM31_General_normal.THD_V_Fase_1 | 192.168.4.32:4660 | 27:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM31_General_normal.THD_V_Fase_2 | 192.168.4.32:4660 | 27:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM31_General_normal.THD_V_Fase_3 | 192.168.4.32:4660 | 27:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM31_General_normal.THD_A_Fase_1 | 192.168.4.32:4660 | 27:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM31_General_normal.THD_A_Fase_2 | 192.168.4.32:4660 | 27:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM31_General_normal.THD_A_Fase_3 | 192.168.4.32:4660 | 27:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM31_General_normal.Tension_Fase_1_2 | 192.168.4.32:4660 | 27:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM31_General_normal.Tension_Fase_2_3 | 192.168.4.32:4660 | 27:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM31_General_normal.Tension_Fase_3_1 | 192.168.4.32:4660 | 27:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM33_Alumbrado.Tension_Fase_1_N | 192.168.4.32:4660 | 30:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM33_Alumbrado.Tension_Fase_2_N | 192.168.4.32:4660 | 30:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM33_Alumbrado.Tension_Fase_3_N | 192.168.4.32:4660 | 30:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM33_Alumbrado.Intensidad_Fase_1 | 192.168.4.32:4660 | 30:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM33_Alumbrado.Intensidad_Fase_2 | 192.168.4.32:4660 | 30:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM33_Alumbrado.Intensidad_Fase_3 | 192.168.4.32:4660 | 30:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM33_Alumbrado.Intensidad_Neutro | 192.168.4.32:4660 | 30:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM33_Alumbrado.Potencia_activa_Fase_1 | 192.168.4.32:4660 | 30:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM33_Alumbrado.Potencia_activa_Fase_2 | 192.168.4.32:4660 | 30:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM33_Alumbrado.Potencia_activa_Fase_3 | 192.168.4.32:4660 | 30:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM33_Alumbrado.Potencia_reactiva_Fase_1 | 192.168.4.32:4660 | 30:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM33_Alumbrado.Potencia_reactiva_Fase_2 | 192.168.4.32:4660 | 30:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM33_Alumbrado.Potencia_reactiva_Fase_3 | 192.168.4.32:4660 | 30:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM33_Alumbrado.Frecuencia | 192.168.4.32:4660 | 30:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM33_Alumbrado.Energia_activa | 192.168.4.32:4660 | 30:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM33_Alumbrado.Energia_reactiva_inductiva | 192.168.4.32:4660 | 30:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM33_Alumbrado.Energia_reactiva_capacitiva | 192.168.4.32:4660 | 30:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM33_Alumbrado.Energia_aparente | 192.168.4.32:4660 | 30:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM33_Alumbrado.Potencia_activa_trifasica | 192.168.4.32:4660 | 30:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM33_Alumbrado.Potencia_inductiva_trifasica | 192.168.4.32:4660 | 30:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM33_Alumbrado.Potencia_capacitiva_trif | 192.168.4.32:4660 | 30:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM33_Alumbrado.cos_fi_trifasico | 192.168.4.32:4660 | 30:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM33_Alumbrado.Factor_de_potencia_trif | 192.168.4.32:4660 | 30:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM33_Alumbrado.Potencia_Aparente | 192.168.4.32:4660 | 30:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM33_Alumbrado.THD_V_Fase_1 | 192.168.4.32:4660 | 30:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM33_Alumbrado.THD_V_Fase_2 | 192.168.4.32:4660 | 30:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM33_Alumbrado.THD_V_Fase_3 | 192.168.4.32:4660 | 30:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM33_Alumbrado.THD_A_Fase_1 | 192.168.4.32:4660 | 30:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM33_Alumbrado.THD_A_Fase_2 | 192.168.4.32:4660 | 30:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM33_Alumbrado.THD_A_Fase_3 | 192.168.4.32:4660 | 30:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM33_Alumbrado.Tension_Fase_1_2 | 192.168.4.32:4660 | 30:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM33_Alumbrado.Tension_Fase_2_3 | 192.168.4.32:4660 | 30:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM33_Alumbrado.Tension_Fase_3_1 | 192.168.4.32:4660 | 30:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM30_Alumbrado.Tension_Fase_1_N | 192.168.4.32:4660 | 25:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM30_Alumbrado.Tension_Fase_2_N | 192.168.4.32:4660 | 25:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM30_Alumbrado.Tension_Fase_3_N | 192.168.4.32:4660 | 25:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM30_Alumbrado.Intensidad_Fase_1 | 192.168.4.32:4660 | 25:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM30_Alumbrado.Intensidad_Fase_2 | 192.168.4.32:4660 | 25:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM30_Alumbrado.Intensidad_Fase_3 | 192.168.4.32:4660 | 25:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM30_Alumbrado.Intensidad_Neutro | 192.168.4.32:4660 | 25:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM30_Alumbrado.Potencia_activa_Fase_1 | 192.168.4.32:4660 | 25:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM30_Alumbrado.Potencia_activa_Fase_2 | 192.168.4.32:4660 | 25:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM30_Alumbrado.Potencia_activa_Fase_3 | 192.168.4.32:4660 | 25:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM30_Alumbrado.Potencia_reactiva_Fase_1 | 192.168.4.32:4660 | 25:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM30_Alumbrado.Potencia_reactiva_Fase_2 | 192.168.4.32:4660 | 25:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM30_Alumbrado.Potencia_reactiva_Fase_3 | 192.168.4.32:4660 | 25:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM30_Alumbrado.Frecuencia | 192.168.4.32:4660 | 25:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM30_Alumbrado.Energia_activa | 192.168.4.32:4660 | 25:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM30_Alumbrado.Energia_reactiva_inductiva | 192.168.4.32:4660 | 25:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM30_Alumbrado.Energia_reactiva_capacitiva | 192.168.4.32:4660 | 25:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM30_Alumbrado.Energia_aparente | 192.168.4.32:4660 | 25:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM30_Alumbrado.Potencia_activa_trifasica | 192.168.4.32:4660 | 25:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM30_Alumbrado.Potencia_inductiva_trifasica | 192.168.4.32:4660 | 25:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM30_Alumbrado.Potencia_capacitiva_trif | 192.168.4.32:4660 | 25:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM30_Alumbrado.cos_fi_trifasico | 192.168.4.32:4660 | 25:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM30_Alumbrado.Factor_de_potencia_trif | 192.168.4.32:4660 | 25:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM30_Alumbrado.Potencia_Aparente | 192.168.4.32:4660 | 25:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM30_Alumbrado.THD_V_Fase_1 | 192.168.4.32:4660 | 25:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM30_Alumbrado.THD_V_Fase_2 | 192.168.4.32:4660 | 25:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM30_Alumbrado.THD_V_Fase_3 | 192.168.4.32:4660 | 25:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM30_Alumbrado.THD_A_Fase_1 | 192.168.4.32:4660 | 25:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM30_Alumbrado.THD_A_Fase_2 | 192.168.4.32:4660 | 25:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM30_Alumbrado.THD_A_Fase_3 | 192.168.4.32:4660 | 25:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM30_Alumbrado.Tension_Fase_1_2 | 192.168.4.32:4660 | 25:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM30_Alumbrado.Tension_Fase_2_3 | 192.168.4.32:4660 | 25:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM30_Alumbrado.Tension_Fase_3_1 | 192.168.4.32:4660 | 25:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM33_Clima_vent.Tension_Fase_1_N | 192.168.4.32:4660 | 31:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM33_Clima_vent.Tension_Fase_2_N | 192.168.4.32:4660 | 31:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM33_Clima_vent.Tension_Fase_3_N | 192.168.4.32:4660 | 31:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM33_Clima_vent.Intensidad_Fase_1 | 192.168.4.32:4660 | 31:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM33_Clima_vent.Intensidad_Fase_2 | 192.168.4.32:4660 | 31:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM33_Clima_vent.Intensidad_Fase_3 | 192.168.4.32:4660 | 31:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM33_Clima_vent.Intensidad_Neutro | 192.168.4.32:4660 | 31:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM33_Clima_vent.Potencia_activa_Fase_1 | 192.168.4.32:4660 | 31:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM33_Clima_vent.Potencia_activa_Fase_2 | 192.168.4.32:4660 | 31:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM33_Clima_vent.Potencia_activa_Fase_3 | 192.168.4.32:4660 | 31:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM33_Clima_vent.Potencia_reactiva_Fase_1 | 192.168.4.32:4660 | 31:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM33_Clima_vent.Potencia_reactiva_Fase_2 | 192.168.4.32:4660 | 31:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM33_Clima_vent.Potencia_reactiva_Fase_3 | 192.168.4.32:4660 | 31:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM33_Clima_vent.Frecuencia | 192.168.4.32:4660 | 31:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM33_Clima_vent.Energia_activa | 192.168.4.32:4660 | 31:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM33_Clima_vent.Energia_reactiva_inductiva | 192.168.4.32:4660 | 31:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM33_Clima_vent.Energia_reactiva_capacitiva | 192.168.4.32:4660 | 31:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM33_Clima_vent.Energia_aparente | 192.168.4.32:4660 | 31:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM33_Clima_vent.Potencia_activa_trifasica | 192.168.4.32:4660 | 31:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM33_Clima_vent.Potencia_inductiva_trifasica | 192.168.4.32:4660 | 31:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM33_Clima_vent.Potencia_capacitiva_trif | 192.168.4.32:4660 | 31:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM33_Clima_vent.cos_fi_trifasico | 192.168.4.32:4660 | 31:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM33_Clima_vent.Factor_de_potencia_trif | 192.168.4.32:4660 | 31:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM33_Clima_vent.Potencia_Aparente | 192.168.4.32:4660 | 31:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM33_Clima_vent.THD_V_Fase_1 | 192.168.4.32:4660 | 31:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM33_Clima_vent.THD_V_Fase_2 | 192.168.4.32:4660 | 31:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM33_Clima_vent.THD_V_Fase_3 | 192.168.4.32:4660 | 31:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM33_Clima_vent.THD_A_Fase_1 | 192.168.4.32:4660 | 31:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM33_Clima_vent.THD_A_Fase_2 | 192.168.4.32:4660 | 31:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM33_Clima_vent.THD_A_Fase_3 | 192.168.4.32:4660 | 31:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM33_Clima_vent.Tension_Fase_1_2 | 192.168.4.32:4660 | 31:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM33_Clima_vent.Tension_Fase_2_3 | 192.168.4.32:4660 | 31:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM33_Clima_vent.Tension_Fase_3_1 | 192.168.4.32:4660 | 31:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM31_Clima_vent.Tension_Fase_1_N | 192.168.4.32:4660 | 28:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM31_Clima_vent.Tension_Fase_2_N | 192.168.4.32:4660 | 28:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM31_Clima_vent.Tension_Fase_3_N | 192.168.4.32:4660 | 28:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM31_Clima_vent.Intensidad_Fase_1 | 192.168.4.32:4660 | 28:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM31_Clima_vent.Intensidad_Fase_2 | 192.168.4.32:4660 | 28:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM31_Clima_vent.Intensidad_Fase_3 | 192.168.4.32:4660 | 28:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM31_Clima_vent.Intensidad_Neutro | 192.168.4.32:4660 | 28:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM31_Clima_vent.Potencia_activa_Fase_1 | 192.168.4.32:4660 | 28:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM31_Clima_vent.Potencia_activa_Fase_2 | 192.168.4.32:4660 | 28:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM31_Clima_vent.Potencia_activa_Fase_3 | 192.168.4.32:4660 | 28:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM31_Clima_vent.Potencia_reactiva_Fase_1 | 192.168.4.32:4660 | 28:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM31_Clima_vent.Potencia_reactiva_Fase_2 | 192.168.4.32:4660 | 28:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM31_Clima_vent.Potencia_reactiva_Fase_3 | 192.168.4.32:4660 | 28:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM31_Clima_vent.Frecuencia | 192.168.4.32:4660 | 28:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM31_Clima_vent.Energia_activa | 192.168.4.32:4660 | 28:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM31_Clima_vent.Energia_reactiva_inductiva | 192.168.4.32:4660 | 28:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM31_Clima_vent.Energia_reactiva_capacitiva | 192.168.4.32:4660 | 28:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM31_Clima_vent.Energia_aparente | 192.168.4.32:4660 | 28:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM31_Clima_vent.Potencia_activa_trifasica | 192.168.4.32:4660 | 28:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM31_Clima_vent.Potencia_inductiva_trifasica | 192.168.4.32:4660 | 28:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM31_Clima_vent.Potencia_capacitiva_trif | 192.168.4.32:4660 | 28:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM31_Clima_vent.cos_fi_trifasico | 192.168.4.32:4660 | 28:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM31_Clima_vent.Factor_de_potencia_trif | 192.168.4.32:4660 | 28:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM31_Clima_vent.Potencia_Aparente | 192.168.4.32:4660 | 28:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM31_Clima_vent.THD_V_Fase_1 | 192.168.4.32:4660 | 28:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM31_Clima_vent.THD_V_Fase_2 | 192.168.4.32:4660 | 28:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM31_Clima_vent.THD_V_Fase_3 | 192.168.4.32:4660 | 28:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM31_Clima_vent.THD_A_Fase_1 | 192.168.4.32:4660 | 28:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM31_Clima_vent.THD_A_Fase_2 | 192.168.4.32:4660 | 28:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM31_Clima_vent.THD_A_Fase_3 | 192.168.4.32:4660 | 28:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM31_Clima_vent.Tension_Fase_1_2 | 192.168.4.32:4660 | 28:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM31_Clima_vent.Tension_Fase_2_3 | 192.168.4.32:4660 | 28:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM31_Clima_vent.Tension_Fase_3_1 | 192.168.4.32:4660 | 28:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM30_Clima_vent.Tension_Fase_1_N | 192.168.4.32:4660 | 26:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM30_Clima_vent.Tension_Fase_2_N | 192.168.4.32:4660 | 26:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM30_Clima_vent.Tension_Fase_3_N | 192.168.4.32:4660 | 26:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM30_Clima_vent.Intensidad_Fase_1 | 192.168.4.32:4660 | 26:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM30_Clima_vent.Intensidad_Fase_2 | 192.168.4.32:4660 | 26:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM30_Clima_vent.Intensidad_Fase_3 | 192.168.4.32:4660 | 26:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM30_Clima_vent.Intensidad_Neutro | 192.168.4.32:4660 | 26:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM30_Clima_vent.Potencia_activa_Fase_1 | 192.168.4.32:4660 | 26:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM30_Clima_vent.Potencia_activa_Fase_2 | 192.168.4.32:4660 | 26:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM30_Clima_vent.Potencia_activa_Fase_3 | 192.168.4.32:4660 | 26:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM30_Clima_vent.Potencia_reactiva_Fase_1 | 192.168.4.32:4660 | 26:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM30_Clima_vent.Potencia_reactiva_Fase_2 | 192.168.4.32:4660 | 26:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM30_Clima_vent.Potencia_reactiva_Fase_3 | 192.168.4.32:4660 | 26:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM30_Clima_vent.Frecuencia | 192.168.4.32:4660 | 26:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM30_Clima_vent.Energia_activa | 192.168.4.32:4660 | 26:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM30_Clima_vent.Energia_reactiva_inductiva | 192.168.4.32:4660 | 26:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM30_Clima_vent.Energia_reactiva_capacitiva | 192.168.4.32:4660 | 26:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM30_Clima_vent.Energia_aparente | 192.168.4.32:4660 | 26:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM30_Clima_vent.Potencia_activa_trifasica | 192.168.4.32:4660 | 26:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM30_Clima_vent.Potencia_inductiva_trifasica | 192.168.4.32:4660 | 26:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM30_Clima_vent.Potencia_capacitiva_trif | 192.168.4.32:4660 | 26:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM30_Clima_vent.cos_fi_trifasico | 192.168.4.32:4660 | 26:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM30_Clima_vent.Factor_de_potencia_trif | 192.168.4.32:4660 | 26:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM30_Clima_vent.Potencia_Aparente | 192.168.4.32:4660 | 26:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM30_Clima_vent.THD_V_Fase_1 | 192.168.4.32:4660 | 26:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM30_Clima_vent.THD_V_Fase_2 | 192.168.4.32:4660 | 26:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM30_Clima_vent.THD_V_Fase_3 | 192.168.4.32:4660 | 26:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM30_Clima_vent.THD_A_Fase_1 | 192.168.4.32:4660 | 26:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM30_Clima_vent.THD_A_Fase_2 | 192.168.4.32:4660 | 26:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM30_Clima_vent.THD_A_Fase_3 | 192.168.4.32:4660 | 26:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM30_Clima_vent.Tension_Fase_1_2 | 192.168.4.32:4660 | 26:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM30_Clima_vent.Tension_Fase_2_3 | 192.168.4.32:4660 | 26:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM30_Clima_vent.Tension_Fase_3_1 | 192.168.4.32:4660 | 26:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM30_Pergolas_Tamarit.Tension_Fase_1_N | 192.168.4.32:4660 | 54:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM30_Pergolas_Tamarit.Tension_Fase_2_N | 192.168.4.32:4660 | 54:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM30_Pergolas_Tamarit.Tension_Fase_3_N | 192.168.4.32:4660 | 54:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM30_Pergolas_Tamarit.Intensidad_Fase_1 | 192.168.4.32:4660 | 54:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Tamarit.Intensidad_Fase_2 | 192.168.4.32:4660 | 54:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Tamarit.Intensidad_Fase_3 | 192.168.4.32:4660 | 54:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Tamarit.Intensidad_Neutro | 192.168.4.32:4660 | 54:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Tamarit.Potencia_activa_Fase_1 | 192.168.4.32:4660 | 54:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Tamarit.Potencia_activa_Fase_2 | 192.168.4.32:4660 | 54:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Tamarit.Potencia_activa_Fase_3 | 192.168.4.32:4660 | 54:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Tamarit.Potencia_reactiva_Fase_1 | 192.168.4.32:4660 | 54:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Tamarit.Potencia_reactiva_Fase_2 | 192.168.4.32:4660 | 54:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Tamarit.Potencia_reactiva_Fase_3 | 192.168.4.32:4660 | 54:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Tamarit.Frecuencia | 192.168.4.32:4660 | 54:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM30_Pergolas_Tamarit.Energia_activa | 192.168.4.32:4660 | 54:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Tamarit.Energia_reactiva_inductiva | 192.168.4.32:4660 | 54:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Tamarit.Energia_reactiva_capacitiva | 192.168.4.32:4660 | 54:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Tamarit.Energia_aparente | 192.168.4.32:4660 | 54:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Tamarit.Potencia_activa_trifasica | 192.168.4.32:4660 | 54:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Tamarit.Potencia_inductiva_trifasica | 192.168.4.32:4660 | 54:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Tamarit.Potencia_capacitiva_trif | 192.168.4.32:4660 | 54:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Tamarit.cos_fi_trifasico | 192.168.4.32:4660 | 54:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM30_Pergolas_Tamarit.Factor_de_potencia_trif | 192.168.4.32:4660 | 54:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM30_Pergolas_Tamarit.Potencia_Aparente | 192.168.4.32:4660 | 54:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Tamarit.THD_V_Fase_1 | 192.168.4.32:4660 | 54:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM30_Pergolas_Tamarit.THD_V_Fase_2 | 192.168.4.32:4660 | 54:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM30_Pergolas_Tamarit.THD_V_Fase_3 | 192.168.4.32:4660 | 54:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM30_Pergolas_Tamarit.THD_A_Fase_1 | 192.168.4.32:4660 | 54:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM30_Pergolas_Tamarit.THD_A_Fase_2 | 192.168.4.32:4660 | 54:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM30_Pergolas_Tamarit.THD_A_Fase_3 | 192.168.4.32:4660 | 54:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM30_Pergolas_Tamarit.Tension_Fase_1_2 | 192.168.4.32:4660 | 54:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM30_Pergolas_Tamarit.Tension_Fase_2_3 | 192.168.4.32:4660 | 54:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM30_Pergolas_Tamarit.Tension_Fase_3_1 | 192.168.4.32:4660 | 54:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM30_Pergolas_Dominical.Tension_Fase_1_N | 192.168.4.32:4660 | 58:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM30_Pergolas_Dominical.Tension_Fase_2_N | 192.168.4.32:4660 | 58:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM30_Pergolas_Dominical.Tension_Fase_3_N | 192.168.4.32:4660 | 58:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM30_Pergolas_Dominical.Intensidad_Fase_1 | 192.168.4.32:4660 | 58:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Dominical.Intensidad_Fase_2 | 192.168.4.32:4660 | 58:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Dominical.Intensidad_Fase_3 | 192.168.4.32:4660 | 58:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Dominical.Intensidad_Neutro | 192.168.4.32:4660 | 58:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Dominical.Potencia_activa_Fase_1 | 192.168.4.32:4660 | 58:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Dominical.Potencia_activa_Fase_2 | 192.168.4.32:4660 | 58:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Dominical.Potencia_activa_Fase_3 | 192.168.4.32:4660 | 58:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Dominical.Potencia_reactiva_Fase_1 | 192.168.4.32:4660 | 58:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Dominical.Potencia_reactiva_Fase_2 | 192.168.4.32:4660 | 58:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Dominical.Potencia_reactiva_Fase_3 | 192.168.4.32:4660 | 58:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Dominical.Frecuencia | 192.168.4.32:4660 | 58:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM30_Pergolas_Dominical.Energia_activa | 192.168.4.32:4660 | 58:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Dominical.Energia_reactiva_inductiva | 192.168.4.32:4660 | 58:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Dominical.Energia_reactiva_capacitiva | 192.168.4.32:4660 | 58:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Dominical.Energia_aparente | 192.168.4.32:4660 | 58:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Dominical.Potencia_activa_trifasica | 192.168.4.32:4660 | 58:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Dominical.Potencia_inductiva_trifasica | 192.168.4.32:4660 | 58:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Dominical.Potencia_capacitiva_trif | 192.168.4.32:4660 | 58:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Dominical.cos_fi_trifasico | 192.168.4.32:4660 | 58:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM30_Pergolas_Dominical.Factor_de_potencia_trif | 192.168.4.32:4660 | 58:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM30_Pergolas_Dominical.Potencia_Aparente | 192.168.4.32:4660 | 58:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM30_Pergolas_Dominical.THD_V_Fase_1 | 192.168.4.32:4660 | 58:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM30_Pergolas_Dominical.THD_V_Fase_2 | 192.168.4.32:4660 | 58:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM30_Pergolas_Dominical.THD_V_Fase_3 | 192.168.4.32:4660 | 58:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM30_Pergolas_Dominical.THD_A_Fase_1 | 192.168.4.32:4660 | 58:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM30_Pergolas_Dominical.THD_A_Fase_2 | 192.168.4.32:4660 | 58:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM30_Pergolas_Dominical.THD_A_Fase_3 | 192.168.4.32:4660 | 58:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM30_Pergolas_Dominical.Tension_Fase_1_2 | 192.168.4.32:4660 | 58:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM30_Pergolas_Dominical.Tension_Fase_2_3 | 192.168.4.32:4660 | 58:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM30_Pergolas_Dominical.Tension_Fase_3_1 | 192.168.4.32:4660 | 58:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM44_General_normal.Tension_Fase_1_N | 192.168.4.42:4660 | 56:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM44_General_normal.Tension_Fase_2_N | 192.168.4.42:4660 | 56:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM44_General_normal.Tension_Fase_3_N | 192.168.4.42:4660 | 56:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM44_General_normal.Intensidad_Fase_1 | 192.168.4.42:4660 | 56:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM44_General_normal.Intensidad_Fase_2 | 192.168.4.42:4660 | 56:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM44_General_normal.Intensidad_Fase_3 | 192.168.4.42:4660 | 56:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM44_General_normal.Intensidad_Neutro | 192.168.4.42:4660 | 56:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM44_General_normal.Potencia_activa_Fase_1 | 192.168.4.42:4660 | 56:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM44_General_normal.Potencia_activa_Fase_2 | 192.168.4.42:4660 | 56:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM44_General_normal.Potencia_activa_Fase_3 | 192.168.4.42:4660 | 56:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM44_General_normal.Potencia_reactiva_Fase_1 | 192.168.4.42:4660 | 56:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM44_General_normal.Potencia_reactiva_Fase_2 | 192.168.4.42:4660 | 56:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM44_General_normal.Potencia_reactiva_Fase_3 | 192.168.4.42:4660 | 56:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM44_General_normal.Frecuencia | 192.168.4.42:4660 | 56:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM44_General_normal.Energia_activa | 192.168.4.42:4660 | 56:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM44_General_normal.Energia_reactiva_inductiva | 192.168.4.42:4660 | 56:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM44_General_normal.Energia_reactiva_capacitiva | 192.168.4.42:4660 | 56:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM44_General_normal.Energia_aparente | 192.168.4.42:4660 | 56:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM44_General_normal.Potencia_activa_trifasica | 192.168.4.42:4660 | 56:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM44_General_normal.Potencia_inductiva_trifasica | 192.168.4.42:4660 | 56:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM44_General_normal.Potencia_capacitiva_trif | 192.168.4.42:4660 | 56:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM44_General_normal.cos_fi_trifasico | 192.168.4.42:4660 | 56:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM44_General_normal.Factor_de_potencia_trif | 192.168.4.42:4660 | 56:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM44_General_normal.Potencia_Aparente | 192.168.4.42:4660 | 56:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM44_General_normal.THD_V_Fase_1 | 192.168.4.42:4660 | 56:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM44_General_normal.THD_V_Fase_2 | 192.168.4.42:4660 | 56:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM44_General_normal.THD_V_Fase_3 | 192.168.4.42:4660 | 56:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM44_General_normal.THD_A_Fase_1 | 192.168.4.42:4660 | 56:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM44_General_normal.THD_A_Fase_2 | 192.168.4.42:4660 | 56:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM44_General_normal.THD_A_Fase_3 | 192.168.4.42:4660 | 56:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM44_General_normal.Tension_Fase_1_2 | 192.168.4.42:4660 | 56:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM44_General_normal.Tension_Fase_2_3 | 192.168.4.42:4660 | 56:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM44_General_normal.Tension_Fase_3_1 | 192.168.4.42:4660 | 56:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM43_General_normal.Tension_Fase_1_N | 192.168.4.42:4660 | 40:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM43_General_normal.Tension_Fase_2_N | 192.168.4.42:4660 | 40:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM43_General_normal.Tension_Fase_3_N | 192.168.4.42:4660 | 40:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM43_General_normal.Intensidad_Fase_1 | 192.168.4.42:4660 | 40:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM43_General_normal.Intensidad_Fase_2 | 192.168.4.42:4660 | 40:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM43_General_normal.Intensidad_Fase_3 | 192.168.4.42:4660 | 40:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM43_General_normal.Intensidad_Neutro | 192.168.4.42:4660 | 40:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM43_General_normal.Potencia_activa_Fase_1 | 192.168.4.42:4660 | 40:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM43_General_normal.Potencia_activa_Fase_2 | 192.168.4.42:4660 | 40:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM43_General_normal.Potencia_activa_Fase_3 | 192.168.4.42:4660 | 40:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM43_General_normal.Potencia_reactiva_Fase_1 | 192.168.4.42:4660 | 40:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM43_General_normal.Potencia_reactiva_Fase_2 | 192.168.4.42:4660 | 40:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM43_General_normal.Potencia_reactiva_Fase_3 | 192.168.4.42:4660 | 40:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM43_General_normal.Frecuencia | 192.168.4.42:4660 | 40:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM43_General_normal.Energia_activa | 192.168.4.42:4660 | 40:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM43_General_normal.Energia_reactiva_inductiva | 192.168.4.42:4660 | 40:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM43_General_normal.Energia_reactiva_capacitiva | 192.168.4.42:4660 | 40:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM43_General_normal.Energia_aparente | 192.168.4.42:4660 | 40:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM43_General_normal.Potencia_activa_trifasica | 192.168.4.42:4660 | 40:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM43_General_normal.Potencia_inductiva_trifasica | 192.168.4.42:4660 | 40:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM43_General_normal.Potencia_capacitiva_trif | 192.168.4.42:4660 | 40:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM43_General_normal.cos_fi_trifasico | 192.168.4.42:4660 | 40:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM43_General_normal.Factor_de_potencia_trif | 192.168.4.42:4660 | 40:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM43_General_normal.Potencia_Aparente | 192.168.4.42:4660 | 40:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM43_General_normal.THD_V_Fase_1 | 192.168.4.42:4660 | 40:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM43_General_normal.THD_V_Fase_2 | 192.168.4.42:4660 | 40:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM43_General_normal.THD_V_Fase_3 | 192.168.4.42:4660 | 40:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM43_General_normal.THD_A_Fase_1 | 192.168.4.42:4660 | 40:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM43_General_normal.THD_A_Fase_2 | 192.168.4.42:4660 | 40:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM43_General_normal.THD_A_Fase_3 | 192.168.4.42:4660 | 40:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM43_General_normal.Tension_Fase_1_2 | 192.168.4.42:4660 | 40:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM43_General_normal.Tension_Fase_2_3 | 192.168.4.42:4660 | 40:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM43_General_normal.Tension_Fase_3_1 | 192.168.4.42:4660 | 40:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM42_General_normal.Tension_Fase_1_N | 192.168.4.42:4660 | 37:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM42_General_normal.Tension_Fase_2_N | 192.168.4.42:4660 | 37:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM42_General_normal.Tension_Fase_3_N | 192.168.4.42:4660 | 37:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM42_General_normal.Intensidad_Fase_1 | 192.168.4.42:4660 | 37:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM42_General_normal.Intensidad_Fase_2 | 192.168.4.42:4660 | 37:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM42_General_normal.Intensidad_Fase_3 | 192.168.4.42:4660 | 37:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM42_General_normal.Intensidad_Neutro | 192.168.4.42:4660 | 37:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM42_General_normal.Potencia_activa_Fase_1 | 192.168.4.42:4660 | 37:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM42_General_normal.Potencia_activa_Fase_2 | 192.168.4.42:4660 | 37:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM42_General_normal.Potencia_activa_Fase_3 | 192.168.4.42:4660 | 37:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM42_General_normal.Potencia_reactiva_Fase_1 | 192.168.4.42:4660 | 37:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM42_General_normal.Potencia_reactiva_Fase_2 | 192.168.4.42:4660 | 37:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM42_General_normal.Potencia_reactiva_Fase_3 | 192.168.4.42:4660 | 37:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM42_General_normal.Frecuencia | 192.168.4.42:4660 | 37:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM42_General_normal.Energia_activa | 192.168.4.42:4660 | 37:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM42_General_normal.Energia_reactiva_inductiva | 192.168.4.42:4660 | 37:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM42_General_normal.Energia_reactiva_capacitiva | 192.168.4.42:4660 | 37:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM42_General_normal.Energia_aparente | 192.168.4.42:4660 | 37:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM42_General_normal.Potencia_activa_trifasica | 192.168.4.42:4660 | 37:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM42_General_normal.Potencia_inductiva_trifasica | 192.168.4.42:4660 | 37:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM42_General_normal.Potencia_capacitiva_trif | 192.168.4.42:4660 | 37:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM42_General_normal.cos_fi_trifasico | 192.168.4.42:4660 | 37:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM42_General_normal.Factor_de_potencia_trif | 192.168.4.42:4660 | 37:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM42_General_normal.Potencia_Aparente | 192.168.4.42:4660 | 37:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM42_General_normal.THD_V_Fase_1 | 192.168.4.42:4660 | 37:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM42_General_normal.THD_V_Fase_2 | 192.168.4.42:4660 | 37:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM42_General_normal.THD_V_Fase_3 | 192.168.4.42:4660 | 37:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM42_General_normal.THD_A_Fase_1 | 192.168.4.42:4660 | 37:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM42_General_normal.THD_A_Fase_2 | 192.168.4.42:4660 | 37:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM42_General_normal.THD_A_Fase_3 | 192.168.4.42:4660 | 37:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM42_General_normal.Tension_Fase_1_2 | 192.168.4.42:4660 | 37:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM42_General_normal.Tension_Fase_2_3 | 192.168.4.42:4660 | 37:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM42_General_normal.Tension_Fase_3_1 | 192.168.4.42:4660 | 37:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM41_General_normal.Tension_Fase_1_N | 192.168.4.42:4660 | 35:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM41_General_normal.Tension_Fase_2_N | 192.168.4.42:4660 | 35:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM41_General_normal.Tension_Fase_3_N | 192.168.4.42:4660 | 35:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM41_General_normal.Intensidad_Fase_1 | 192.168.4.42:4660 | 35:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM41_General_normal.Intensidad_Fase_2 | 192.168.4.42:4660 | 35:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM41_General_normal.Intensidad_Fase_3 | 192.168.4.42:4660 | 35:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM41_General_normal.Intensidad_Neutro | 192.168.4.42:4660 | 35:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM41_General_normal.Potencia_activa_Fase_1 | 192.168.4.42:4660 | 35:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM41_General_normal.Potencia_activa_Fase_2 | 192.168.4.42:4660 | 35:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM41_General_normal.Potencia_activa_Fase_3 | 192.168.4.42:4660 | 35:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM41_General_normal.Potencia_reactiva_Fase_1 | 192.168.4.42:4660 | 35:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM41_General_normal.Potencia_reactiva_Fase_2 | 192.168.4.42:4660 | 35:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM41_General_normal.Potencia_reactiva_Fase_3 | 192.168.4.42:4660 | 35:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM41_General_normal.Frecuencia | 192.168.4.42:4660 | 35:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM41_General_normal.Energia_activa | 192.168.4.42:4660 | 35:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM41_General_normal.Energia_reactiva_inductiva | 192.168.4.42:4660 | 35:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM41_General_normal.Energia_reactiva_capacitiva | 192.168.4.42:4660 | 35:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM41_General_normal.Energia_aparente | 192.168.4.42:4660 | 35:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM41_General_normal.Potencia_activa_trifasica | 192.168.4.42:4660 | 35:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM41_General_normal.Potencia_inductiva_trifasica | 192.168.4.42:4660 | 35:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM41_General_normal.Potencia_capacitiva_trif | 192.168.4.42:4660 | 35:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM41_General_normal.cos_fi_trifasico | 192.168.4.42:4660 | 35:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM41_General_normal.Factor_de_potencia_trif | 192.168.4.42:4660 | 35:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM41_General_normal.Potencia_Aparente | 192.168.4.42:4660 | 35:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM41_General_normal.THD_V_Fase_1 | 192.168.4.42:4660 | 35:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM41_General_normal.THD_V_Fase_2 | 192.168.4.42:4660 | 35:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM41_General_normal.THD_V_Fase_3 | 192.168.4.42:4660 | 35:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM41_General_normal.THD_A_Fase_1 | 192.168.4.42:4660 | 35:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM41_General_normal.THD_A_Fase_2 | 192.168.4.42:4660 | 35:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM41_General_normal.THD_A_Fase_3 | 192.168.4.42:4660 | 35:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM41_General_normal.Tension_Fase_1_2 | 192.168.4.42:4660 | 35:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM41_General_normal.Tension_Fase_2_3 | 192.168.4.42:4660 | 35:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM41_General_normal.Tension_Fase_3_1 | 192.168.4.42:4660 | 35:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM43_Alumbrado.Tension_Fase_1_N | 192.168.4.42:4660 | 41:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM43_Alumbrado.Tension_Fase_2_N | 192.168.4.42:4660 | 41:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM43_Alumbrado.Tension_Fase_3_N | 192.168.4.42:4660 | 41:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM43_Alumbrado.Intensidad_Fase_1 | 192.168.4.42:4660 | 41:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM43_Alumbrado.Intensidad_Fase_2 | 192.168.4.42:4660 | 41:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM43_Alumbrado.Intensidad_Fase_3 | 192.168.4.42:4660 | 41:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM43_Alumbrado.Intensidad_Neutro | 192.168.4.42:4660 | 41:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM43_Alumbrado.Potencia_activa_Fase_1 | 192.168.4.42:4660 | 41:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM43_Alumbrado.Potencia_activa_Fase_2 | 192.168.4.42:4660 | 41:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM43_Alumbrado.Potencia_activa_Fase_3 | 192.168.4.42:4660 | 41:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM43_Alumbrado.Potencia_reactiva_Fase_1 | 192.168.4.42:4660 | 41:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM43_Alumbrado.Potencia_reactiva_Fase_2 | 192.168.4.42:4660 | 41:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM43_Alumbrado.Potencia_reactiva_Fase_3 | 192.168.4.42:4660 | 41:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM43_Alumbrado.Frecuencia | 192.168.4.42:4660 | 41:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM43_Alumbrado.Energia_activa | 192.168.4.42:4660 | 41:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM43_Alumbrado.Energia_reactiva_inductiva | 192.168.4.42:4660 | 41:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM43_Alumbrado.Energia_reactiva_capacitiva | 192.168.4.42:4660 | 41:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM43_Alumbrado.Energia_aparente | 192.168.4.42:4660 | 41:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM43_Alumbrado.Potencia_activa_trifasica | 192.168.4.42:4660 | 41:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM43_Alumbrado.Potencia_inductiva_trifasica | 192.168.4.42:4660 | 41:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM43_Alumbrado.Potencia_capacitiva_trif | 192.168.4.42:4660 | 41:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM43_Alumbrado.cos_fi_trifasico | 192.168.4.42:4660 | 41:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM43_Alumbrado.Factor_de_potencia_trif | 192.168.4.42:4660 | 41:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM43_Alumbrado.Potencia_Aparente | 192.168.4.42:4660 | 41:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM43_Alumbrado.THD_V_Fase_1 | 192.168.4.42:4660 | 41:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM43_Alumbrado.THD_V_Fase_2 | 192.168.4.42:4660 | 41:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM43_Alumbrado.THD_V_Fase_3 | 192.168.4.42:4660 | 41:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM43_Alumbrado.THD_A_Fase_1 | 192.168.4.42:4660 | 41:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM43_Alumbrado.THD_A_Fase_2 | 192.168.4.42:4660 | 41:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM43_Alumbrado.THD_A_Fase_3 | 192.168.4.42:4660 | 41:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM43_Alumbrado.Tension_Fase_1_2 | 192.168.4.42:4660 | 41:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM43_Alumbrado.Tension_Fase_2_3 | 192.168.4.42:4660 | 41:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM43_Alumbrado.Tension_Fase_3_1 | 192.168.4.42:4660 | 41:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM42_Alumbrado.Tension_Fase_1_N | 192.168.4.42:4660 | 38:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM42_Alumbrado.Tension_Fase_2_N | 192.168.4.42:4660 | 38:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM42_Alumbrado.Tension_Fase_3_N | 192.168.4.42:4660 | 38:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM42_Alumbrado.Intensidad_Fase_1 | 192.168.4.42:4660 | 38:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM42_Alumbrado.Intensidad_Fase_2 | 192.168.4.42:4660 | 38:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM42_Alumbrado.Intensidad_Fase_3 | 192.168.4.42:4660 | 38:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM42_Alumbrado.Intensidad_Neutro | 192.168.4.42:4660 | 38:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM42_Alumbrado.Potencia_activa_Fase_1 | 192.168.4.42:4660 | 38:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM42_Alumbrado.Potencia_activa_Fase_2 | 192.168.4.42:4660 | 38:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM42_Alumbrado.Potencia_activa_Fase_3 | 192.168.4.42:4660 | 38:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM42_Alumbrado.Potencia_reactiva_Fase_1 | 192.168.4.42:4660 | 38:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM42_Alumbrado.Potencia_reactiva_Fase_2 | 192.168.4.42:4660 | 38:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM42_Alumbrado.Potencia_reactiva_Fase_3 | 192.168.4.42:4660 | 38:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM42_Alumbrado.Frecuencia | 192.168.4.42:4660 | 38:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM42_Alumbrado.Energia_activa | 192.168.4.42:4660 | 38:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM42_Alumbrado.Energia_reactiva_inductiva | 192.168.4.42:4660 | 38:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM42_Alumbrado.Energia_reactiva_capacitiva | 192.168.4.42:4660 | 38:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM42_Alumbrado.Energia_aparente | 192.168.4.42:4660 | 38:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM42_Alumbrado.Potencia_activa_trifasica | 192.168.4.42:4660 | 38:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM42_Alumbrado.Potencia_inductiva_trifasica | 192.168.4.42:4660 | 38:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM42_Alumbrado.Potencia_capacitiva_trif | 192.168.4.42:4660 | 38:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM42_Alumbrado.cos_fi_trifasico | 192.168.4.42:4660 | 38:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM42_Alumbrado.Factor_de_potencia_trif | 192.168.4.42:4660 | 38:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM42_Alumbrado.Potencia_Aparente | 192.168.4.42:4660 | 38:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM42_Alumbrado.THD_V_Fase_1 | 192.168.4.42:4660 | 38:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM42_Alumbrado.THD_V_Fase_2 | 192.168.4.42:4660 | 38:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM42_Alumbrado.THD_V_Fase_3 | 192.168.4.42:4660 | 38:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM42_Alumbrado.THD_A_Fase_1 | 192.168.4.42:4660 | 38:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM42_Alumbrado.THD_A_Fase_2 | 192.168.4.42:4660 | 38:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM42_Alumbrado.THD_A_Fase_3 | 192.168.4.42:4660 | 38:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM42_Alumbrado.Tension_Fase_1_2 | 192.168.4.42:4660 | 38:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM42_Alumbrado.Tension_Fase_2_3 | 192.168.4.42:4660 | 38:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM42_Alumbrado.Tension_Fase_3_1 | 192.168.4.42:4660 | 38:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM40_Alumbrado.Tension_Fase_1_N | 192.168.4.42:4660 | 33:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM40_Alumbrado.Tension_Fase_2_N | 192.168.4.42:4660 | 33:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM40_Alumbrado.Tension_Fase_3_N | 192.168.4.42:4660 | 33:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM40_Alumbrado.Intensidad_Fase_1 | 192.168.4.42:4660 | 33:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM40_Alumbrado.Intensidad_Fase_2 | 192.168.4.42:4660 | 33:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM40_Alumbrado.Intensidad_Fase_3 | 192.168.4.42:4660 | 33:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM40_Alumbrado.Intensidad_Neutro | 192.168.4.42:4660 | 33:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM40_Alumbrado.Potencia_activa_Fase_1 | 192.168.4.42:4660 | 33:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM40_Alumbrado.Potencia_activa_Fase_2 | 192.168.4.42:4660 | 33:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM40_Alumbrado.Potencia_activa_Fase_3 | 192.168.4.42:4660 | 33:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM40_Alumbrado.Potencia_reactiva_Fase_1 | 192.168.4.42:4660 | 33:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM40_Alumbrado.Potencia_reactiva_Fase_2 | 192.168.4.42:4660 | 33:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM40_Alumbrado.Potencia_reactiva_Fase_3 | 192.168.4.42:4660 | 33:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM40_Alumbrado.Frecuencia | 192.168.4.42:4660 | 33:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM40_Alumbrado.Energia_activa | 192.168.4.42:4660 | 33:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM40_Alumbrado.Energia_reactiva_inductiva | 192.168.4.42:4660 | 33:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM40_Alumbrado.Energia_reactiva_capacitiva | 192.168.4.42:4660 | 33:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM40_Alumbrado.Energia_aparente | 192.168.4.42:4660 | 33:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM40_Alumbrado.Potencia_activa_trifasica | 192.168.4.42:4660 | 33:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM40_Alumbrado.Potencia_inductiva_trifasica | 192.168.4.42:4660 | 33:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM40_Alumbrado.Potencia_capacitiva_trif | 192.168.4.42:4660 | 33:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM40_Alumbrado.cos_fi_trifasico | 192.168.4.42:4660 | 33:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM40_Alumbrado.Factor_de_potencia_trif | 192.168.4.42:4660 | 33:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM40_Alumbrado.Potencia_Aparente | 192.168.4.42:4660 | 33:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM40_Alumbrado.THD_V_Fase_1 | 192.168.4.42:4660 | 33:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM40_Alumbrado.THD_V_Fase_2 | 192.168.4.42:4660 | 33:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM40_Alumbrado.THD_V_Fase_3 | 192.168.4.42:4660 | 33:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM40_Alumbrado.THD_A_Fase_1 | 192.168.4.42:4660 | 33:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM40_Alumbrado.THD_A_Fase_2 | 192.168.4.42:4660 | 33:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM40_Alumbrado.THD_A_Fase_3 | 192.168.4.42:4660 | 33:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM40_Alumbrado.Tension_Fase_1_2 | 192.168.4.42:4660 | 33:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM40_Alumbrado.Tension_Fase_2_3 | 192.168.4.42:4660 | 33:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM40_Alumbrado.Tension_Fase_3_1 | 192.168.4.42:4660 | 33:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM43_Clima_vent.Tension_Fase_1_N | 192.168.4.42:4660 | 42:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM43_Clima_vent.Tension_Fase_2_N | 192.168.4.42:4660 | 42:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM43_Clima_vent.Tension_Fase_3_N | 192.168.4.42:4660 | 42:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM43_Clima_vent.Intensidad_Fase_1 | 192.168.4.42:4660 | 42:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM43_Clima_vent.Intensidad_Fase_2 | 192.168.4.42:4660 | 42:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM43_Clima_vent.Intensidad_Fase_3 | 192.168.4.42:4660 | 42:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM43_Clima_vent.Intensidad_Neutro | 192.168.4.42:4660 | 42:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM43_Clima_vent.Potencia_activa_Fase_1 | 192.168.4.42:4660 | 42:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM43_Clima_vent.Potencia_activa_Fase_2 | 192.168.4.42:4660 | 42:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM43_Clima_vent.Potencia_activa_Fase_3 | 192.168.4.42:4660 | 42:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM43_Clima_vent.Potencia_reactiva_Fase_1 | 192.168.4.42:4660 | 42:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM43_Clima_vent.Potencia_reactiva_Fase_2 | 192.168.4.42:4660 | 42:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM43_Clima_vent.Potencia_reactiva_Fase_3 | 192.168.4.42:4660 | 42:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM43_Clima_vent.Frecuencia | 192.168.4.42:4660 | 42:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM43_Clima_vent.Energia_activa | 192.168.4.42:4660 | 42:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM43_Clima_vent.Energia_reactiva_inductiva | 192.168.4.42:4660 | 42:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM43_Clima_vent.Energia_reactiva_capacitiva | 192.168.4.42:4660 | 42:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM43_Clima_vent.Energia_aparente | 192.168.4.42:4660 | 42:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM43_Clima_vent.Potencia_activa_trifasica | 192.168.4.42:4660 | 42:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM43_Clima_vent.Potencia_inductiva_trifasica | 192.168.4.42:4660 | 42:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM43_Clima_vent.Potencia_capacitiva_trif | 192.168.4.42:4660 | 42:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM43_Clima_vent.cos_fi_trifasico | 192.168.4.42:4660 | 42:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM43_Clima_vent.Factor_de_potencia_trif | 192.168.4.42:4660 | 42:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM43_Clima_vent.Potencia_Aparente | 192.168.4.42:4660 | 42:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM43_Clima_vent.THD_V_Fase_1 | 192.168.4.42:4660 | 42:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM43_Clima_vent.THD_V_Fase_2 | 192.168.4.42:4660 | 42:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM43_Clima_vent.THD_V_Fase_3 | 192.168.4.42:4660 | 42:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM43_Clima_vent.THD_A_Fase_1 | 192.168.4.42:4660 | 42:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM43_Clima_vent.THD_A_Fase_2 | 192.168.4.42:4660 | 42:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM43_Clima_vent.THD_A_Fase_3 | 192.168.4.42:4660 | 42:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM43_Clima_vent.Tension_Fase_1_2 | 192.168.4.42:4660 | 42:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM43_Clima_vent.Tension_Fase_2_3 | 192.168.4.42:4660 | 42:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM43_Clima_vent.Tension_Fase_3_1 | 192.168.4.42:4660 | 42:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM42_Clima_vent.Tension_Fase_1_N | 192.168.4.42:4660 | 39:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM42_Clima_vent.Tension_Fase_2_N | 192.168.4.42:4660 | 39:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM42_Clima_vent.Tension_Fase_3_N | 192.168.4.42:4660 | 39:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM42_Clima_vent.Intensidad_Fase_1 | 192.168.4.42:4660 | 39:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM42_Clima_vent.Intensidad_Fase_2 | 192.168.4.42:4660 | 39:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM42_Clima_vent.Intensidad_Fase_3 | 192.168.4.42:4660 | 39:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM42_Clima_vent.Intensidad_Neutro | 192.168.4.42:4660 | 39:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM42_Clima_vent.Potencia_activa_Fase_1 | 192.168.4.42:4660 | 39:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM42_Clima_vent.Potencia_activa_Fase_2 | 192.168.4.42:4660 | 39:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM42_Clima_vent.Potencia_activa_Fase_3 | 192.168.4.42:4660 | 39:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM42_Clima_vent.Potencia_reactiva_Fase_1 | 192.168.4.42:4660 | 39:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM42_Clima_vent.Potencia_reactiva_Fase_2 | 192.168.4.42:4660 | 39:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM42_Clima_vent.Potencia_reactiva_Fase_3 | 192.168.4.42:4660 | 39:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM42_Clima_vent.Frecuencia | 192.168.4.42:4660 | 39:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM42_Clima_vent.Energia_activa | 192.168.4.42:4660 | 39:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM42_Clima_vent.Energia_reactiva_inductiva | 192.168.4.42:4660 | 39:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM42_Clima_vent.Energia_reactiva_capacitiva | 192.168.4.42:4660 | 39:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM42_Clima_vent.Energia_aparente | 192.168.4.42:4660 | 39:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM42_Clima_vent.Potencia_activa_trifasica | 192.168.4.42:4660 | 39:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM42_Clima_vent.Potencia_inductiva_trifasica | 192.168.4.42:4660 | 39:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM42_Clima_vent.Potencia_capacitiva_trif | 192.168.4.42:4660 | 39:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM42_Clima_vent.cos_fi_trifasico | 192.168.4.42:4660 | 39:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM42_Clima_vent.Factor_de_potencia_trif | 192.168.4.42:4660 | 39:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM42_Clima_vent.Potencia_Aparente | 192.168.4.42:4660 | 39:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM42_Clima_vent.THD_V_Fase_1 | 192.168.4.42:4660 | 39:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM42_Clima_vent.THD_V_Fase_2 | 192.168.4.42:4660 | 39:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM42_Clima_vent.THD_V_Fase_3 | 192.168.4.42:4660 | 39:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM42_Clima_vent.THD_A_Fase_1 | 192.168.4.42:4660 | 39:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM42_Clima_vent.THD_A_Fase_2 | 192.168.4.42:4660 | 39:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM42_Clima_vent.THD_A_Fase_3 | 192.168.4.42:4660 | 39:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM42_Clima_vent.Tension_Fase_1_2 | 192.168.4.42:4660 | 39:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM42_Clima_vent.Tension_Fase_2_3 | 192.168.4.42:4660 | 39:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM42_Clima_vent.Tension_Fase_3_1 | 192.168.4.42:4660 | 39:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM41_Clima_vent.Tension_Fase_1_N | 192.168.4.42:4660 | 36:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM41_Clima_vent.Tension_Fase_2_N | 192.168.4.42:4660 | 36:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM41_Clima_vent.Tension_Fase_3_N | 192.168.4.42:4660 | 36:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM41_Clima_vent.Intensidad_Fase_1 | 192.168.4.42:4660 | 36:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM41_Clima_vent.Intensidad_Fase_2 | 192.168.4.42:4660 | 36:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM41_Clima_vent.Intensidad_Fase_3 | 192.168.4.42:4660 | 36:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM41_Clima_vent.Intensidad_Neutro | 192.168.4.42:4660 | 36:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM41_Clima_vent.Potencia_activa_Fase_1 | 192.168.4.42:4660 | 36:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM41_Clima_vent.Potencia_activa_Fase_2 | 192.168.4.42:4660 | 36:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM41_Clima_vent.Potencia_activa_Fase_3 | 192.168.4.42:4660 | 36:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM41_Clima_vent.Potencia_reactiva_Fase_1 | 192.168.4.42:4660 | 36:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM41_Clima_vent.Potencia_reactiva_Fase_2 | 192.168.4.42:4660 | 36:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM41_Clima_vent.Potencia_reactiva_Fase_3 | 192.168.4.42:4660 | 36:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM41_Clima_vent.Frecuencia | 192.168.4.42:4660 | 36:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM41_Clima_vent.Energia_activa | 192.168.4.42:4660 | 36:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM41_Clima_vent.Energia_reactiva_inductiva | 192.168.4.42:4660 | 36:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM41_Clima_vent.Energia_reactiva_capacitiva | 192.168.4.42:4660 | 36:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM41_Clima_vent.Energia_aparente | 192.168.4.42:4660 | 36:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM41_Clima_vent.Potencia_activa_trifasica | 192.168.4.42:4660 | 36:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM41_Clima_vent.Potencia_inductiva_trifasica | 192.168.4.42:4660 | 36:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM41_Clima_vent.Potencia_capacitiva_trif | 192.168.4.42:4660 | 36:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM41_Clima_vent.cos_fi_trifasico | 192.168.4.42:4660 | 36:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM41_Clima_vent.Factor_de_potencia_trif | 192.168.4.42:4660 | 36:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM41_Clima_vent.Potencia_Aparente | 192.168.4.42:4660 | 36:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM41_Clima_vent.THD_V_Fase_1 | 192.168.4.42:4660 | 36:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM41_Clima_vent.THD_V_Fase_2 | 192.168.4.42:4660 | 36:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM41_Clima_vent.THD_V_Fase_3 | 192.168.4.42:4660 | 36:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM41_Clima_vent.THD_A_Fase_1 | 192.168.4.42:4660 | 36:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM41_Clima_vent.THD_A_Fase_2 | 192.168.4.42:4660 | 36:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM41_Clima_vent.THD_A_Fase_3 | 192.168.4.42:4660 | 36:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM41_Clima_vent.Tension_Fase_1_2 | 192.168.4.42:4660 | 36:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM41_Clima_vent.Tension_Fase_2_3 | 192.168.4.42:4660 | 36:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM41_Clima_vent.Tension_Fase_3_1 | 192.168.4.42:4660 | 36:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM40_Clima_vent.Tension_Fase_1_N | 192.168.4.42:4660 | 34:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM40_Clima_vent.Tension_Fase_2_N | 192.168.4.42:4660 | 34:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM40_Clima_vent.Tension_Fase_3_N | 192.168.4.42:4660 | 34:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM40_Clima_vent.Intensidad_Fase_1 | 192.168.4.42:4660 | 34:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM40_Clima_vent.Intensidad_Fase_2 | 192.168.4.42:4660 | 34:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM40_Clima_vent.Intensidad_Fase_3 | 192.168.4.42:4660 | 34:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM40_Clima_vent.Intensidad_Neutro | 192.168.4.42:4660 | 34:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM40_Clima_vent.Potencia_activa_Fase_1 | 192.168.4.42:4660 | 34:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM40_Clima_vent.Potencia_activa_Fase_2 | 192.168.4.42:4660 | 34:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM40_Clima_vent.Potencia_activa_Fase_3 | 192.168.4.42:4660 | 34:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM40_Clima_vent.Potencia_reactiva_Fase_1 | 192.168.4.42:4660 | 34:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM40_Clima_vent.Potencia_reactiva_Fase_2 | 192.168.4.42:4660 | 34:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM40_Clima_vent.Potencia_reactiva_Fase_3 | 192.168.4.42:4660 | 34:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM40_Clima_vent.Frecuencia | 192.168.4.42:4660 | 34:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM40_Clima_vent.Energia_activa | 192.168.4.42:4660 | 34:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM40_Clima_vent.Energia_reactiva_inductiva | 192.168.4.42:4660 | 34:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM40_Clima_vent.Energia_reactiva_capacitiva | 192.168.4.42:4660 | 34:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM40_Clima_vent.Energia_aparente | 192.168.4.42:4660 | 34:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM40_Clima_vent.Potencia_activa_trifasica | 192.168.4.42:4660 | 34:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM40_Clima_vent.Potencia_inductiva_trifasica | 192.168.4.42:4660 | 34:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM40_Clima_vent.Potencia_capacitiva_trif | 192.168.4.42:4660 | 34:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM40_Clima_vent.cos_fi_trifasico | 192.168.4.42:4660 | 34:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM40_Clima_vent.Factor_de_potencia_trif | 192.168.4.42:4660 | 34:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM40_Clima_vent.Potencia_Aparente | 192.168.4.42:4660 | 34:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM40_Clima_vent.THD_V_Fase_1 | 192.168.4.42:4660 | 34:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM40_Clima_vent.THD_V_Fase_2 | 192.168.4.42:4660 | 34:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM40_Clima_vent.THD_V_Fase_3 | 192.168.4.42:4660 | 34:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM40_Clima_vent.THD_A_Fase_1 | 192.168.4.42:4660 | 34:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM40_Clima_vent.THD_A_Fase_2 | 192.168.4.42:4660 | 34:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM40_Clima_vent.THD_A_Fase_3 | 192.168.4.42:4660 | 34:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM40_Clima_vent.Tension_Fase_1_2 | 192.168.4.42:4660 | 34:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM40_Clima_vent.Tension_Fase_2_3 | 192.168.4.42:4660 | 34:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM40_Clima_vent.Tension_Fase_3_1 | 192.168.4.42:4660 | 34:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM50_Pergolas_Urgell.Tension_Fase_1_N | 192.168.4.52:4660 | 55:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM50_Pergolas_Urgell.Tension_Fase_2_N | 192.168.4.52:4660 | 55:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM50_Pergolas_Urgell.Tension_Fase_3_N | 192.168.4.52:4660 | 55:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM50_Pergolas_Urgell.Intensidad_Fase_1 | 192.168.4.52:4660 | 55:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM50_Pergolas_Urgell.Intensidad_Fase_2 | 192.168.4.52:4660 | 55:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM50_Pergolas_Urgell.Intensidad_Fase_3 | 192.168.4.52:4660 | 55:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM50_Pergolas_Urgell.Intensidad_Neutro | 192.168.4.52:4660 | 55:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM50_Pergolas_Urgell.Potencia_activa_Fase_1 | 192.168.4.52:4660 | 55:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM50_Pergolas_Urgell.Potencia_activa_Fase_2 | 192.168.4.52:4660 | 55:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM50_Pergolas_Urgell.Potencia_activa_Fase_3 | 192.168.4.52:4660 | 55:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM50_Pergolas_Urgell.Potencia_reactiva_Fase_1 | 192.168.4.52:4660 | 55:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM50_Pergolas_Urgell.Potencia_reactiva_Fase_2 | 192.168.4.52:4660 | 55:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM50_Pergolas_Urgell.Potencia_reactiva_Fase_3 | 192.168.4.52:4660 | 55:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM50_Pergolas_Urgell.Frecuencia | 192.168.4.52:4660 | 55:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM50_Pergolas_Urgell.Energia_activa | 192.168.4.52:4660 | 55:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM50_Pergolas_Urgell.Energia_reactiva_inductiva | 192.168.4.52:4660 | 55:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM50_Pergolas_Urgell.Energia_reactiva_capacitiva | 192.168.4.52:4660 | 55:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM50_Pergolas_Urgell.Energia_aparente | 192.168.4.52:4660 | 55:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM50_Pergolas_Urgell.Potencia_activa_trifasica | 192.168.4.52:4660 | 55:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM50_Pergolas_Urgell.Potencia_inductiva_trifasica | 192.168.4.52:4660 | 55:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM50_Pergolas_Urgell.Potencia_capacitiva_trif | 192.168.4.52:4660 | 55:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM50_Pergolas_Urgell.cos_fi_trifasico | 192.168.4.52:4660 | 55:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM50_Pergolas_Urgell.Factor_de_potencia_trif | 192.168.4.52:4660 | 55:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM50_Pergolas_Urgell.Potencia_Aparente | 192.168.4.52:4660 | 55:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM50_Pergolas_Urgell.THD_V_Fase_1 | 192.168.4.52:4660 | 55:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM50_Pergolas_Urgell.THD_V_Fase_2 | 192.168.4.52:4660 | 55:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM50_Pergolas_Urgell.THD_V_Fase_3 | 192.168.4.52:4660 | 55:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM50_Pergolas_Urgell.THD_A_Fase_1 | 192.168.4.52:4660 | 55:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM50_Pergolas_Urgell.THD_A_Fase_2 | 192.168.4.52:4660 | 55:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM50_Pergolas_Urgell.THD_A_Fase_3 | 192.168.4.52:4660 | 55:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM50_Pergolas_Urgell.Tension_Fase_1_2 | 192.168.4.52:4660 | 55:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM50_Pergolas_Urgell.Tension_Fase_2_3 | 192.168.4.52:4660 | 55:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM50_Pergolas_Urgell.Tension_Fase_3_1 | 192.168.4.52:4660 | 55:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM54_General_normal.Tension_Fase_1_N | 192.168.4.52:4660 | 51:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM54_General_normal.Tension_Fase_2_N | 192.168.4.52:4660 | 51:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM54_General_normal.Tension_Fase_3_N | 192.168.4.52:4660 | 51:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM54_General_normal.Intensidad_Fase_1 | 192.168.4.52:4660 | 51:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM54_General_normal.Intensidad_Fase_2 | 192.168.4.52:4660 | 51:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM54_General_normal.Intensidad_Fase_3 | 192.168.4.52:4660 | 51:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM54_General_normal.Intensidad_Neutro | 192.168.4.52:4660 | 51:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM54_General_normal.Potencia_activa_Fase_1 | 192.168.4.52:4660 | 51:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM54_General_normal.Potencia_activa_Fase_2 | 192.168.4.52:4660 | 51:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM54_General_normal.Potencia_activa_Fase_3 | 192.168.4.52:4660 | 51:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM54_General_normal.Potencia_reactiva_Fase_1 | 192.168.4.52:4660 | 51:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM54_General_normal.Potencia_reactiva_Fase_2 | 192.168.4.52:4660 | 51:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM54_General_normal.Potencia_reactiva_Fase_3 | 192.168.4.52:4660 | 51:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM54_General_normal.Frecuencia | 192.168.4.52:4660 | 51:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM54_General_normal.Energia_activa | 192.168.4.52:4660 | 51:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM54_General_normal.Energia_reactiva_inductiva | 192.168.4.52:4660 | 51:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM54_General_normal.Energia_reactiva_capacitiva | 192.168.4.52:4660 | 51:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM54_General_normal.Energia_aparente | 192.168.4.52:4660 | 51:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM54_General_normal.Potencia_activa_trifasica | 192.168.4.52:4660 | 51:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM54_General_normal.Potencia_inductiva_trifasica | 192.168.4.52:4660 | 51:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM54_General_normal.Potencia_capacitiva_trif | 192.168.4.52:4660 | 51:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM54_General_normal.cos_fi_trifasico | 192.168.4.52:4660 | 51:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM54_General_normal.Factor_de_potencia_trif | 192.168.4.52:4660 | 51:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM54_General_normal.Potencia_Aparente | 192.168.4.52:4660 | 51:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM54_General_normal.THD_V_Fase_1 | 192.168.4.52:4660 | 51:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM54_General_normal.THD_V_Fase_2 | 192.168.4.52:4660 | 51:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM54_General_normal.THD_V_Fase_3 | 192.168.4.52:4660 | 51:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM54_General_normal.THD_A_Fase_1 | 192.168.4.52:4660 | 51:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM54_General_normal.THD_A_Fase_2 | 192.168.4.52:4660 | 51:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM54_General_normal.THD_A_Fase_3 | 192.168.4.52:4660 | 51:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM54_General_normal.Tension_Fase_1_2 | 192.168.4.52:4660 | 51:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM54_General_normal.Tension_Fase_2_3 | 192.168.4.52:4660 | 51:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM54_General_normal.Tension_Fase_3_1 | 192.168.4.52:4660 | 51:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM53_General_normal.Tension_Fase_1_N | 192.168.4.52:4660 | 48:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM53_General_normal.Tension_Fase_2_N | 192.168.4.52:4660 | 48:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM53_General_normal.Tension_Fase_3_N | 192.168.4.52:4660 | 48:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM53_General_normal.Intensidad_Fase_1 | 192.168.4.52:4660 | 48:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM53_General_normal.Intensidad_Fase_2 | 192.168.4.52:4660 | 48:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM53_General_normal.Intensidad_Fase_3 | 192.168.4.52:4660 | 48:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM53_General_normal.Intensidad_Neutro | 192.168.4.52:4660 | 48:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM53_General_normal.Potencia_activa_Fase_1 | 192.168.4.52:4660 | 48:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM53_General_normal.Potencia_activa_Fase_2 | 192.168.4.52:4660 | 48:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM53_General_normal.Potencia_activa_Fase_3 | 192.168.4.52:4660 | 48:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM53_General_normal.Potencia_reactiva_Fase_1 | 192.168.4.52:4660 | 48:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM53_General_normal.Potencia_reactiva_Fase_2 | 192.168.4.52:4660 | 48:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM53_General_normal.Potencia_reactiva_Fase_3 | 192.168.4.52:4660 | 48:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM53_General_normal.Frecuencia | 192.168.4.52:4660 | 48:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM53_General_normal.Energia_activa | 192.168.4.52:4660 | 48:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM53_General_normal.Energia_reactiva_inductiva | 192.168.4.52:4660 | 48:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM53_General_normal.Energia_reactiva_capacitiva | 192.168.4.52:4660 | 48:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM53_General_normal.Energia_aparente | 192.168.4.52:4660 | 48:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM53_General_normal.Potencia_activa_trifasica | 192.168.4.52:4660 | 48:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM53_General_normal.Potencia_inductiva_trifasica | 192.168.4.52:4660 | 48:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM53_General_normal.Potencia_capacitiva_trif | 192.168.4.52:4660 | 48:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM53_General_normal.cos_fi_trifasico | 192.168.4.52:4660 | 48:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM53_General_normal.Factor_de_potencia_trif | 192.168.4.52:4660 | 48:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM53_General_normal.Potencia_Aparente | 192.168.4.52:4660 | 48:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM53_General_normal.THD_V_Fase_1 | 192.168.4.52:4660 | 48:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM53_General_normal.THD_V_Fase_2 | 192.168.4.52:4660 | 48:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM53_General_normal.THD_V_Fase_3 | 192.168.4.52:4660 | 48:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM53_General_normal.THD_A_Fase_1 | 192.168.4.52:4660 | 48:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM53_General_normal.THD_A_Fase_2 | 192.168.4.52:4660 | 48:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM53_General_normal.THD_A_Fase_3 | 192.168.4.52:4660 | 48:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM53_General_normal.Tension_Fase_1_2 | 192.168.4.52:4660 | 48:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM53_General_normal.Tension_Fase_2_3 | 192.168.4.52:4660 | 48:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM53_General_normal.Tension_Fase_3_1 | 192.168.4.52:4660 | 48:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM13_General_normal.Tension_Fase_1_N | 192.168.4.52:4660 | 5:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM13_General_normal.Tension_Fase_2_N | 192.168.4.52:4660 | 5:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM13_General_normal.Tension_Fase_3_N | 192.168.4.52:4660 | 5:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM13_General_normal.Intensidad_Fase_1 | 192.168.4.52:4660 | 5:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM13_General_normal.Intensidad_Fase_2 | 192.168.4.52:4660 | 5:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM13_General_normal.Intensidad_Fase_3 | 192.168.4.52:4660 | 5:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM13_General_normal.Intensidad_Neutro | 192.168.4.52:4660 | 5:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM13_General_normal.Potencia_activa_Fase_1 | 192.168.4.52:4660 | 5:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM13_General_normal.Potencia_activa_Fase_2 | 192.168.4.52:4660 | 5:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM13_General_normal.Potencia_activa_Fase_3 | 192.168.4.52:4660 | 5:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM13_General_normal.Potencia_reactiva_Fase_1 | 192.168.4.52:4660 | 5:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM13_General_normal.Potencia_reactiva_Fase_2 | 192.168.4.52:4660 | 5:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM13_General_normal.Potencia_reactiva_Fase_3 | 192.168.4.52:4660 | 5:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM13_General_normal.Frecuencia | 192.168.4.52:4660 | 5:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM13_General_normal.Energia_activa | 192.168.4.52:4660 | 5:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM13_General_normal.Energia_reactiva_inductiva | 192.168.4.52:4660 | 5:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM13_General_normal.Energia_reactiva_capacitiva | 192.168.4.52:4660 | 5:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM13_General_normal.Energia_aparente | 192.168.4.52:4660 | 5:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM13_General_normal.Potencia_activa_trifasica | 192.168.4.52:4660 | 5:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM13_General_normal.Potencia_inductiva_trifasica | 192.168.4.52:4660 | 5:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM13_General_normal.Potencia_capacitiva_trif | 192.168.4.52:4660 | 5:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM13_General_normal.cos_fi_trifasico | 192.168.4.52:4660 | 5:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM13_General_normal.Factor_de_potencia_trif | 192.168.4.52:4660 | 5:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM13_General_normal.Potencia_Aparente | 192.168.4.52:4660 | 5:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM13_General_normal.THD_V_Fase_1 | 192.168.4.52:4660 | 5:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM13_General_normal.THD_V_Fase_2 | 192.168.4.52:4660 | 5:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM13_General_normal.THD_V_Fase_3 | 192.168.4.52:4660 | 5:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM13_General_normal.THD_A_Fase_1 | 192.168.4.52:4660 | 5:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM13_General_normal.THD_A_Fase_2 | 192.168.4.52:4660 | 5:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM13_General_normal.THD_A_Fase_3 | 192.168.4.52:4660 | 5:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM13_General_normal.Tension_Fase_1_2 | 192.168.4.52:4660 | 5:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM13_General_normal.Tension_Fase_2_3 | 192.168.4.52:4660 | 5:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM13_General_normal.Tension_Fase_3_1 | 192.168.4.52:4660 | 5:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM51_General_normal.Tension_Fase_1_N | 192.168.4.52:4660 | 45:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM51_General_normal.Tension_Fase_2_N | 192.168.4.52:4660 | 45:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM51_General_normal.Tension_Fase_3_N | 192.168.4.52:4660 | 45:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM51_General_normal.Intensidad_Fase_1 | 192.168.4.52:4660 | 45:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM51_General_normal.Intensidad_Fase_2 | 192.168.4.52:4660 | 45:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM51_General_normal.Intensidad_Fase_3 | 192.168.4.52:4660 | 45:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM51_General_normal.Intensidad_Neutro | 192.168.4.52:4660 | 45:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM51_General_normal.Potencia_activa_Fase_1 | 192.168.4.52:4660 | 45:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM51_General_normal.Potencia_activa_Fase_2 | 192.168.4.52:4660 | 45:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM51_General_normal.Potencia_activa_Fase_3 | 192.168.4.52:4660 | 45:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM51_General_normal.Potencia_reactiva_Fase_1 | 192.168.4.52:4660 | 45:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM51_General_normal.Potencia_reactiva_Fase_2 | 192.168.4.52:4660 | 45:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM51_General_normal.Potencia_reactiva_Fase_3 | 192.168.4.52:4660 | 45:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM51_General_normal.Frecuencia | 192.168.4.52:4660 | 45:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM51_General_normal.Energia_activa | 192.168.4.52:4660 | 45:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM51_General_normal.Energia_reactiva_inductiva | 192.168.4.52:4660 | 45:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM51_General_normal.Energia_reactiva_capacitiva | 192.168.4.52:4660 | 45:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM51_General_normal.Energia_aparente | 192.168.4.52:4660 | 45:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM51_General_normal.Potencia_activa_trifasica | 192.168.4.52:4660 | 45:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM51_General_normal.Potencia_inductiva_trifasica | 192.168.4.52:4660 | 45:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM51_General_normal.Potencia_capacitiva_trif | 192.168.4.52:4660 | 45:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM51_General_normal.cos_fi_trifasico | 192.168.4.52:4660 | 45:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM51_General_normal.Factor_de_potencia_trif | 192.168.4.52:4660 | 45:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM51_General_normal.Potencia_Aparente | 192.168.4.52:4660 | 45:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM51_General_normal.THD_V_Fase_1 | 192.168.4.52:4660 | 45:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM51_General_normal.THD_V_Fase_2 | 192.168.4.52:4660 | 45:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM51_General_normal.THD_V_Fase_3 | 192.168.4.52:4660 | 45:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM51_General_normal.THD_A_Fase_1 | 192.168.4.52:4660 | 45:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM51_General_normal.THD_A_Fase_2 | 192.168.4.52:4660 | 45:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM51_General_normal.THD_A_Fase_3 | 192.168.4.52:4660 | 45:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM51_General_normal.Tension_Fase_1_2 | 192.168.4.52:4660 | 45:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM51_General_normal.Tension_Fase_2_3 | 192.168.4.52:4660 | 45:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM51_General_normal.Tension_Fase_3_1 | 192.168.4.52:4660 | 45:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM15_General_normal.Tension_Fase_1_N | 192.168.4.52:4660 | 9:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM15_General_normal.Tension_Fase_2_N | 192.168.4.52:4660 | 9:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM15_General_normal.Tension_Fase_3_N | 192.168.4.52:4660 | 9:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM15_General_normal.Intensidad_Fase_1 | 192.168.4.52:4660 | 9:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM15_General_normal.Intensidad_Fase_2 | 192.168.4.52:4660 | 9:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM15_General_normal.Intensidad_Fase_3 | 192.168.4.52:4660 | 9:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM15_General_normal.Intensidad_Neutro | 192.168.4.52:4660 | 9:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM15_General_normal.Potencia_activa_Fase_1 | 192.168.4.52:4660 | 9:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM15_General_normal.Potencia_activa_Fase_2 | 192.168.4.52:4660 | 9:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM15_General_normal.Potencia_activa_Fase_3 | 192.168.4.52:4660 | 9:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM15_General_normal.Potencia_reactiva_Fase_1 | 192.168.4.52:4660 | 9:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM15_General_normal.Potencia_reactiva_Fase_2 | 192.168.4.52:4660 | 9:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM15_General_normal.Potencia_reactiva_Fase_3 | 192.168.4.52:4660 | 9:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM15_General_normal.Frecuencia | 192.168.4.52:4660 | 9:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM15_General_normal.Energia_activa | 192.168.4.52:4660 | 9:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM15_General_normal.Energia_reactiva_inductiva | 192.168.4.52:4660 | 9:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM15_General_normal.Energia_reactiva_capacitiva | 192.168.4.52:4660 | 9:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM15_General_normal.Energia_aparente | 192.168.4.52:4660 | 9:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM15_General_normal.Potencia_activa_trifasica | 192.168.4.52:4660 | 9:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM15_General_normal.Potencia_inductiva_trifasica | 192.168.4.52:4660 | 9:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM15_General_normal.Potencia_capacitiva_trif | 192.168.4.52:4660 | 9:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM15_General_normal.cos_fi_trifasico | 192.168.4.52:4660 | 9:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM15_General_normal.Factor_de_potencia_trif | 192.168.4.52:4660 | 9:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM15_General_normal.Potencia_Aparente | 192.168.4.52:4660 | 9:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM15_General_normal.THD_V_Fase_1 | 192.168.4.52:4660 | 9:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM15_General_normal.THD_V_Fase_2 | 192.168.4.52:4660 | 9:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM15_General_normal.THD_V_Fase_3 | 192.168.4.52:4660 | 9:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM15_General_normal.THD_A_Fase_1 | 192.168.4.52:4660 | 9:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM15_General_normal.THD_A_Fase_2 | 192.168.4.52:4660 | 9:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM15_General_normal.THD_A_Fase_3 | 192.168.4.52:4660 | 9:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM15_General_normal.Tension_Fase_1_2 | 192.168.4.52:4660 | 9:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM15_General_normal.Tension_Fase_2_3 | 192.168.4.52:4660 | 9:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM15_General_normal.Tension_Fase_3_1 | 192.168.4.52:4660 | 9:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM14_General_normal.Tension_Fase_1_N | 192.168.4.52:4660 | 6:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM14_General_normal.Tension_Fase_2_N | 192.168.4.52:4660 | 6:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM14_General_normal.Tension_Fase_3_N | 192.168.4.52:4660 | 6:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM14_General_normal.Intensidad_Fase_1 | 192.168.4.52:4660 | 6:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM14_General_normal.Intensidad_Fase_2 | 192.168.4.52:4660 | 6:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM14_General_normal.Intensidad_Fase_3 | 192.168.4.52:4660 | 6:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM14_General_normal.Intensidad_Neutro | 192.168.4.52:4660 | 6:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM14_General_normal.Potencia_activa_Fase_1 | 192.168.4.52:4660 | 6:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM14_General_normal.Potencia_activa_Fase_2 | 192.168.4.52:4660 | 6:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM14_General_normal.Potencia_activa_Fase_3 | 192.168.4.52:4660 | 6:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM14_General_normal.Potencia_reactiva_Fase_1 | 192.168.4.52:4660 | 6:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM14_General_normal.Potencia_reactiva_Fase_2 | 192.168.4.52:4660 | 6:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM14_General_normal.Potencia_reactiva_Fase_3 | 192.168.4.52:4660 | 6:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM14_General_normal.Frecuencia | 192.168.4.52:4660 | 6:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM14_General_normal.Energia_activa | 192.168.4.52:4660 | 6:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM14_General_normal.Energia_reactiva_inductiva | 192.168.4.52:4660 | 6:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM14_General_normal.Energia_reactiva_capacitiva | 192.168.4.52:4660 | 6:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM14_General_normal.Energia_aparente | 192.168.4.52:4660 | 6:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM14_General_normal.Potencia_activa_trifasica | 192.168.4.52:4660 | 6:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM14_General_normal.Potencia_inductiva_trifasica | 192.168.4.52:4660 | 6:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM14_General_normal.Potencia_capacitiva_trif | 192.168.4.52:4660 | 6:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM14_General_normal.cos_fi_trifasico | 192.168.4.52:4660 | 6:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM14_General_normal.Factor_de_potencia_trif | 192.168.4.52:4660 | 6:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM14_General_normal.Potencia_Aparente | 192.168.4.52:4660 | 6:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM14_General_normal.THD_V_Fase_1 | 192.168.4.52:4660 | 6:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM14_General_normal.THD_V_Fase_2 | 192.168.4.52:4660 | 6:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM14_General_normal.THD_V_Fase_3 | 192.168.4.52:4660 | 6:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM14_General_normal.THD_A_Fase_1 | 192.168.4.52:4660 | 6:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM14_General_normal.THD_A_Fase_2 | 192.168.4.52:4660 | 6:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM14_General_normal.THD_A_Fase_3 | 192.168.4.52:4660 | 6:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM14_General_normal.Tension_Fase_1_2 | 192.168.4.52:4660 | 6:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM14_General_normal.Tension_Fase_2_3 | 192.168.4.52:4660 | 6:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM14_General_normal.Tension_Fase_3_1 | 192.168.4.52:4660 | 6:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM53_Alumbrado.Tension_Fase_1_N | 192.168.4.52:4660 | 49:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM53_Alumbrado.Tension_Fase_2_N | 192.168.4.52:4660 | 49:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM53_Alumbrado.Tension_Fase_3_N | 192.168.4.52:4660 | 49:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM53_Alumbrado.Intensidad_Fase_1 | 192.168.4.52:4660 | 49:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM53_Alumbrado.Intensidad_Fase_2 | 192.168.4.52:4660 | 49:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM53_Alumbrado.Intensidad_Fase_3 | 192.168.4.52:4660 | 49:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM53_Alumbrado.Intensidad_Neutro | 192.168.4.52:4660 | 49:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM53_Alumbrado.Potencia_activa_Fase_1 | 192.168.4.52:4660 | 49:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM53_Alumbrado.Potencia_activa_Fase_2 | 192.168.4.52:4660 | 49:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM53_Alumbrado.Potencia_activa_Fase_3 | 192.168.4.52:4660 | 49:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM53_Alumbrado.Potencia_reactiva_Fase_1 | 192.168.4.52:4660 | 49:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM53_Alumbrado.Potencia_reactiva_Fase_2 | 192.168.4.52:4660 | 49:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM53_Alumbrado.Potencia_reactiva_Fase_3 | 192.168.4.52:4660 | 49:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM53_Alumbrado.Frecuencia | 192.168.4.52:4660 | 49:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM53_Alumbrado.Energia_activa | 192.168.4.52:4660 | 49:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM53_Alumbrado.Energia_reactiva_inductiva | 192.168.4.52:4660 | 49:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM53_Alumbrado.Energia_reactiva_capacitiva | 192.168.4.52:4660 | 49:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM53_Alumbrado.Energia_aparente | 192.168.4.52:4660 | 49:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM53_Alumbrado.Potencia_activa_trifasica | 192.168.4.52:4660 | 49:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM53_Alumbrado.Potencia_inductiva_trifasica | 192.168.4.52:4660 | 49:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM53_Alumbrado.Potencia_capacitiva_trif | 192.168.4.52:4660 | 49:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM53_Alumbrado.cos_fi_trifasico | 192.168.4.52:4660 | 49:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM53_Alumbrado.Factor_de_potencia_trif | 192.168.4.52:4660 | 49:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM53_Alumbrado.Potencia_Aparente | 192.168.4.52:4660 | 49:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM53_Alumbrado.THD_V_Fase_1 | 192.168.4.52:4660 | 49:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM53_Alumbrado.THD_V_Fase_2 | 192.168.4.52:4660 | 49:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM53_Alumbrado.THD_V_Fase_3 | 192.168.4.52:4660 | 49:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM53_Alumbrado.THD_A_Fase_1 | 192.168.4.52:4660 | 49:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM53_Alumbrado.THD_A_Fase_2 | 192.168.4.52:4660 | 49:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM53_Alumbrado.THD_A_Fase_3 | 192.168.4.52:4660 | 49:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM53_Alumbrado.Tension_Fase_1_2 | 192.168.4.52:4660 | 49:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM53_Alumbrado.Tension_Fase_2_3 | 192.168.4.52:4660 | 49:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM53_Alumbrado.Tension_Fase_3_1 | 192.168.4.52:4660 | 49:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM15_Alumbrado.Tension_Fase_1_N | 192.168.4.52:4660 | 10:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM15_Alumbrado.Tension_Fase_2_N | 192.168.4.52:4660 | 10:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM15_Alumbrado.Tension_Fase_3_N | 192.168.4.52:4660 | 10:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM15_Alumbrado.Intensidad_Fase_1 | 192.168.4.52:4660 | 10:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM15_Alumbrado.Intensidad_Fase_2 | 192.168.4.52:4660 | 10:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM15_Alumbrado.Intensidad_Fase_3 | 192.168.4.52:4660 | 10:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM15_Alumbrado.Intensidad_Neutro | 192.168.4.52:4660 | 10:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM15_Alumbrado.Potencia_activa_Fase_1 | 192.168.4.52:4660 | 10:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM15_Alumbrado.Potencia_activa_Fase_2 | 192.168.4.52:4660 | 10:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM15_Alumbrado.Potencia_activa_Fase_3 | 192.168.4.52:4660 | 10:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM15_Alumbrado.Potencia_reactiva_Fase_1 | 192.168.4.52:4660 | 10:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM15_Alumbrado.Potencia_reactiva_Fase_2 | 192.168.4.52:4660 | 10:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM15_Alumbrado.Potencia_reactiva_Fase_3 | 192.168.4.52:4660 | 10:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM15_Alumbrado.Frecuencia | 192.168.4.52:4660 | 10:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM15_Alumbrado.Energia_activa | 192.168.4.52:4660 | 10:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM15_Alumbrado.Energia_reactiva_inductiva | 192.168.4.52:4660 | 10:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM15_Alumbrado.Energia_reactiva_capacitiva | 192.168.4.52:4660 | 10:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM15_Alumbrado.Energia_aparente | 192.168.4.52:4660 | 10:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM15_Alumbrado.Potencia_activa_trifasica | 192.168.4.52:4660 | 10:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM15_Alumbrado.Potencia_inductiva_trifasica | 192.168.4.52:4660 | 10:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM15_Alumbrado.Potencia_capacitiva_trif | 192.168.4.52:4660 | 10:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM15_Alumbrado.cos_fi_trifasico | 192.168.4.52:4660 | 10:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM15_Alumbrado.Factor_de_potencia_trif | 192.168.4.52:4660 | 10:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM15_Alumbrado.Potencia_Aparente | 192.168.4.52:4660 | 10:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM15_Alumbrado.THD_V_Fase_1 | 192.168.4.52:4660 | 10:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM15_Alumbrado.THD_V_Fase_2 | 192.168.4.52:4660 | 10:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM15_Alumbrado.THD_V_Fase_3 | 192.168.4.52:4660 | 10:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM15_Alumbrado.THD_A_Fase_1 | 192.168.4.52:4660 | 10:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM15_Alumbrado.THD_A_Fase_2 | 192.168.4.52:4660 | 10:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM15_Alumbrado.THD_A_Fase_3 | 192.168.4.52:4660 | 10:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM15_Alumbrado.Tension_Fase_1_2 | 192.168.4.52:4660 | 10:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM15_Alumbrado.Tension_Fase_2_3 | 192.168.4.52:4660 | 10:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM15_Alumbrado.Tension_Fase_3_1 | 192.168.4.52:4660 | 10:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM14_Alumbrado.Tension_Fase_1_N | 192.168.4.52:4660 | 7:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM14_Alumbrado.Tension_Fase_2_N | 192.168.4.52:4660 | 7:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM14_Alumbrado.Tension_Fase_3_N | 192.168.4.52:4660 | 7:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM14_Alumbrado.Intensidad_Fase_1 | 192.168.4.52:4660 | 7:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM14_Alumbrado.Intensidad_Fase_2 | 192.168.4.52:4660 | 7:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM14_Alumbrado.Intensidad_Fase_3 | 192.168.4.52:4660 | 7:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM14_Alumbrado.Intensidad_Neutro | 192.168.4.52:4660 | 7:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM14_Alumbrado.Potencia_activa_Fase_1 | 192.168.4.52:4660 | 7:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM14_Alumbrado.Potencia_activa_Fase_2 | 192.168.4.52:4660 | 7:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM14_Alumbrado.Potencia_activa_Fase_3 | 192.168.4.52:4660 | 7:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM14_Alumbrado.Potencia_reactiva_Fase_1 | 192.168.4.52:4660 | 7:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM14_Alumbrado.Potencia_reactiva_Fase_2 | 192.168.4.52:4660 | 7:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM14_Alumbrado.Potencia_reactiva_Fase_3 | 192.168.4.52:4660 | 7:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM14_Alumbrado.Frecuencia | 192.168.4.52:4660 | 7:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM14_Alumbrado.Energia_activa | 192.168.4.52:4660 | 7:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM14_Alumbrado.Energia_reactiva_inductiva | 192.168.4.52:4660 | 7:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM14_Alumbrado.Energia_reactiva_capacitiva | 192.168.4.52:4660 | 7:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM14_Alumbrado.Energia_aparente | 192.168.4.52:4660 | 7:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM14_Alumbrado.Potencia_activa_trifasica | 192.168.4.52:4660 | 7:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM14_Alumbrado.Potencia_inductiva_trifasica | 192.168.4.52:4660 | 7:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM14_Alumbrado.Potencia_capacitiva_trif | 192.168.4.52:4660 | 7:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM14_Alumbrado.cos_fi_trifasico | 192.168.4.52:4660 | 7:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM14_Alumbrado.Factor_de_potencia_trif | 192.168.4.52:4660 | 7:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM14_Alumbrado.Potencia_Aparente | 192.168.4.52:4660 | 7:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM14_Alumbrado.THD_V_Fase_1 | 192.168.4.52:4660 | 7:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM14_Alumbrado.THD_V_Fase_2 | 192.168.4.52:4660 | 7:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM14_Alumbrado.THD_V_Fase_3 | 192.168.4.52:4660 | 7:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM14_Alumbrado.THD_A_Fase_1 | 192.168.4.52:4660 | 7:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM14_Alumbrado.THD_A_Fase_2 | 192.168.4.52:4660 | 7:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM14_Alumbrado.THD_A_Fase_3 | 192.168.4.52:4660 | 7:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM14_Alumbrado.Tension_Fase_1_2 | 192.168.4.52:4660 | 7:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM14_Alumbrado.Tension_Fase_2_3 | 192.168.4.52:4660 | 7:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM14_Alumbrado.Tension_Fase_3_1 | 192.168.4.52:4660 | 7:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM50_Alumbrado.Tension_Fase_1_N | 192.168.4.52:4660 | 43:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM50_Alumbrado.Tension_Fase_2_N | 192.168.4.52:4660 | 43:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM50_Alumbrado.Tension_Fase_3_N | 192.168.4.52:4660 | 43:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM50_Alumbrado.Intensidad_Fase_1 | 192.168.4.52:4660 | 43:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM50_Alumbrado.Intensidad_Fase_2 | 192.168.4.52:4660 | 43:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM50_Alumbrado.Intensidad_Fase_3 | 192.168.4.52:4660 | 43:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM50_Alumbrado.Intensidad_Neutro | 192.168.4.52:4660 | 43:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM50_Alumbrado.Potencia_activa_Fase_1 | 192.168.4.52:4660 | 43:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM50_Alumbrado.Potencia_activa_Fase_2 | 192.168.4.52:4660 | 43:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM50_Alumbrado.Potencia_activa_Fase_3 | 192.168.4.52:4660 | 43:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM50_Alumbrado.Potencia_reactiva_Fase_1 | 192.168.4.52:4660 | 43:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM50_Alumbrado.Potencia_reactiva_Fase_2 | 192.168.4.52:4660 | 43:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM50_Alumbrado.Potencia_reactiva_Fase_3 | 192.168.4.52:4660 | 43:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM50_Alumbrado.Frecuencia | 192.168.4.52:4660 | 43:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM50_Alumbrado.Energia_activa | 192.168.4.52:4660 | 43:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM50_Alumbrado.Energia_reactiva_inductiva | 192.168.4.52:4660 | 43:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM50_Alumbrado.Energia_reactiva_capacitiva | 192.168.4.52:4660 | 43:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM50_Alumbrado.Energia_aparente | 192.168.4.52:4660 | 43:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM50_Alumbrado.Potencia_activa_trifasica | 192.168.4.52:4660 | 43:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM50_Alumbrado.Potencia_inductiva_trifasica | 192.168.4.52:4660 | 43:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM50_Alumbrado.Potencia_capacitiva_trif | 192.168.4.52:4660 | 43:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM50_Alumbrado.cos_fi_trifasico | 192.168.4.52:4660 | 43:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM50_Alumbrado.Factor_de_potencia_trif | 192.168.4.52:4660 | 43:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM50_Alumbrado.Potencia_Aparente | 192.168.4.52:4660 | 43:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM50_Alumbrado.THD_V_Fase_1 | 192.168.4.52:4660 | 43:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM50_Alumbrado.THD_V_Fase_2 | 192.168.4.52:4660 | 43:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM50_Alumbrado.THD_V_Fase_3 | 192.168.4.52:4660 | 43:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM50_Alumbrado.THD_A_Fase_1 | 192.168.4.52:4660 | 43:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM50_Alumbrado.THD_A_Fase_2 | 192.168.4.52:4660 | 43:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM50_Alumbrado.THD_A_Fase_3 | 192.168.4.52:4660 | 43:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM50_Alumbrado.Tension_Fase_1_2 | 192.168.4.52:4660 | 43:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM50_Alumbrado.Tension_Fase_2_3 | 192.168.4.52:4660 | 43:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM50_Alumbrado.Tension_Fase_3_1 | 192.168.4.52:4660 | 43:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM53_Clima_vent.Tension_Fase_1_N | 192.168.4.52:4660 | 50:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM53_Clima_vent.Tension_Fase_2_N | 192.168.4.52:4660 | 50:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM53_Clima_vent.Tension_Fase_3_N | 192.168.4.52:4660 | 50:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM53_Clima_vent.Intensidad_Fase_1 | 192.168.4.52:4660 | 50:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM53_Clima_vent.Intensidad_Fase_2 | 192.168.4.52:4660 | 50:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM53_Clima_vent.Intensidad_Fase_3 | 192.168.4.52:4660 | 50:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM53_Clima_vent.Intensidad_Neutro | 192.168.4.52:4660 | 50:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM53_Clima_vent.Potencia_activa_Fase_1 | 192.168.4.52:4660 | 50:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM53_Clima_vent.Potencia_activa_Fase_2 | 192.168.4.52:4660 | 50:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM53_Clima_vent.Potencia_activa_Fase_3 | 192.168.4.52:4660 | 50:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM53_Clima_vent.Potencia_reactiva_Fase_1 | 192.168.4.52:4660 | 50:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM53_Clima_vent.Potencia_reactiva_Fase_2 | 192.168.4.52:4660 | 50:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM53_Clima_vent.Potencia_reactiva_Fase_3 | 192.168.4.52:4660 | 50:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM53_Clima_vent.Frecuencia | 192.168.4.52:4660 | 50:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM53_Clima_vent.Energia_activa | 192.168.4.52:4660 | 50:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM53_Clima_vent.Energia_reactiva_inductiva | 192.168.4.52:4660 | 50:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM53_Clima_vent.Energia_reactiva_capacitiva | 192.168.4.52:4660 | 50:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM53_Clima_vent.Energia_aparente | 192.168.4.52:4660 | 50:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM53_Clima_vent.Potencia_activa_trifasica | 192.168.4.52:4660 | 50:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM53_Clima_vent.Potencia_inductiva_trifasica | 192.168.4.52:4660 | 50:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM53_Clima_vent.Potencia_capacitiva_trif | 192.168.4.52:4660 | 50:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM53_Clima_vent.cos_fi_trifasico | 192.168.4.52:4660 | 50:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM53_Clima_vent.Factor_de_potencia_trif | 192.168.4.52:4660 | 50:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM53_Clima_vent.Potencia_Aparente | 192.168.4.52:4660 | 50:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM53_Clima_vent.THD_V_Fase_1 | 192.168.4.52:4660 | 50:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM53_Clima_vent.THD_V_Fase_2 | 192.168.4.52:4660 | 50:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM53_Clima_vent.THD_V_Fase_3 | 192.168.4.52:4660 | 50:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM53_Clima_vent.THD_A_Fase_1 | 192.168.4.52:4660 | 50:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM53_Clima_vent.THD_A_Fase_2 | 192.168.4.52:4660 | 50:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM53_Clima_vent.THD_A_Fase_3 | 192.168.4.52:4660 | 50:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM53_Clima_vent.Tension_Fase_1_2 | 192.168.4.52:4660 | 50:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM53_Clima_vent.Tension_Fase_2_3 | 192.168.4.52:4660 | 50:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM53_Clima_vent.Tension_Fase_3_1 | 192.168.4.52:4660 | 50:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM51_Clima_vent.Tension_Fase_1_N | 192.168.4.52:4660 | 46:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM51_Clima_vent.Tension_Fase_2_N | 192.168.4.52:4660 | 46:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM51_Clima_vent.Tension_Fase_3_N | 192.168.4.52:4660 | 46:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM51_Clima_vent.Intensidad_Fase_1 | 192.168.4.52:4660 | 46:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM51_Clima_vent.Intensidad_Fase_2 | 192.168.4.52:4660 | 46:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM51_Clima_vent.Intensidad_Fase_3 | 192.168.4.52:4660 | 46:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM51_Clima_vent.Intensidad_Neutro | 192.168.4.52:4660 | 46:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM51_Clima_vent.Potencia_activa_Fase_1 | 192.168.4.52:4660 | 46:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM51_Clima_vent.Potencia_activa_Fase_2 | 192.168.4.52:4660 | 46:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM51_Clima_vent.Potencia_activa_Fase_3 | 192.168.4.52:4660 | 46:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM51_Clima_vent.Potencia_reactiva_Fase_1 | 192.168.4.52:4660 | 46:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM51_Clima_vent.Potencia_reactiva_Fase_2 | 192.168.4.52:4660 | 46:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM51_Clima_vent.Potencia_reactiva_Fase_3 | 192.168.4.52:4660 | 46:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM51_Clima_vent.Frecuencia | 192.168.4.52:4660 | 46:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM51_Clima_vent.Energia_activa | 192.168.4.52:4660 | 46:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM51_Clima_vent.Energia_reactiva_inductiva | 192.168.4.52:4660 | 46:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM51_Clima_vent.Energia_reactiva_capacitiva | 192.168.4.52:4660 | 46:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM51_Clima_vent.Energia_aparente | 192.168.4.52:4660 | 46:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM51_Clima_vent.Potencia_activa_trifasica | 192.168.4.52:4660 | 46:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM51_Clima_vent.Potencia_inductiva_trifasica | 192.168.4.52:4660 | 46:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM51_Clima_vent.Potencia_capacitiva_trif | 192.168.4.52:4660 | 46:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM51_Clima_vent.cos_fi_trifasico | 192.168.4.52:4660 | 46:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM51_Clima_vent.Factor_de_potencia_trif | 192.168.4.52:4660 | 46:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM51_Clima_vent.Potencia_Aparente | 192.168.4.52:4660 | 46:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM51_Clima_vent.THD_V_Fase_1 | 192.168.4.52:4660 | 46:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM51_Clima_vent.THD_V_Fase_2 | 192.168.4.52:4660 | 46:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM51_Clima_vent.THD_V_Fase_3 | 192.168.4.52:4660 | 46:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM51_Clima_vent.THD_A_Fase_1 | 192.168.4.52:4660 | 46:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM51_Clima_vent.THD_A_Fase_2 | 192.168.4.52:4660 | 46:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM51_Clima_vent.THD_A_Fase_3 | 192.168.4.52:4660 | 46:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM51_Clima_vent.Tension_Fase_1_2 | 192.168.4.52:4660 | 46:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM51_Clima_vent.Tension_Fase_2_3 | 192.168.4.52:4660 | 46:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM51_Clima_vent.Tension_Fase_3_1 | 192.168.4.52:4660 | 46:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM15_Clima_vent.Tension_Fase_1_N | 192.168.4.52:4660 | 11:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM15_Clima_vent.Tension_Fase_2_N | 192.168.4.52:4660 | 11:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM15_Clima_vent.Tension_Fase_3_N | 192.168.4.52:4660 | 11:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM15_Clima_vent.Intensidad_Fase_1 | 192.168.4.52:4660 | 11:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM15_Clima_vent.Intensidad_Fase_2 | 192.168.4.52:4660 | 11:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM15_Clima_vent.Intensidad_Fase_3 | 192.168.4.52:4660 | 11:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM15_Clima_vent.Intensidad_Neutro | 192.168.4.52:4660 | 11:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM15_Clima_vent.Potencia_activa_Fase_1 | 192.168.4.52:4660 | 11:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM15_Clima_vent.Potencia_activa_Fase_2 | 192.168.4.52:4660 | 11:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM15_Clima_vent.Potencia_activa_Fase_3 | 192.168.4.52:4660 | 11:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM15_Clima_vent.Potencia_reactiva_Fase_1 | 192.168.4.52:4660 | 11:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM15_Clima_vent.Potencia_reactiva_Fase_2 | 192.168.4.52:4660 | 11:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM15_Clima_vent.Potencia_reactiva_Fase_3 | 192.168.4.52:4660 | 11:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM15_Clima_vent.Frecuencia | 192.168.4.52:4660 | 11:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM15_Clima_vent.Energia_activa | 192.168.4.52:4660 | 11:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM15_Clima_vent.Energia_reactiva_inductiva | 192.168.4.52:4660 | 11:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM15_Clima_vent.Energia_reactiva_capacitiva | 192.168.4.52:4660 | 11:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM15_Clima_vent.Energia_aparente | 192.168.4.52:4660 | 11:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM15_Clima_vent.Potencia_activa_trifasica | 192.168.4.52:4660 | 11:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM15_Clima_vent.Potencia_inductiva_trifasica | 192.168.4.52:4660 | 11:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM15_Clima_vent.Potencia_capacitiva_trif | 192.168.4.52:4660 | 11:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM15_Clima_vent.cos_fi_trifasico | 192.168.4.52:4660 | 11:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM15_Clima_vent.Factor_de_potencia_trif | 192.168.4.52:4660 | 11:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM15_Clima_vent.Potencia_Aparente | 192.168.4.52:4660 | 11:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM15_Clima_vent.THD_V_Fase_1 | 192.168.4.52:4660 | 11:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM15_Clima_vent.THD_V_Fase_2 | 192.168.4.52:4660 | 11:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM15_Clima_vent.THD_V_Fase_3 | 192.168.4.52:4660 | 11:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM15_Clima_vent.THD_A_Fase_1 | 192.168.4.52:4660 | 11:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM15_Clima_vent.THD_A_Fase_2 | 192.168.4.52:4660 | 11:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM15_Clima_vent.THD_A_Fase_3 | 192.168.4.52:4660 | 11:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM15_Clima_vent.Tension_Fase_1_2 | 192.168.4.52:4660 | 11:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM15_Clima_vent.Tension_Fase_2_3 | 192.168.4.52:4660 | 11:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM15_Clima_vent.Tension_Fase_3_1 | 192.168.4.52:4660 | 11:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM14_Clima_vent.Tension_Fase_1_N | 192.168.4.52:4660 | 8:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM14_Clima_vent.Tension_Fase_2_N | 192.168.4.52:4660 | 8:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM14_Clima_vent.Tension_Fase_3_N | 192.168.4.52:4660 | 8:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM14_Clima_vent.Intensidad_Fase_1 | 192.168.4.52:4660 | 8:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM14_Clima_vent.Intensidad_Fase_2 | 192.168.4.52:4660 | 8:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM14_Clima_vent.Intensidad_Fase_3 | 192.168.4.52:4660 | 8:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM14_Clima_vent.Intensidad_Neutro | 192.168.4.52:4660 | 8:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM14_Clima_vent.Potencia_activa_Fase_1 | 192.168.4.52:4660 | 8:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM14_Clima_vent.Potencia_activa_Fase_2 | 192.168.4.52:4660 | 8:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM14_Clima_vent.Potencia_activa_Fase_3 | 192.168.4.52:4660 | 8:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM14_Clima_vent.Potencia_reactiva_Fase_1 | 192.168.4.52:4660 | 8:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM14_Clima_vent.Potencia_reactiva_Fase_2 | 192.168.4.52:4660 | 8:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM14_Clima_vent.Potencia_reactiva_Fase_3 | 192.168.4.52:4660 | 8:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM14_Clima_vent.Frecuencia | 192.168.4.52:4660 | 8:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM14_Clima_vent.Energia_activa | 192.168.4.52:4660 | 8:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM14_Clima_vent.Energia_reactiva_inductiva | 192.168.4.52:4660 | 8:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM14_Clima_vent.Energia_reactiva_capacitiva | 192.168.4.52:4660 | 8:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM14_Clima_vent.Energia_aparente | 192.168.4.52:4660 | 8:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM14_Clima_vent.Potencia_activa_trifasica | 192.168.4.52:4660 | 8:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM14_Clima_vent.Potencia_inductiva_trifasica | 192.168.4.52:4660 | 8:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM14_Clima_vent.Potencia_capacitiva_trif | 192.168.4.52:4660 | 8:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM14_Clima_vent.cos_fi_trifasico | 192.168.4.52:4660 | 8:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM14_Clima_vent.Factor_de_potencia_trif | 192.168.4.52:4660 | 8:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM14_Clima_vent.Potencia_Aparente | 192.168.4.52:4660 | 8:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM14_Clima_vent.THD_V_Fase_1 | 192.168.4.52:4660 | 8:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM14_Clima_vent.THD_V_Fase_2 | 192.168.4.52:4660 | 8:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM14_Clima_vent.THD_V_Fase_3 | 192.168.4.52:4660 | 8:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM14_Clima_vent.THD_A_Fase_1 | 192.168.4.52:4660 | 8:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM14_Clima_vent.THD_A_Fase_2 | 192.168.4.52:4660 | 8:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM14_Clima_vent.THD_A_Fase_3 | 192.168.4.52:4660 | 8:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM14_Clima_vent.Tension_Fase_1_2 | 192.168.4.52:4660 | 8:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM14_Clima_vent.Tension_Fase_2_3 | 192.168.4.52:4660 | 8:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM14_Clima_vent.Tension_Fase_3_1 | 192.168.4.52:4660 | 8:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM50_Clima_vent.Tension_Fase_1_N | 192.168.4.52:4660 | 44:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM50_Clima_vent.Tension_Fase_2_N | 192.168.4.52:4660 | 44:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM50_Clima_vent.Tension_Fase_3_N | 192.168.4.52:4660 | 44:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM50_Clima_vent.Intensidad_Fase_1 | 192.168.4.52:4660 | 44:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM50_Clima_vent.Intensidad_Fase_2 | 192.168.4.52:4660 | 44:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM50_Clima_vent.Intensidad_Fase_3 | 192.168.4.52:4660 | 44:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM50_Clima_vent.Intensidad_Neutro | 192.168.4.52:4660 | 44:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM50_Clima_vent.Potencia_activa_Fase_1 | 192.168.4.52:4660 | 44:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM50_Clima_vent.Potencia_activa_Fase_2 | 192.168.4.52:4660 | 44:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM50_Clima_vent.Potencia_activa_Fase_3 | 192.168.4.52:4660 | 44:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM50_Clima_vent.Potencia_reactiva_Fase_1 | 192.168.4.52:4660 | 44:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM50_Clima_vent.Potencia_reactiva_Fase_2 | 192.168.4.52:4660 | 44:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM50_Clima_vent.Potencia_reactiva_Fase_3 | 192.168.4.52:4660 | 44:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM50_Clima_vent.Frecuencia | 192.168.4.52:4660 | 44:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM50_Clima_vent.Energia_activa | 192.168.4.52:4660 | 44:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM50_Clima_vent.Energia_reactiva_inductiva | 192.168.4.52:4660 | 44:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM50_Clima_vent.Energia_reactiva_capacitiva | 192.168.4.52:4660 | 44:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM50_Clima_vent.Energia_aparente | 192.168.4.52:4660 | 44:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM50_Clima_vent.Potencia_activa_trifasica | 192.168.4.52:4660 | 44:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM50_Clima_vent.Potencia_inductiva_trifasica | 192.168.4.52:4660 | 44:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM50_Clima_vent.Potencia_capacitiva_trif | 192.168.4.52:4660 | 44:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM50_Clima_vent.cos_fi_trifasico | 192.168.4.52:4660 | 44:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM50_Clima_vent.Factor_de_potencia_trif | 192.168.4.52:4660 | 44:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM50_Clima_vent.Potencia_Aparente | 192.168.4.52:4660 | 44:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM50_Clima_vent.THD_V_Fase_1 | 192.168.4.52:4660 | 44:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM50_Clima_vent.THD_V_Fase_2 | 192.168.4.52:4660 | 44:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM50_Clima_vent.THD_V_Fase_3 | 192.168.4.52:4660 | 44:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM50_Clima_vent.THD_A_Fase_1 | 192.168.4.52:4660 | 44:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM50_Clima_vent.THD_A_Fase_2 | 192.168.4.52:4660 | 44:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM50_Clima_vent.THD_A_Fase_3 | 192.168.4.52:4660 | 44:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM50_Clima_vent.Tension_Fase_1_2 | 192.168.4.52:4660 | 44:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM50_Clima_vent.Tension_Fase_2_3 | 192.168.4.52:4660 | 44:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM50_Clima_vent.Tension_Fase_3_1 | 192.168.4.52:4660 | 44:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM51_Esp_multifuncion.Tension_Fase_1_N | 192.168.4.52:4660 | 47:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM51_Esp_multifuncion.Tension_Fase_2_N | 192.168.4.52:4660 | 47:4X:11DS | Read | Always | 10000000
MSA_Analizador_QM51_Esp_multifuncion.Tension_Fase_3_N | 192.168.4.52:4660 | 47:4X:21DS | Read | Always | 10000000
MSA_Analizador_QM51_Esp_multifuncion.Intensidad_Fase_1 | 192.168.4.52:4660 | 47:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM51_Esp_multifuncion.Intensidad_Fase_2 | 192.168.4.52:4660 | 47:4X:13DS | Read | Always | 1000000000
MSA_Analizador_QM51_Esp_multifuncion.Intensidad_Fase_3 | 192.168.4.52:4660 | 47:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM51_Esp_multifuncion.Intensidad_Neutro | 192.168.4.52:4660 | 47:4X:73DS | Read | Always | 1000000000
MSA_Analizador_QM51_Esp_multifuncion.Potencia_activa_Fase_1 | 192.168.4.52:4660 | 47:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM51_Esp_multifuncion.Potencia_activa_Fase_2 | 192.168.4.52:4660 | 47:4X:15DS | Read | Always | 1000000000
MSA_Analizador_QM51_Esp_multifuncion.Potencia_activa_Fase_3 | 192.168.4.52:4660 | 47:4X:25DS | Read | Always | 1000000000
MSA_Analizador_QM51_Esp_multifuncion.Potencia_reactiva_Fase_1 | 192.168.4.52:4660 | 47:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM51_Esp_multifuncion.Potencia_reactiva_Fase_2 | 192.168.4.52:4660 | 47:4X:17DS | Read | Always | 1000000000
MSA_Analizador_QM51_Esp_multifuncion.Potencia_reactiva_Fase_3 | 192.168.4.52:4660 | 47:4X:27DS | Read | Always | 1000000000
MSA_Analizador_QM51_Esp_multifuncion.Frecuencia | 192.168.4.52:4660 | 47:4X:41DS | Read | Always | 10000000
MSA_Analizador_QM51_Esp_multifuncion.Energia_activa | 192.168.4.52:4660 | 47:4X:61DS | Read | Always | 1000000000
MSA_Analizador_QM51_Esp_multifuncion.Energia_reactiva_inductiva | 192.168.4.52:4660 | 47:4X:63DS | Read | Always | 1000000000
MSA_Analizador_QM51_Esp_multifuncion.Energia_reactiva_capacitiva | 192.168.4.52:4660 | 47:4X:65DS | Read | Always | 1000000000
MSA_Analizador_QM51_Esp_multifuncion.Energia_aparente | 192.168.4.52:4660 | 47:4X:87DS | Read | Always | 1000000000
MSA_Analizador_QM51_Esp_multifuncion.Potencia_activa_trifasica | 192.168.4.52:4660 | 47:4X:31DS | Read | Always | 1000000000
MSA_Analizador_QM51_Esp_multifuncion.Potencia_inductiva_trifasica | 192.168.4.52:4660 | 47:4X:33DS | Read | Always | 1000000000
MSA_Analizador_QM51_Esp_multifuncion.Potencia_capacitiva_trif | 192.168.4.52:4660 | 47:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM51_Esp_multifuncion.cos_fi_trifasico | 192.168.4.52:4660 | 47:4X:37DS | Read | Always | 100000000
MSA_Analizador_QM51_Esp_multifuncion.Factor_de_potencia_trif | 192.168.4.52:4660 | 47:4X:39DS | Read | Always | 100000000
MSA_Analizador_QM51_Esp_multifuncion.Potencia_Aparente | 192.168.4.52:4660 | 47:4X:67DS | Read | Always | 1000000000
MSA_Analizador_QM51_Esp_multifuncion.THD_V_Fase_1 | 192.168.4.52:4660 | 47:4X:49DS | Read | Always | 10000000
MSA_Analizador_QM51_Esp_multifuncion.THD_V_Fase_2 | 192.168.4.52:4660 | 47:4X:51DS | Read | Always | 10000000
MSA_Analizador_QM51_Esp_multifuncion.THD_V_Fase_3 | 192.168.4.52:4660 | 47:4X:53DS | Read | Always | 10000000
MSA_Analizador_QM51_Esp_multifuncion.THD_A_Fase_1 | 192.168.4.52:4660 | 47:4X:55DS | Read | Always | 10000000
MSA_Analizador_QM51_Esp_multifuncion.THD_A_Fase_2 | 192.168.4.52:4660 | 47:4X:57DS | Read | Always | 10000000
MSA_Analizador_QM51_Esp_multifuncion.THD_A_Fase_3 | 192.168.4.52:4660 | 47:4X:59DS | Read | Always | 10000000
MSA_Analizador_QM51_Esp_multifuncion.Tension_Fase_1_2 | 192.168.4.52:4660 | 47:4X:43DS | Read | Always | 10000000
MSA_Analizador_QM51_Esp_multifuncion.Tension_Fase_2_3 | 192.168.4.52:4660 | 47:4X:45DS | Read | Always | 10000000
MSA_Analizador_QM51_Esp_multifuncion.Tension_Fase_3_1 | 192.168.4.52:4660 | 47:4X:47DS | Read | Always | 10000000
MSA_Analizador_QM10_General_normal.Tension_Fase_L1 | 192.168.4.42:4660 | 1:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM10_General_normal.Corriente_L1 | 192.168.4.42:4660 | 1:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_normal.Potencia_Activa_L1 | 192.168.4.42:4660 | 1:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_normal.Potencia_Reactiva_L1 | 192.168.4.42:4660 | 1:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_normal.Factor_de_Potencia_L1 | 192.168.4.42:4660 | 1:4X:13DS | Read | Always | 100000000
MSA_Analizador_QM10_General_normal.Tension_Fase_L2 | 192.168.4.42:4660 | 1:4X:17DS | Read | Always | 10000000
MSA_Analizador_QM10_General_normal.Corriente_L2 | 192.168.4.42:4660 | 1:4X:19DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_normal.Potencia_Activa_L2 | 192.168.4.42:4660 | 1:4X:21DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_normal.Potencia_Reactiva_L2 | 192.168.4.42:4660 | 1:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_normal.Factor_de_Potencia_L2 | 192.168.4.42:4660 | 1:4X:29DS | Read | Always | 100000000
MSA_Analizador_QM10_General_normal.Tension_Fase_L3 | 192.168.4.42:4660 | 1:4X:33DS | Read | Always | 10000000
MSA_Analizador_QM10_General_normal.Corriente_L3 | 192.168.4.42:4660 | 1:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_normal.Potencia_Activa_L3 | 192.168.4.42:4660 | 1:4X:37DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_normal.Potencia_Reactiva_L3 | 192.168.4.42:4660 | 1:4X:39DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_normal.Factor_de_Potencia_L3 | 192.168.4.42:4660 | 1:4X:45DS | Read | Always | 100000000
MSA_Analizador_QM10_General_normal.Potencia_Activa_III | 192.168.4.42:4660 | 1:4X:49DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_normal.Potencia_Inductiva_III | 192.168.4.42:4660 | 1:4X:51DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_normal.Potencia_Capacitiva_III | 192.168.4.42:4660 | 1:4X:53DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_normal.Cos_Z_III | 192.168.4.42:4660 | 1:4X:59DS | Read | Always | 100000000
MSA_Analizador_QM10_General_normal.Factor_de_Potencia_III | 192.168.4.42:4660 | 1:4X:57DS | Read | Always | 100000000
MSA_Analizador_QM10_General_normal.Frecuencia | 192.168.4.42:4660 | 1:4X:61DS | Read | Always | 100000000
MSA_Analizador_QM10_General_normal.Tension_Linea_L1_L2 | 192.168.4.42:4660 | 1:4X:63DS | Read | Always | 10000000
MSA_Analizador_QM10_General_normal.Tension_Linea_L2_L3 | 192.168.4.42:4660 | 1:4X:65DS | Read | Always | 10000000
MSA_Analizador_QM10_General_normal.Tension_Linea_L3_L1 | 192.168.4.42:4660 | 1:4X:67DS | Read | Always | 10000000
MSA_Analizador_QM10_General_normal.THD_L1_V | 192.168.4.42:4660 | 1:4X:71DS | Read | Always | 10000000
MSA_Analizador_QM10_General_normal.THD_L2_V | 192.168.4.42:4660 | 1:4X:73DS | Read | Always | 10000000
MSA_Analizador_QM10_General_normal.THD_L3_V | 192.168.4.42:4660 | 1:4X:75DS | Read | Always | 10000000
MSA_Analizador_QM10_General_normal.THD_L1_A | 192.168.4.42:4660 | 1:4X:77DS | Read | Always | 10000000
MSA_Analizador_QM10_General_normal.THD_L2_A | 192.168.4.42:4660 | 1:4X:79DS | Read | Always | 10000000
MSA_Analizador_QM10_General_normal.THD_L3_A | 192.168.4.42:4660 | 1:4X:81DS | Read | Always | 10000000
MSA_Analizador_QM10_General_normal.Energia_Activa_III | 192.168.4.42:4660 | 1:4X:95DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_normal.Energia_Reactiva_Inductiva_III | 192.168.4.42:4660 | 1:4X:99DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_normal.Energia_React__Capacitiva_III | 192.168.4.42:4660 | 1:4X:103DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_normal.Potencia_Aparente_III | 192.168.4.42:4660 | 1:4X:55DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_normal.Corriente_Neutro | 192.168.4.42:4660 | 1:4X:69DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_normal.Energia_Aparente_III | 192.168.4.42:4660 | 1:4X:107DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_complement.Tension_Fase_L1 | 192.168.4.42:4660 | 2:4X:1DS | Read | Always | 10000000
MSA_Analizador_QM10_General_complement.Corriente_L1 | 192.168.4.42:4660 | 2:4X:3DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_complement.Potencia_Activa_L1 | 192.168.4.42:4660 | 2:4X:5DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_complement.Potencia_Reactiva_L1 | 192.168.4.42:4660 | 2:4X:7DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_complement.Factor_de_Potencia_L1 | 192.168.4.42:4660 | 2:4X:13DS | Read | Always | 100000000
MSA_Analizador_QM10_General_complement.Tension_Fase_L2 | 192.168.4.42:4660 | 2:4X:17DS | Read | Always | 10000000
MSA_Analizador_QM10_General_complement.Corriente_L2 | 192.168.4.42:4660 | 2:4X:19DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_complement.Potencia_Activa_L2 | 192.168.4.42:4660 | 2:4X:21DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_complement.Potencia_Reactiva_L2 | 192.168.4.42:4660 | 2:4X:23DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_complement.Factor_de_Potencia_L2 | 192.168.4.42:4660 | 2:4X:29DS | Read | Always | 100000000
MSA_Analizador_QM10_General_complement.Tension_Fase_L3 | 192.168.4.42:4660 | 2:4X:33DS | Read | Always | 10000000
MSA_Analizador_QM10_General_complement.Corriente_L3 | 192.168.4.42:4660 | 2:4X:35DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_complement.Potencia_Activa_L3 | 192.168.4.42:4660 | 2:4X:37DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_complement.Potencia_Reactiva_L3 | 192.168.4.42:4660 | 2:4X:39DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_complement.Factor_de_Potencia_L3 | 192.168.4.42:4660 | 2:4X:45DS | Read | Always | 100000000
MSA_Analizador_QM10_General_complement.Potencia_Activa_III | 192.168.4.42:4660 | 2:4X:49DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_complement.Potencia_Inductiva_III | 192.168.4.42:4660 | 2:4X:51DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_complement.Potencia_Capacitiva_III | 192.168.4.42:4660 | 2:4X:53DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_complement.Cos_Z_III | 192.168.4.42:4660 | 2:4X:59DS | Read | Always | 100000000
MSA_Analizador_QM10_General_complement.Factor_de_Potencia_III | 192.168.4.42:4660 | 2:4X:57DS | Read | Always | 100000000
MSA_Analizador_QM10_General_complement.Frecuencia | 192.168.4.42:4660 | 2:4X:61DS | Read | Always | 100000000
MSA_Analizador_QM10_General_complement.Tension_Linea_L1_L2 | 192.168.4.42:4660 | 2:4X:63DS | Read | Always | 10000000
MSA_Analizador_QM10_General_complement.Tension_Linea_L2_L3 | 192.168.4.42:4660 | 2:4X:65DS | Read | Always | 10000000
MSA_Analizador_QM10_General_complement.Tension_Linea_L3_L1 | 192.168.4.42:4660 | 2:4X:67DS | Read | Always | 10000000
MSA_Analizador_QM10_General_complement.THD_L1_V | 192.168.4.42:4660 | 2:4X:71DS | Read | Always | 10000000
MSA_Analizador_QM10_General_complement.THD_L2_V | 192.168.4.42:4660 | 2:4X:73DS | Read | Always | 10000000
MSA_Analizador_QM10_General_complement.THD_L3_V | 192.168.4.42:4660 | 2:4X:75DS | Read | Always | 10000000
MSA_Analizador_QM10_General_complement.THD_L1_A | 192.168.4.42:4660 | 2:4X:77DS | Read | Always | 10000000
MSA_Analizador_QM10_General_complement.THD_L2_A | 192.168.4.42:4660 | 2:4X:79DS | Read | Always | 10000000
MSA_Analizador_QM10_General_complement.THD_L3_A | 192.168.4.42:4660 | 2:4X:81DS | Read | Always | 10000000
MSA_Analizador_QM10_General_complement.Energia_Activa_III | 192.168.4.42:4660 | 2:4X:95DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_complement.Energia_Reactiva_Inductiva_III | 192.168.4.42:4660 | 2:4X:99DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_complement.Energia_React__Capacitiva_III | 192.168.4.42:4660 | 2:4X:103DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_complement.Potencia_Aparente_III | 192.168.4.42:4660 | 2:4X:55DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_complement.Corriente_Neutro | 192.168.4.42:4660 | 2:4X:69DS | Read | Always | 1000000000
MSA_Analizador_QM10_General_complement.Energia_Aparente_III | 192.168.4.42:4660 | 2:4X:107DS | Read | Always | 1000000000
MSA_BM_Cortinas_aire.Marcha_Paro | 192.168.4.27:4660 | 1:4X:12301SX | Read+Write | Always
MSA_BM_Cortinas_aire.Velocidad_ventilacion | 192.168.4.27:4660 | 1:4X:12310SX | Read+Write | Always
MSA_BM_Cortinas_aire.Velocidad_ventilacion_lectura | 192.168.4.27:4660 | 1:4X:4119SX | Read | Always
MSA_BT_Cortinas_aire.Marcha_Paro | 192.168.4.37:4660 | 1:4X:12301SX | Read+Write | Always
MSA_BT_Cortinas_aire.Velocidad_ventilacion | 192.168.4.37:4660 | 1:4X:12310SX | Read+Write | Always
MSA_BT_Cortinas_aire.Velocidad_ventilacion_lectura | 192.168.4.37:4660 | 1:4X:4119SX | Read | Always
MSA_UM_Cortinas_aire.Marcha_Paro | 192.168.4.57:4660 | 1:4X:12301SX | Read+Write | Always
MSA_UM_Cortinas_aire.Velocidad_ventilacion | 192.168.4.57:4660 | 1:4X:12310SX | Read+Write | Always
MSA_UM_Cortinas_aire.Velocidad_ventilacion_lectura | 192.168.4.57:4660 | 1:4X:4119SX | Read | Always
MSA_UT_Cortinas_aire.Marcha_Paro | 192.168.4.47:4660 | 1:4X:12301SX | Read+Write | Always
MSA_UT_Cortinas_aire.Velocidad_ventilacion | 192.168.4.47:4660 | 1:4X:12310SX | Read+Write | Always
MSA_UT_Cortinas_aire.Velocidad_ventilacion_lectura | 192.168.4.47:4660 | 1:4X:4119SX | Read | Always
MSA_BM_Pozo_fecales_Alarma_Bomba | 192.168.4.23:4660 | 10:0X:204 | Read | Always
MSA_BM_Pozo_fecales_Alarma_Nivel | 192.168.4.23:4660 | 10:0X:205 | Read | Always
MSA_BM_Pozo_freaticas_Alarma_Bomba | 192.168.4.23:4660 | 10:0X:206 | Read | Always
MSA_BM_Pozo_freaticas_Alarma_Nivel | 192.168.4.23:4660 | 10:0X:207 | Read | Always
MSA_BT_Pozo_fecales_Alarma_Bomba | 192.168.4.33:4660 | 9:0X:207 | Read | Always
MSA_BT_Pozo_fecales_Alarma_Nivel | 192.168.4.33:4660 | 9:0X:208 | Read | Always
MSA_UT_pozo_fecales_Alarma_Bomba | 192.168.4.43:4660 | 10:0X:218 | Read | Always
MSA_UT_pozo_fecales_Alarma_Nivel | 192.168.4.43:4660 | 10:0X:219 | Read | Always
MSA_UT_Pozo_freatico_Alarma_Bomba | 192.168.4.43:4660 | 10:0X:220 | Read | Always
MSA_UT_Pozo_freatico_Alarma_Nivel | 192.168.4.43:4660 | 10:0X:221 | Read | Always
MSA_UM_51_Pozo_freaticas_Alarma_nivel | 192.168.4.53:4660 | 5:0X:245 | Read | Always
MSA_UM_51_Pozo_freaticas_Alarma_grupo | 192.168.4.53:4660 | 5:0X:246 | Read | Always
MSA_UM_Pozo_fecales_Alarma_Bomba | 192.168.4.53:4660 | 9:0X:217 | Read | Always
MSA_UM_Pozo_fecales_Alarma_Nivel | 192.168.4.53:4660 | 9:0X:218 | Read | Always
MSA_UM_53_Poza_freaticas_Alarma_Bomba | 192.168.4.53:4660 | 9:0X:219 | Read | Always
MSA_UM_53_Poza_freaticas_Alarma_Nivel | 192.168.4.53:4660 | 9:0X:220 | Read | Always
MSA_BM_Arqueta_PB_Nivel_alto | 192.168.4.23:4660 | 5:0X:244 | Read | Always
MSA_UT_Arqueta_PB_Nivel_alto | 192.168.4.43:4660 | 6:0X:244 | Read | Always
MSA_UM_Arqueta_PB_Nivel_alto | 192.168.4.53:4660 | 5:0X:244 | Read | Always
MSA_UM_Alarma_Bba_Trasvase_Freaticas | 192.168.4.53:4660 | 5:0X:247 | Read | Always
MSA_UM_Alarma_Bbs_Fluxores | 192.168.4.53:4660 | 5:0X:248 | Read | Always
MSA_BM_Alarma_nivel_bajo_aljibe_PCI | 192.168.4.23:4660 | 10:0X:208 | Read | Always
MSA_BM_Alarma_grupo_CI | 192.168.4.23:4660 | 9:0X:208 | Read | Always
MSA_BM_Contador_freatica.Contaje | 192.168.4.23:4660 | 8:3X:671D | Read | Always | 10000000
MSA_BM_Contador_freatica.Inicial | 192.168.4.23:4660 | 8:3X:627D | Read+Write | Always | 10000000
MSA_BM_Contador_freatica.Reset | 192.168.4.23:4660 | 8:0X:417 | Read+Write | Always
MSA_UT_Contador_freatica.Contaje | 192.168.4.43:4660 | 10:3X:583D | Read | Always | 10000000
MSA_UT_Contador_freatica.Inicial | 192.168.4.43:4660 | 10:3X:539D | Read+Write | Always | 10000000
MSA_UT_Contador_freatica.Reset | 192.168.4.43:4660 | 10:0X:417 | Read+Write | Always
MSA_UM_Contador_freatica_1.Contaje | 192.168.4.53:4660 | 8:3X:1023D | Read | Always | 10000000
MSA_UM_Contador_freatica_1.Inicial | 192.168.4.53:4660 | 8:3X:979D | Read+Write | Always | 10000000
MSA_UM_Contador_freatica_1.Reset | 192.168.4.53:4660 | 8:0X:313 | Read+Write | Always
MSA_UM_Contador_freatica_2.Contaje | 192.168.4.53:4660 | 8:3X:935D | Read | Always | 10000000
MSA_UM_Contador_freatica_2.Inicial | 192.168.4.53:4660 | 8:3X:891D | Read+Write | Always | 10000000
MSA_UM_Contador_freatica_2.Reset | 192.168.4.53:4660 | 8:0X:314 | Read+Write | Always
MSA_UM_Contador_freatica_3.Contaje | 192.168.4.53:4660 | 11:3X:1023D | Read | Always | 10000000
MSA_UM_Contador_freatica_3.Inicial | 192.168.4.53:4660 | 11:3X:979D | Read+Write | Always | 10000000
MSA_UM_Contador_freatica_3.Reset | 192.168.4.53:4660 | 11:0X:322 | Read+Write | Always
MSA_UM_51_Climatizacion_Estado_proteccion | 192.168.4.53:4660 | 6:0X:228 | Read | Always
MSA_UM_51_Climatizacion_Estado_Pref_NoPref | 192.168.4.53:4660 | 6:0X:229 | Read | Always
MSA_UM_51_Climatizacion_Estado_contactor | 192.168.4.53:4660 | 6:0X:230 | Read | Always
MSA_UM_Vent_Desenf_4.Horario_A | 192.168.4.53:4660 | 6:3X:365T80 | Read+Write | Always
MSA_UM_Vent_Desenf_4.Horario_estado | 192.168.4.53:4660 | 6:0X:425 | Read | Always
MSA_UM_Vent_Desenf_4.Manual_horario | 192.168.4.53:4660 | 6:0X:426 | Read+Write | Always
MSA_UM_Vent_Desenf_4.Marcha_paro | 192.168.4.53:4660 | 6:0X:427 | Read+Write | Always
MSA_UM_Vent_Desenf_4.Reset_horas | 192.168.4.53:4660 | 6:0X:428 | Read+Write | Always
MSA_UM_Vent_Desenf_4.Horas_funcionam | 192.168.4.53:4660 | 6:3X:628 | Read | Always
MSA_UM_Vent_Desenf_4.Estado | 192.168.4.53:4660 | 6:0X:429 | Read | Always
MSA_UM_Vent_Desenf_4.Orden | 192.168.4.53:4660 | 6:0X:430 | Read | Always
MSA_UM_Vent_Desenf_4.Fallo | 192.168.4.53:4660 | 6:0X:431 | Read | Always
MSA_UM_Contador_Llenado_Instalaciones_Total | 192.168.4.53:4660 | 8:3X:937D | Read | Always | 100000000
MSA_UM_Contador_Llenado_Instalaciones_Inicial | 192.168.4.53:4660 | 8:3X:893D | Read+Write | Always | 100000000
MSA_UM_Contador_Llenado_Instalaciones_Reset | 192.168.4.53:4660 | 8:0X:315 | Read+Write | Always
MSA_BT_Enfriadora.Estado_unidad | 192.168.4.38:4660 | 2:0X:2 | Read | Always
MSA_BT_Enfriadora.Estado_bomba1_Evaporador | 192.168.4.38:4660 | 2:0X:4 | Read | Always
MSA_BT_Enfriadora.Estado_bomba2_Evaporador | 192.168.4.38:4660 | 2:0X:5 | Read | Always
MSA_BT_Enfriadora.Estado_bomba_recuperador | 192.168.4.38:4660 | 2:0X:6 | Read | Always
MSA_BT_Enfriadora.Estado_bomba_condensacion | 192.168.4.38:4660 | 2:0X:7 | Read | Always
MSA_BT_Enfriadora.Estado_bomba_secundario_para_agua | 192.168.4.38:4660 | 2:0X:8 | Read | Always
MSA_BT_Enfriadora.Orden_marcha_desde_supervisor | 192.168.4.38:4660 | 2:0X:9 | Read+Write | Always
MSA_BT_Enfriadora.Habilitar_cambio_modo_operacion_desde_supervisor | 192.168.4.38:4660 | 2:0X:12 | Read | Always
MSA_BT_Enfriadora.Consigna_temperatura_enfriadora | 192.168.4.38:4660 | 2:4X:2 | Read+Write | Always | 10000000
MSA_BT_Enfriadora.Consigna_temperatura_bomba_calor | 192.168.4.38:4660 | 2:4X:3 | Read+Write | Always | 10000000
MSA_BT_Enfriadora.Consigna_recuperacion | 192.168.4.38:4660 | 2:4X:4 | Read+Write | Always | 10000000
MSA_BT_Enfriadora.Banda_ajuste_temperatura | 192.168.4.38:4660 | 2:4X:5 | Read+Write | Always | 10000000
MSA_BT_Enfriadora.Banda_ajuste_recuperacion | 192.168.4.38:4660 | 2:4X:6 | Read+Write | Always | 10000000
MSA_BT_Enfriadora.Temperatura_entrada_evaporador | 192.168.4.38:4660 | 2:4X:7 | Read | Always | 10000000
MSA_BT_Enfriadora.Temperatura_salida_evaporador | 192.168.4.38:4660 | 2:4X:8 | Read | Always | 10000000
MSA_BT_Enfriadora.Temperatura_entrada_condensador | 192.168.4.38:4660 | 2:4X:9 | Read | Always | 10000000
MSA_BT_Enfriadora.Temperatura_salida_condensador | 192.168.4.38:4660 | 2:4X:10 | Read | Always | 10000000
MSA_BT_Enfriadora.Temperatura_entrada_recuperador | 192.168.4.38:4660 | 2:4X:11 | Read | Always | 10000000
MSA_BT_Enfriadora.Temperatura_salida_recuperador | 192.168.4.38:4660 | 2:4X:12 | Read | Always | 10000000
MSA_BT_Enfriadora.Transuctor_alta_presion1 | 192.168.4.38:4660 | 2:4X:13 | Read | Always | 10000000
MSA_BT_Enfriadora.Transuctor_alta_presion2 | 192.168.4.38:4660 | 2:4X:14 | Read | Always | 10000000
MSA_BT_Enfriadora.Transuctor_alta_presion3 | 192.168.4.38:4660 | 2:4X:15 | Read | Always | 10000000
MSA_BT_Enfriadora.Transuctor_alta_presion4 | 192.168.4.38:4660 | 2:4X:16 | Read | Always | 10000000
MSA_BT_Enfriadora.Transuctor_baja_presion1 | 192.168.4.38:4660 | 2:4X:17 | Read | Always | 10000000
MSA_BT_Enfriadora.Transuctor_baja_presion2 | 192.168.4.38:4660 | 2:4X:18 | Read | Always | 10000000
MSA_BT_Enfriadora.Transuctor_baja_presion3 | 192.168.4.38:4660 | 2:4X:19 | Read | Always | 10000000
MSA_BT_Enfriadora.Transuctor_baja_presion4 | 192.168.4.38:4660 | 2:4X:20 | Read | Always | 10000000
MSA_BT_Enfriadora.Temperatura_aire_exterior | 192.168.4.38:4660 | 2:4X:21 | Read | Always | 10000000
MSA_BT_Enfriadora.Porcentaje_demanda_compresor1 | 192.168.4.38:4660 | 2:4X:41 | Read | Always | 10000000
MSA_BT_Enfriadora.Porcentaje_demanda_compresor2 | 192.168.4.38:4660 | 2:4X:42 | Read | Always | 10000000
MSA_BT_Enfriadora.Porcentaje_demanda_compresor3 | 192.168.4.38:4660 | 2:4X:43 | Read | Always | 10000000
MSA_BT_Enfriadora.Porcentaje_demanda_compresor4 | 192.168.4.38:4660 | 2:4X:44 | Read | Always | 10000000
MSA_BT_Enfriadora.Estado_unidad_ampliado | 192.168.4.38:4660 | 2:4X:141 | Read | Always
MSA_BT_Enfriadora.Modo_operacion | 192.168.4.38:4660 | 2:4X:143 | Read+Write | Always
MSA_BT_Enfriadora.Estado_compresor1 | 192.168.4.38:4660 | 2:4X:144 | Read | Always
MSA_BT_Enfriadora.Estado_compresor2 | 192.168.4.38:4660 | 2:4X:145 | Read | Always
MSA_BT_Enfriadora.Estado_compresor3 | 192.168.4.38:4660 | 2:4X:146 | Read | Always
MSA_BT_Enfriadora.Estado_compresor4 | 192.168.4.38:4660 | 2:4X:147 | Read | Always
MSA_BT_Enfriadora.Estado_compresor5 | 192.168.4.38:4660 | 2:4X:148 | Read | Always
MSA_BT_Enfriadora.Estado_compresor6 | 192.168.4.38:4660 | 2:4X:149 | Read | Always
MSA_BT_Enfriadora.Horas_compresor1 | 192.168.4.38:4660 | 2:4X:184 | Read | Always
MSA_BT_Enfriadora.Horas_compresor2 | 192.168.4.38:4660 | 2:4X:186 | Read | Always
MSA_BT_Enfriadora.Horas_compresor3 | 192.168.4.38:4660 | 2:4X:188 | Read | Always
MSA_BT_Enfriadora.Horas_compresor4 | 192.168.4.38:4660 | 2:4X:190 | Read | Always
MSA_BT_Enfriadora.Horas_compresor5 | 192.168.4.38:4660 | 2:4X:192 | Read | Always
MSA_BT_Enfriadora.Horas_compresor6 | 192.168.4.38:4660 | 2:4X:194 | Read | Always
MSA_BM_Enfriadora.Estado_unidad | 192.168.4.28:4660 | 1:0X:2 | Read | Always
MSA_BM_Enfriadora.Estado_bomba1_Evaporador | 192.168.4.28:4660 | 1:0X:4 | Read | Always
MSA_BM_Enfriadora.Estado_bomba2_Evaporador | 192.168.4.28:4660 | 1:0X:5 | Read | Always
MSA_BM_Enfriadora.Estado_bomba_recuperador | 192.168.4.28:4660 | 1:0X:6 | Read | Always
MSA_BM_Enfriadora.Estado_bomba_condensacion | 192.168.4.28:4660 | 1:0X:7 | Read | Always
MSA_BM_Enfriadora.Estado_bomba_secundario_para_agua | 192.168.4.28:4660 | 1:0X:8 | Read | Always
MSA_BM_Enfriadora.Orden_marcha_desde_supervisor | 192.168.4.28:4660 | 1:0X:9 | Read+Write | Always
MSA_BM_Enfriadora.Habilitar_cambio_modo_operacion_desde_supervisor | 192.168.4.28:4660 | 1:0X:12 | Read | Always
MSA_BM_Enfriadora.Consigna_temperatura_enfriadora | 192.168.4.28:4660 | 1:4X:2 | Read+Write | Always | 10000000
MSA_BM_Enfriadora.Consigna_temperatura_bomba_calor | 192.168.4.28:4660 | 1:4X:3 | Read+Write | Always | 10000000
MSA_BM_Enfriadora.Consigna_recuperacion | 192.168.4.28:4660 | 1:4X:4 | Read+Write | Always | 10000000
MSA_BM_Enfriadora.Banda_ajuste_temperatura | 192.168.4.28:4660 | 1:4X:5 | Read+Write | Always | 10000000
MSA_BM_Enfriadora.Banda_ajuste_recuperacion | 192.168.4.28:4660 | 1:4X:6 | Read+Write | Always | 10000000
MSA_BM_Enfriadora.Temperatura_entrada_evaporador | 192.168.4.28:4660 | 1:4X:7 | Read | Always | 10000000
MSA_BM_Enfriadora.Temperatura_salida_evaporador | 192.168.4.28:4660 | 1:4X:8 | Read | Always | 10000000
MSA_BM_Enfriadora.Temperatura_entrada_condensador | 192.168.4.28:4660 | 1:4X:9 | Read | Always | 10000000
MSA_BM_Enfriadora.Temperatura_salida_condensador | 192.168.4.28:4660 | 1:4X:10 | Read | Always | 10000000
MSA_BM_Enfriadora.Temperatura_entrada_recuperador | 192.168.4.28:4660 | 1:4X:11 | Read | Always | 10000000
MSA_BM_Enfriadora.Temperatura_salida_recuperador | 192.168.4.28:4660 | 1:4X:12 | Read | Always | 10000000
MSA_BM_Enfriadora.Transuctor_alta_presion1 | 192.168.4.28:4660 | 1:4X:13 | Read | Always | 10000000
MSA_BM_Enfriadora.Transuctor_alta_presion2 | 192.168.4.28:4660 | 1:4X:14 | Read | Always | 10000000
MSA_BM_Enfriadora.Transuctor_alta_presion3 | 192.168.4.28:4660 | 1:4X:15 | Read | Always | 10000000
MSA_BM_Enfriadora.Transuctor_alta_presion4 | 192.168.4.28:4660 | 1:4X:16 | Read | Always | 10000000
MSA_BM_Enfriadora.Transuctor_baja_presion1 | 192.168.4.28:4660 | 1:4X:17 | Read | Always | 10000000
MSA_BM_Enfriadora.Transuctor_baja_presion2 | 192.168.4.28:4660 | 1:4X:18 | Read | Always | 10000000
MSA_BM_Enfriadora.Transuctor_baja_presion3 | 192.168.4.28:4660 | 1:4X:19 | Read | Always | 10000000
MSA_BM_Enfriadora.Transuctor_baja_presion4 | 192.168.4.28:4660 | 1:4X:20 | Read | Always | 10000000
MSA_BM_Enfriadora.Temperatura_aire_exterior | 192.168.4.28:4660 | 1:4X:21 | Read | Always | 10000000
MSA_BM_Enfriadora.Porcentaje_demanda_compresor1 | 192.168.4.28:4660 | 1:4X:41 | Read | Always | 10000000
MSA_BM_Enfriadora.Porcentaje_demanda_compresor2 | 192.168.4.28:4660 | 1:4X:42 | Read | Always | 10000000
MSA_BM_Enfriadora.Porcentaje_demanda_compresor3 | 192.168.4.28:4660 | 1:4X:43 | Read | Always | 10000000
MSA_BM_Enfriadora.Porcentaje_demanda_compresor4 | 192.168.4.28:4660 | 1:4X:44 | Read | Always | 10000000
MSA_BM_Enfriadora.Estado_unidad_ampliado | 192.168.4.28:4660 | 1:4X:141 | Read | Always
MSA_BM_Enfriadora.Modo_operacion | 192.168.4.28:4660 | 1:4X:143 | Read+Write | Always
MSA_BM_Enfriadora.Estado_compresor1 | 192.168.4.28:4660 | 1:4X:144 | Read | Always
MSA_BM_Enfriadora.Estado_compresor2 | 192.168.4.28:4660 | 1:4X:145 | Read | Always
MSA_BM_Enfriadora.Estado_compresor3 | 192.168.4.28:4660 | 1:4X:146 | Read | Always
MSA_BM_Enfriadora.Estado_compresor4 | 192.168.4.28:4660 | 1:4X:147 | Read | Always
MSA_BM_Enfriadora.Estado_compresor5 | 192.168.4.28:4660 | 1:4X:148 | Read | Always
MSA_BM_Enfriadora.Estado_compresor6 | 192.168.4.28:4660 | 1:4X:149 | Read | Always
MSA_BM_Enfriadora.Horas_compresor1 | 192.168.4.28:4660 | 1:4X:184 | Read | Always
MSA_BM_Enfriadora.Horas_compresor2 | 192.168.4.28:4660 | 1:4X:186 | Read | Always
MSA_BM_Enfriadora.Horas_compresor3 | 192.168.4.28:4660 | 1:4X:188 | Read | Always
MSA_BM_Enfriadora.Horas_compresor4 | 192.168.4.28:4660 | 1:4X:190 | Read | Always
MSA_BM_Enfriadora.Horas_compresor5 | 192.168.4.28:4660 | 1:4X:192 | Read | Always
MSA_BM_Enfriadora.Horas_compresor6 | 192.168.4.28:4660 | 1:4X:194 | Read | Always
MSA_UM_Enfriadora.Estado_unidad | 192.168.4.58:4660 | 4:0X:2 | Read | Always
MSA_UM_Enfriadora.Estado_bomba1_Evaporador | 192.168.4.58:4660 | 4:0X:4 | Read | Always
MSA_UM_Enfriadora.Estado_bomba2_Evaporador | 192.168.4.58:4660 | 4:0X:5 | Read | Always
MSA_UM_Enfriadora.Estado_bomba_recuperador | 192.168.4.58:4660 | 4:0X:6 | Read | Always
MSA_UM_Enfriadora.Estado_bomba_condensacion | 192.168.4.58:4660 | 4:0X:7 | Read | Always
MSA_UM_Enfriadora.Estado_bomba_secundario_para_agua | 192.168.4.58:4660 | 4:0X:8 | Read | Always
MSA_UM_Enfriadora.Orden_marcha_desde_supervisor | 192.168.4.58:4660 | 4:0X:9 | Read+Write | Always
MSA_UM_Enfriadora.Habilitar_cambio_modo_operacion_desde_supervisor | 192.168.4.58:4660 | 4:0X:12 | Read | Always
MSA_UM_Enfriadora.Consigna_temperatura_enfriadora | 192.168.4.58:4660 | 4:4X:2 | Read+Write | Always | 10000000
MSA_UM_Enfriadora.Consigna_temperatura_bomba_calor | 192.168.4.58:4660 | 4:4X:3 | Read+Write | Always | 10000000
MSA_UM_Enfriadora.Consigna_recuperacion | 192.168.4.58:4660 | 4:4X:4 | Read+Write | Always | 10000000
MSA_UM_Enfriadora.Banda_ajuste_temperatura | 192.168.4.58:4660 | 4:4X:5 | Read+Write | Always | 10000000
MSA_UM_Enfriadora.Banda_ajuste_recuperacion | 192.168.4.58:4660 | 4:4X:6 | Read+Write | Always | 10000000
MSA_UM_Enfriadora.Temperatura_entrada_evaporador | 192.168.4.58:4660 | 4:4X:7 | Read | Always | 10000000
MSA_UM_Enfriadora.Temperatura_salida_evaporador | 192.168.4.58:4660 | 4:4X:8 | Read | Always | 10000000
MSA_UM_Enfriadora.Temperatura_entrada_condensador | 192.168.4.58:4660 | 4:4X:9 | Read | Always | 10000000
MSA_UM_Enfriadora.Temperatura_salida_condensador | 192.168.4.58:4660 | 4:4X:10 | Read | Always | 10000000
MSA_UM_Enfriadora.Temperatura_entrada_recuperador | 192.168.4.58:4660 | 4:4X:11 | Read | Always | 10000000
MSA_UM_Enfriadora.Temperatura_salida_recuperador | 192.168.4.58:4660 | 4:4X:12 | Read | Always | 10000000
MSA_UM_Enfriadora.Transuctor_alta_presion1 | 192.168.4.58:4660 | 4:4X:13 | Read | Always | 10000000
MSA_UM_Enfriadora.Transuctor_alta_presion2 | 192.168.4.58:4660 | 4:4X:14 | Read | Always | 10000000
MSA_UM_Enfriadora.Transuctor_alta_presion3 | 192.168.4.58:4660 | 4:4X:15 | Read | Always | 10000000
MSA_UM_Enfriadora.Transuctor_alta_presion4 | 192.168.4.58:4660 | 4:4X:16 | Read | Always | 10000000
MSA_UM_Enfriadora.Transuctor_baja_presion1 | 192.168.4.58:4660 | 4:4X:17 | Read | Always | 10000000
MSA_UM_Enfriadora.Transuctor_baja_presion2 | 192.168.4.58:4660 | 4:4X:18 | Read | Always | 10000000
MSA_UM_Enfriadora.Transuctor_baja_presion3 | 192.168.4.58:4660 | 4:4X:19 | Read | Always | 10000000
MSA_UM_Enfriadora.Transuctor_baja_presion4 | 192.168.4.58:4660 | 4:4X:20 | Read | Always | 10000000
MSA_UM_Enfriadora.Temperatura_aire_exterior | 192.168.4.58:4660 | 4:4X:21 | Read | Always | 10000000
MSA_UM_Enfriadora.Porcentaje_demanda_compresor1 | 192.168.4.58:4660 | 4:4X:41 | Read | Always | 10000000
MSA_UM_Enfriadora.Porcentaje_demanda_compresor2 | 192.168.4.58:4660 | 4:4X:42 | Read | Always | 10000000
MSA_UM_Enfriadora.Porcentaje_demanda_compresor3 | 192.168.4.58:4660 | 4:4X:43 | Read | Always | 10000000
MSA_UM_Enfriadora.Porcentaje_demanda_compresor4 | 192.168.4.58:4660 | 4:4X:44 | Read | Always | 10000000
MSA_UM_Enfriadora.Estado_unidad_ampliado | 192.168.4.58:4660 | 4:4X:141 | Read | Always
MSA_UM_Enfriadora.Modo_operacion | 192.168.4.58:4660 | 4:4X:143 | Read+Write | Always
MSA_UM_Enfriadora.Estado_compresor1 | 192.168.4.58:4660 | 4:4X:144 | Read | Always
MSA_UM_Enfriadora.Estado_compresor2 | 192.168.4.58:4660 | 4:4X:145 | Read | Always
MSA_UM_Enfriadora.Estado_compresor3 | 192.168.4.58:4660 | 4:4X:146 | Read | Always
MSA_UM_Enfriadora.Estado_compresor4 | 192.168.4.58:4660 | 4:4X:147 | Read | Always
MSA_UM_Enfriadora.Estado_compresor5 | 192.168.4.58:4660 | 4:4X:148 | Read | Always
MSA_UM_Enfriadora.Estado_compresor6 | 192.168.4.58:4660 | 4:4X:149 | Read | Always
MSA_UM_Enfriadora.Horas_compresor1 | 192.168.4.58:4660 | 4:4X:184 | Read | Always
MSA_UM_Enfriadora.Horas_compresor2 | 192.168.4.58:4660 | 4:4X:186 | Read | Always
MSA_UM_Enfriadora.Horas_compresor3 | 192.168.4.58:4660 | 4:4X:188 | Read | Always
MSA_UM_Enfriadora.Horas_compresor4 | 192.168.4.58:4660 | 4:4X:190 | Read | Always
MSA_UM_Enfriadora.Horas_compresor5 | 192.168.4.58:4660 | 4:4X:192 | Read | Always
MSA_UM_Enfriadora.Horas_compresor6 | 192.168.4.58:4660 | 4:4X:194 | Read | Always
MSA_UT_Enfriadora.Estado_unidad | 192.168.4.48:4660 | 3:0X:2 | Read | Always
MSA_UT_Enfriadora.Estado_bomba1_Evaporador | 192.168.4.48:4660 | 3:0X:4 | Read | Always
MSA_UT_Enfriadora.Estado_bomba2_Evaporador | 192.168.4.48:4660 | 3:0X:5 | Read | Always
MSA_UT_Enfriadora.Estado_bomba_recuperador | 192.168.4.48:4660 | 3:0X:6 | Read | Always
MSA_UT_Enfriadora.Estado_bomba_condensacion | 192.168.4.48:4660 | 3:0X:7 | Read | Always
MSA_UT_Enfriadora.Estado_bomba_secundario_para_agua | 192.168.4.48:4660 | 3:0X:8 | Read | Always
MSA_UT_Enfriadora.Orden_marcha_desde_supervisor | 192.168.4.48:4660 | 3:0X:9 | Read+Write | Always
MSA_UT_Enfriadora.Habilitar_cambio_modo_operacion_desde_supervisor | 192.168.4.48:4660 | 3:0X:12 | Read | Always
MSA_UT_Enfriadora.Consigna_temperatura_enfriadora | 192.168.4.48:4660 | 3:4X:2 | Read+Write | Always | 10000000
MSA_UT_Enfriadora.Consigna_temperatura_bomba_calor | 192.168.4.48:4660 | 3:4X:3 | Read+Write | Always | 10000000
MSA_UT_Enfriadora.Consigna_recuperacion | 192.168.4.48:4660 | 3:4X:4 | Read+Write | Always | 10000000
MSA_UT_Enfriadora.Banda_ajuste_temperatura | 192.168.4.48:4660 | 3:4X:5 | Read+Write | Always | 10000000
MSA_UT_Enfriadora.Banda_ajuste_recuperacion | 192.168.4.48:4660 | 3:4X:6 | Read+Write | Always | 10000000
MSA_UT_Enfriadora.Temperatura_entrada_evaporador | 192.168.4.48:4660 | 3:4X:7 | Read | Always | 10000000
MSA_UT_Enfriadora.Temperatura_salida_evaporador | 192.168.4.48:4660 | 3:4X:8 | Read | Always | 10000000
MSA_UT_Enfriadora.Temperatura_entrada_condensador | 192.168.4.48:4660 | 3:4X:9 | Read | Always | 10000000
MSA_UT_Enfriadora.Temperatura_salida_condensador | 192.168.4.48:4660 | 3:4X:10 | Read | Always | 10000000
MSA_UT_Enfriadora.Temperatura_entrada_recuperador | 192.168.4.48:4660 | 3:4X:11 | Read | Always | 10000000
MSA_UT_Enfriadora.Temperatura_salida_recuperador | 192.168.4.48:4660 | 3:4X:12 | Read | Always | 10000000
MSA_UT_Enfriadora.Transuctor_alta_presion1 | 192.168.4.48:4660 | 3:4X:13 | Read | Always | 10000000
MSA_UT_Enfriadora.Transuctor_alta_presion2 | 192.168.4.48:4660 | 3:4X:14 | Read | Always | 10000000
MSA_UT_Enfriadora.Transuctor_alta_presion3 | 192.168.4.48:4660 | 3:4X:15 | Read | Always | 10000000
MSA_UT_Enfriadora.Transuctor_alta_presion4 | 192.168.4.48:4660 | 3:4X:16 | Read | Always | 10000000
MSA_UT_Enfriadora.Transuctor_baja_presion1 | 192.168.4.48:4660 | 3:4X:17 | Read | Always | 10000000
MSA_UT_Enfriadora.Transuctor_baja_presion2 | 192.168.4.48:4660 | 3:4X:18 | Read | Always | 10000000
MSA_UT_Enfriadora.Transuctor_baja_presion3 | 192.168.4.48:4660 | 3:4X:19 | Read | Always | 10000000
MSA_UT_Enfriadora.Transuctor_baja_presion4 | 192.168.4.48:4660 | 3:4X:20 | Read | Always | 10000000
MSA_UT_Enfriadora.Temperatura_aire_exterior | 192.168.4.48:4660 | 3:4X:21 | Read | Always | 10000000
MSA_UT_Enfriadora.Porcentaje_demanda_compresor1 | 192.168.4.48:4660 | 3:4X:41 | Read | Always | 10000000
MSA_UT_Enfriadora.Porcentaje_demanda_compresor2 | 192.168.4.48:4660 | 3:4X:42 | Read | Always | 10000000
MSA_UT_Enfriadora.Porcentaje_demanda_compresor3 | 192.168.4.48:4660 | 3:4X:43 | Read | Always | 10000000
MSA_UT_Enfriadora.Porcentaje_demanda_compresor4 | 192.168.4.48:4660 | 3:4X:44 | Read | Always | 10000000
MSA_UT_Enfriadora.Estado_unidad_ampliado | 192.168.4.48:4660 | 3:4X:141 | Read | Always
MSA_UT_Enfriadora.Modo_operacion | 192.168.4.48:4660 | 3:4X:143 | Read+Write | Always
MSA_UT_Enfriadora.Estado_compresor1 | 192.168.4.48:4660 | 3:4X:144 | Read | Always
MSA_UT_Enfriadora.Estado_compresor2 | 192.168.4.48:4660 | 3:4X:145 | Read | Always
MSA_UT_Enfriadora.Estado_compresor3 | 192.168.4.48:4660 | 3:4X:146 | Read | Always
MSA_UT_Enfriadora.Estado_compresor4 | 192.168.4.48:4660 | 3:4X:147 | Read | Always
MSA_UT_Enfriadora.Estado_compresor5 | 192.168.4.48:4660 | 3:4X:148 | Read | Always
MSA_UT_Enfriadora.Estado_compresor6 | 192.168.4.48:4660 | 3:4X:149 | Read | Always
MSA_UT_Enfriadora.Horas_compresor1 | 192.168.4.48:4660 | 3:4X:184 | Read | Always
MSA_UT_Enfriadora.Horas_compresor2 | 192.168.4.48:4660 | 3:4X:186 | Read | Always
MSA_UT_Enfriadora.Horas_compresor3 | 192.168.4.48:4660 | 3:4X:188 | Read | Always
MSA_UT_Enfriadora.Horas_compresor4 | 192.168.4.48:4660 | 3:4X:190 | Read | Always
MSA_UT_Enfriadora.Horas_compresor5 | 192.168.4.48:4660 | 3:4X:192 | Read | Always
MSA_UT_Enfriadora.Horas_compresor6 | 192.168.4.48:4660 | 3:4X:194 | Read | Always
MSA_BT_Enfriadora.codigo_alarma | 192.168.4.38:4660 | 2:4X:161 | Read | Always
MSA_BM_Enfriadora.codigo_alarma | 192.168.4.28:4660 | 1:4X:161 | Read | Always
MSA_UM_Enfriadora.codigo_alarma | 192.168.4.58:4660 | 4:4X:161 | Read | Always
MSA_UT_Enfriadora.codigo_alarma | 192.168.4.48:4660 | 3:4X:161 | Read | Always
MSA_UM_Pozo_Pluviales_Alarma_Bomba | 192.168.4.53:4660 | 9:0X:221 | Read | Always
MSA_UM_Pozo_Pluviales_Alarma_Nivel | 192.168.4.53:4660 | 9:0X:222 | Read | Always

## MBUS
|  |  | (All) | (All)
MSA_Contador_BMF01.Volumen | 78443486 | 2_V | Read | Always
MSA_Contador_BMF01.Temperatura_impulsion | 78443486 | 4_V | Read | Always
MSA_Contador_BMF01.Temperatura_retorno | 78443486 | 5_V | Read | Always
MSA_Contador_BMF01.Diferencial_temperatura | 78443486 | 6_V | Read | Always
MSA_Contador_BMF01.Potencia | 78443486 | 7_V | Read | Always | 1000000000
MSA_Contador_BMF01.Caudal_instantaneo | 78443486 | 9_V | Read | Always
MSA_Contador_BMF01.Energia_acumulada_calor | 78443486 | 1_V | Read | Always | 1000000000
MSA_Contador_BMF01.Volumen_AF | 78443486 | 13_V | Read | Always | 10000000
MSA_Contador_BMF01.Energia_acumulada_frio | 78443486 | 15_V | Read | Always | 1000000000
MSA_Contador_BMF02.Volumen | 78443482 | 2_V | Read | Always
MSA_Contador_BMF02.Temperatura_impulsion | 78443482 | 4_V | Read | Always
MSA_Contador_BMF02.Temperatura_retorno | 78443482 | 5_V | Read | Always
MSA_Contador_BMF02.Diferencial_temperatura | 78443482 | 6_V | Read | Always
MSA_Contador_BMF02.Potencia | 78443482 | 7_V | Read | Always | 1000000000
MSA_Contador_BMF02.Caudal_instantaneo | 78443482 | 9_V | Read | Always
MSA_Contador_BMF02.Energia_acumulada_calor | 78443482 | 1_V | Read | Always | 1000000000
MSA_Contador_BMF02.Volumen_AF | 78443482 | 13_V | Read | Always | 10000000
MSA_Contador_BMF02.Energia_acumulada_frio | 78443482 | 15_V | Read | Always | 1000000000
MSA_Contador_BMF03.Volumen | 78443489 | 2_V | Read | Always
MSA_Contador_BMF03.Temperatura_impulsion | 78443489 | 4_V | Read | Always
MSA_Contador_BMF03.Temperatura_retorno | 78443489 | 5_V | Read | Always
MSA_Contador_BMF03.Diferencial_temperatura | 78443489 | 6_V | Read | Always
MSA_Contador_BMF03.Potencia | 78443489 | 7_V | Read | Always | 1000000000
MSA_Contador_BMF03.Caudal_instantaneo | 78443489 | 9_V | Read | Always
MSA_Contador_BMF03.Energia_acumulada_calor | 78443489 | 1_V | Read | Always | 1000000000
MSA_Contador_BMF03.Volumen_AF | 78443489 | 13_V | Read | Always | 10000000
MSA_Contador_BMF03.Energia_acumulada_frio | 78443489 | 15_V | Read | Always | 1000000000
MSA_Contador_BMF09.Volumen | 78443484 | 2_V | Read | Always
MSA_Contador_BMF09.Temperatura_impulsion | 78443484 | 4_V | Read | Always
MSA_Contador_BMF09.Temperatura_retorno | 78443484 | 5_V | Read | Always
MSA_Contador_BMF09.Diferencial_temperatura | 78443484 | 6_V | Read | Always
MSA_Contador_BMF09.Potencia | 78443484 | 7_V | Read | Always | 1000000000
MSA_Contador_BMF09.Caudal_instantaneo | 78443484 | 9_V | Read | Always
MSA_Contador_BMF09.Energia_acumulada_calor | 78443484 | 1_V | Read | Always | 1000000000
MSA_Contador_BMF09.Volumen_AF | 78443484 | 13_V | Read | Always | 10000000
MSA_Contador_BMF09.Energia_acumulada_frio | 78443484 | 15_V | Read | Always | 1000000000
MSA_Contador_BMF08.Volumen | 78443488 | 2_V | Read | Always
MSA_Contador_BMF08.Temperatura_impulsion | 78443488 | 4_V | Read | Always
MSA_Contador_BMF08.Temperatura_retorno | 78443488 | 5_V | Read | Always
MSA_Contador_BMF08.Diferencial_temperatura | 78443488 | 6_V | Read | Always
MSA_Contador_BMF08.Potencia | 78443488 | 7_V | Read | Always | 1000000000
MSA_Contador_BMF08.Caudal_instantaneo | 78443488 | 9_V | Read | Always
MSA_Contador_BMF08.Energia_acumulada_calor | 78443488 | 1_V | Read | Always | 1000000000
MSA_Contador_BMF08.Volumen_AF | 78443488 | 13_V | Read | Always | 10000000
MSA_Contador_BMF08.Energia_acumulada_frio | 78443488 | 15_V | Read | Always | 1000000000
MSA_Contador_BMF07.Volumen | 78443450 | 2_V | Read | Always
MSA_Contador_BMF07.Temperatura_impulsion | 78443450 | 4_V | Read | Always
MSA_Contador_BMF07.Temperatura_retorno | 78443450 | 5_V | Read | Always
MSA_Contador_BMF07.Diferencial_temperatura | 78443450 | 6_V | Read | Always
MSA_Contador_BMF07.Potencia | 78443450 | 7_V | Read | Always | 1000000000
MSA_Contador_BMF07.Caudal_instantaneo | 78443450 | 9_V | Read | Always
MSA_Contador_BMF07.Energia_acumulada_calor | 78443450 | 1_V | Read | Always | 1000000000
MSA_Contador_BMF07.Volumen_AF | 78443450 | 13_V | Read | Always | 10000000
MSA_Contador_BMF07.Energia_acumulada_frio | 78443450 | 15_V | Read | Always | 1000000000
MSA_Contador_UMF14_1.Volumen | 78443462 | 2_V | Read | Always
MSA_Contador_UMF14_1.Temperatura_impulsion | 78443462 | 4_V | Read | Always
MSA_Contador_UMF14_1.Temperatura_retorno | 78443462 | 5_V | Read | Always
MSA_Contador_UMF14_1.Diferencial_temperatura | 78443462 | 6_V | Read | Always
MSA_Contador_UMF14_1.Potencia | 78443462 | 7_V | Read | Always | 1000000000
MSA_Contador_UMF14_1.Caudal_instantaneo | 78443462 | 9_V | Read | Always
MSA_Contador_UMF14_1.Energia_acumulada_calor | 78443462 | 1_V | Read | Always | 1000000000
MSA_Contador_UMF14_1.Volumen_AF | 78443462 | 13_V | Read | Always | 10000000
MSA_Contador_UMF14_1.Energia_acumulada_frio | 78443462 | 15_V | Read | Always | 1000000000
MSA_Contador_UMF14_2.Volumen | 78443459 | 2_V | Read | Always
MSA_Contador_UMF14_2.Temperatura_impulsion | 78443459 | 4_V | Read | Always
MSA_Contador_UMF14_2.Temperatura_retorno | 78443459 | 5_V | Read | Always
MSA_Contador_UMF14_2.Diferencial_temperatura | 78443459 | 6_V | Read | Always
MSA_Contador_UMF14_2.Potencia | 78443459 | 7_V | Read | Always | 1000000000
MSA_Contador_UMF14_2.Caudal_instantaneo | 78443459 | 9_V | Read | Always
MSA_Contador_UMF14_2.Energia_acumulada_calor | 78443459 | 1_V | Read | Always | 1000000000
MSA_Contador_UMF14_2.Volumen_AF | 78443459 | 13_V | Read | Always | 10000000
MSA_Contador_UMF14_2.Energia_acumulada_frio | 78443459 | 15_V | Read | Always | 1000000000
MSA_Contador_UMF09.Volumen | 78443472 | 2_V | Read | Always
MSA_Contador_UMF09.Temperatura_impulsion | 78443472 | 4_V | Read | Always
MSA_Contador_UMF09.Temperatura_retorno | 78443472 | 5_V | Read | Always
MSA_Contador_UMF09.Diferencial_temperatura | 78443472 | 6_V | Read | Always
MSA_Contador_UMF09.Potencia | 78443472 | 7_V | Read | Always | 1000000000
MSA_Contador_UMF09.Caudal_instantaneo | 78443472 | 9_V | Read | Always
MSA_Contador_UMF09.Energia_acumulada_calor | 78443472 | 1_V | Read | Always | 1000000000
MSA_Contador_UMF09.Volumen_AF | 78443472 | 13_V | Read | Always | 10000000
MSA_Contador_UMF09.Energia_acumulada_frio | 78443472 | 15_V | Read | Always | 1000000000
MSA_Contador_UMF10.Volumen | 78443464 | 2_V | Read | Always
MSA_Contador_UMF10.Temperatura_impulsion | 78443464 | 4_V | Read | Always
MSA_Contador_UMF10.Temperatura_retorno | 78443464 | 5_V | Read | Always
MSA_Contador_UMF10.Diferencial_temperatura | 78443464 | 6_V | Read | Always
MSA_Contador_UMF10.Potencia | 78443464 | 7_V | Read | Always | 1000000000
MSA_Contador_UMF10.Caudal_instantaneo | 78443464 | 9_V | Read | Always
MSA_Contador_UMF10.Energia_acumulada_calor | 78443464 | 1_V | Read | Always | 1000000000
MSA_Contador_UMF10.Volumen_AF | 78443464 | 13_V | Read | Always | 10000000
MSA_Contador_UMF10.Energia_acumulada_frio | 78443464 | 15_V | Read | Always | 1000000000
MSA_Contador_UMF11.Volumen | 78443445 | 2_V | Read | Always
MSA_Contador_UMF11.Temperatura_impulsion | 78443445 | 4_V | Read | Always
MSA_Contador_UMF11.Temperatura_retorno | 78443445 | 5_V | Read | Always
MSA_Contador_UMF11.Diferencial_temperatura | 78443445 | 6_V | Read | Always
MSA_Contador_UMF11.Potencia | 78443445 | 7_V | Read | Always | 1000000000
MSA_Contador_UMF11.Caudal_instantaneo | 78443445 | 9_V | Read | Always
MSA_Contador_UMF11.Energia_acumulada_calor | 78443445 | 1_V | Read | Always | 1000000000
MSA_Contador_UMF11.Volumen_AF | 78443445 | 13_V | Read | Always | 10000000
MSA_Contador_UMF11.Energia_acumulada_frio | 78443445 | 15_V | Read | Always | 1000000000
MSA_Contador_UMF12.Volumen | 78443461 | 2_V | Read | Always
MSA_Contador_UMF12.Temperatura_impulsion | 78443461 | 4_V | Read | Always
MSA_Contador_UMF12.Temperatura_retorno | 78443461 | 5_V | Read | Always
MSA_Contador_UMF12.Diferencial_temperatura | 78443461 | 6_V | Read | Always
MSA_Contador_UMF12.Potencia | 78443461 | 7_V | Read | Always | 1000000000
MSA_Contador_UMF12.Caudal_instantaneo | 78443461 | 9_V | Read | Always
MSA_Contador_UMF12.Energia_acumulada_calor | 78443461 | 1_V | Read | Always | 1000000000
MSA_Contador_UMF12.Volumen_AF | 78443461 | 13_V | Read | Always | 10000000
MSA_Contador_UMF12.Energia_acumulada_frio | 78443461 | 15_V | Read | Always | 1000000000
MSA_Contador_UMF13.Volumen | 78443463 | 2_V | Read | Always
MSA_Contador_UMF13.Temperatura_impulsion | 78443463 | 4_V | Read | Always
MSA_Contador_UMF13.Temperatura_retorno | 78443463 | 5_V | Read | Always
MSA_Contador_UMF13.Diferencial_temperatura | 78443463 | 6_V | Read | Always
MSA_Contador_UMF13.Potencia | 78443463 | 7_V | Read | Always | 1000000000
MSA_Contador_UMF13.Caudal_instantaneo | 78443463 | 9_V | Read | Always
MSA_Contador_UMF13.Energia_acumulada_calor | 78443463 | 1_V | Read | Always | 1000000000
MSA_Contador_UMF13.Volumen_AF | 78443463 | 13_V | Read | Always | 10000000
MSA_Contador_UMF13.Energia_acumulada_frio | 78443463 | 15_V | Read | Always | 1000000000
MSA_BM_Contador_energia_AG_Romanos_AF.Volumen | 78581688 | 2_V | Read | Always
MSA_BM_Contador_energia_AG_Romanos_AF.Temperatura_impulsion | 78581688 | 4_V | Read | Always
MSA_BM_Contador_energia_AG_Romanos_AF.Temperatura_retorno | 78581688 | 5_V | Read | Always
MSA_BM_Contador_energia_AG_Romanos_AF.Diferencial_temperatura | 78581688 | 6_V | Read | Always
MSA_BM_Contador_energia_AG_Romanos_AF.Potencia | 78581688 | 7_V | Read | Always | 1000000000
MSA_BM_Contador_energia_AG_Romanos_AF.Caudal_instantaneo | 78581688 | 9_V | Read | Always
MSA_BM_Contador_energia_AG_Romanos_AF.Energia_acumulada_calor | 78581688 | 1_V | Read | Always | 1000000000000
MSA_BM_Contador_energia_AG_Romanos_AF.Volumen_AF | 78581688 | 13_V | Read | Always | 10000000
MSA_BM_Contador_energia_AG_Romanos_AF.Energia_acumulada_frio | 78581688 | 15_V | Read | Always | 1000000000000
MSA_BM_Contador_energia_AG_Romanos_AC.Volumen | 78581692 | 2_V | Read | Always
MSA_BM_Contador_energia_AG_Romanos_AC.Temperatura_impulsion | 78581692 | 4_V | Read | Always
MSA_BM_Contador_energia_AG_Romanos_AC.Temperatura_retorno | 78581692 | 5_V | Read | Always
MSA_BM_Contador_energia_AG_Romanos_AC.Diferencial_temperatura | 78581692 | 6_V | Read | Always
MSA_BM_Contador_energia_AG_Romanos_AC.Potencia | 78581692 | 7_V | Read | Always | 1000000000
MSA_BM_Contador_energia_AG_Romanos_AC.Caudal_instantaneo | 78581692 | 9_V | Read | Always
MSA_BM_Contador_energia_AG_Romanos_AC.Energia_acumulada_calor | 78581692 | 1_V | Read | Always | 1000000000000
MSA_BM_Contador_energia_AG_Romanos_AC.Volumen_AF | 78581692 | 13_V | Read | Always | 10000000
MSA_BM_Contador_energia_AG_Romanos_AC.Energia_acumulada_frio | 78581692 | 15_V | Read | Always | 1000000000000
MSA_BM_Contador_energia_AG_Ent_Vecinal_AF.Volumen | 78581686 | 2_V | Read | Always
MSA_BM_Contador_energia_AG_Ent_Vecinal_AF.Temperatura_impulsion | 78581686 | 4_V | Read | Always
MSA_BM_Contador_energia_AG_Ent_Vecinal_AF.Temperatura_retorno | 78581686 | 5_V | Read | Always
MSA_BM_Contador_energia_AG_Ent_Vecinal_AF.Diferencial_temperatura | 78581686 | 6_V | Read | Always
MSA_BM_Contador_energia_AG_Ent_Vecinal_AF.Potencia | 78581686 | 7_V | Read | Always | 1000000000
MSA_BM_Contador_energia_AG_Ent_Vecinal_AF.Caudal_instantaneo | 78581686 | 9_V | Read | Always
MSA_BM_Contador_energia_AG_Ent_Vecinal_AF.Energia_acumulada_calor | 78581686 | 1_V | Read | Always | 1000000000000
MSA_BM_Contador_energia_AG_Ent_Vecinal_AF.Volumen_AF | 78581686 | 13_V | Read | Always | 10000000
MSA_BM_Contador_energia_AG_Ent_Vecinal_AF.Energia_acumulada_frio | 78581686 | 15_V | Read | Always | 1000000000000
MSA_BM_Contador_energia_AG_Ent_Vecinal_AC.Volumen | 78581707 | 2_V | Read | Always
MSA_BM_Contador_energia_AG_Ent_Vecinal_AC.Temperatura_impulsion | 78581707 | 4_V | Read | Always
MSA_BM_Contador_energia_AG_Ent_Vecinal_AC.Temperatura_retorno | 78581707 | 5_V | Read | Always
MSA_BM_Contador_energia_AG_Ent_Vecinal_AC.Diferencial_temperatura | 78581707 | 6_V | Read | Always
MSA_BM_Contador_energia_AG_Ent_Vecinal_AC.Potencia | 78581707 | 7_V | Read | Always | 1000000000
MSA_BM_Contador_energia_AG_Ent_Vecinal_AC.Caudal_instantaneo | 78581707 | 9_V | Read | Always
MSA_BM_Contador_energia_AG_Ent_Vecinal_AC.Energia_acumulada_calor | 78581707 | 1_V | Read | Always | 1000000000000
MSA_BM_Contador_energia_AG_Ent_Vecinal_AC.Volumen_AF | 78581707 | 13_V | Read | Always | 10000000
MSA_BM_Contador_energia_AG_Ent_Vecinal_AC.Energia_acumulada_frio | 78581707 | 15_V | Read | Always | 1000000000000
MSA_BM_Contador_energia_Geotermia_Condens.Volumen | 78581700 | 2_V | Read | Always
MSA_BM_Contador_energia_Geotermia_Condens.Temperatura_impulsion | 78581700 | 4_V | Read | Always
MSA_BM_Contador_energia_Geotermia_Condens.Temperatura_retorno | 78581700 | 5_V | Read | Always
MSA_BM_Contador_energia_Geotermia_Condens.Diferencial_temperatura | 78581700 | 6_V | Read | Always
MSA_BM_Contador_energia_Geotermia_Condens.Potencia | 78581700 | 7_V | Read | Always | 1000000000
MSA_BM_Contador_energia_Geotermia_Condens.Caudal_instantaneo | 78581700 | 9_V | Read | Always
MSA_BM_Contador_energia_Geotermia_Condens.Energia_acumulada_calor | 78581700 | 1_V | Read | Always | 1000000000000
MSA_BM_Contador_energia_Geotermia_Condens.Volumen_AF | 78581700 | 13_V | Read | Always | 10000000
MSA_BM_Contador_energia_Geotermia_Condens.Energia_acumulada_frio | 78581700 | 15_V | Read | Always | 1000000000000
MSA_BM_Contador_energia_Climas.Volumen | 78581694 | 2_V | Read | Always
MSA_BM_Contador_energia_Climas.Temperatura_impulsion | 78581694 | 4_V | Read | Always
MSA_BM_Contador_energia_Climas.Temperatura_retorno | 78581694 | 5_V | Read | Always
MSA_BM_Contador_energia_Climas.Diferencial_temperatura | 78581694 | 6_V | Read | Always
MSA_BM_Contador_energia_Climas.Potencia | 78581694 | 7_V | Read | Always | 1000000000
MSA_BM_Contador_energia_Climas.Caudal_instantaneo | 78581694 | 9_V | Read | Always
MSA_BM_Contador_energia_Climas.Energia_acumulada_calor | 78581694 | 1_V | Read | Always | 1000000000000
MSA_BM_Contador_energia_Climas.Volumen_AF | 78581694 | 13_V | Read | Always | 10000000
MSA_BM_Contador_energia_Climas.Energia_acumulada_frio | 78581694 | 15_V | Read | Always | 1000000000000
MSA_BM_Contador_energia_Geotermia_AF.Volumen | 78611276 | 2_V | Read | Always
MSA_BM_Contador_energia_Geotermia_AF.Temperatura_impulsion | 78611276 | 4_V | Read | Always
MSA_BM_Contador_energia_Geotermia_AF.Temperatura_retorno | 78611276 | 5_V | Read | Always
MSA_BM_Contador_energia_Geotermia_AF.Diferencial_temperatura | 78611276 | 6_V | Read | Always
MSA_BM_Contador_energia_Geotermia_AF.Potencia | 78611276 | 7_V | Read | Always | 1000000000
MSA_BM_Contador_energia_Geotermia_AF.Caudal_instantaneo | 78611276 | 9_V | Read | Always
MSA_BM_Contador_energia_Geotermia_AF.Energia_acumulada_calor | 78611276 | 1_V | Read | Always | 1000000000000
MSA_BM_Contador_energia_Geotermia_AF.Volumen_AF | 78611276 | 13_V | Read | Always | 10000000
MSA_BM_Contador_energia_Geotermia_AF.Energia_acumulada_frio | 78611276 | 15_V | Read | Always | 1000000000000
MSA_BM_Contador_energia_Geotermia_AC.Volumen | 78611280 | 2_V | Read | Always
MSA_BM_Contador_energia_Geotermia_AC.Temperatura_impulsion | 78611280 | 4_V | Read | Always
MSA_BM_Contador_energia_Geotermia_AC.Temperatura_retorno | 78611280 | 5_V | Read | Always
MSA_BM_Contador_energia_Geotermia_AC.Diferencial_temperatura | 78611280 | 6_V | Read | Always
MSA_BM_Contador_energia_Geotermia_AC.Potencia | 78611280 | 7_V | Read | Always | 1000000000
MSA_BM_Contador_energia_Geotermia_AC.Caudal_instantaneo | 78611280 | 9_V | Read | Always
MSA_BM_Contador_energia_Geotermia_AC.Energia_acumulada_calor | 78611280 | 1_V | Read | Always | 1000000000000
MSA_BM_Contador_energia_Geotermia_AC.Volumen_AF | 78611280 | 13_V | Read | Always | 10000000
MSA_BM_Contador_energia_Geotermia_AC.Energia_acumulada_frio | 78611280 | 15_V | Read | Always | 1000000000000

## MBUS2
|  |  | (All) | (All)
MSA_Contador_BTF14.Volumen | 78443458 | 2_V | Read | Always
MSA_Contador_BTF14.Temperatura_impulsion | 78443458 | 4_V | Read | Always
MSA_Contador_BTF14.Temperatura_retorno | 78443458 | 5_V | Read | Always
MSA_Contador_BTF14.Diferencial_temperatura | 78443458 | 6_V | Read | Always
MSA_Contador_BTF14.Potencia | 78443458 | 7_V | Read | Always | 1000000000
MSA_Contador_BTF14.Caudal_instantaneo | 78443458 | 9_V | Read | Always
MSA_Contador_BTF14.Energia_acumulada_calor | 78443458 | 1_V | Read | Always | 1000000000
MSA_Contador_BTF14.Volumen_AF | 78443458 | 13_V | Read | Always | 10000000
MSA_Contador_BTF14.Energia_acumulada_frio | 78443458 | 15_V | Read | Always | 1000000000
MSA_Contador_BTF13.Volumen | 78443457 | 2_V | Read | Always
MSA_Contador_BTF13.Temperatura_impulsion | 78443457 | 4_V | Read | Always
MSA_Contador_BTF13.Temperatura_retorno | 78443457 | 5_V | Read | Always
MSA_Contador_BTF13.Diferencial_temperatura | 78443457 | 6_V | Read | Always
MSA_Contador_BTF13.Potencia | 78443457 | 7_V | Read | Always | 1000000000
MSA_Contador_BTF13.Caudal_instantaneo | 78443457 | 9_V | Read | Always
MSA_Contador_BTF13.Energia_acumulada_calor | 78443457 | 1_V | Read | Always | 1000000000
MSA_Contador_BTF13.Volumen_AF | 78443457 | 13_V | Read | Always | 10000000
MSA_Contador_BTF13.Energia_acumulada_frio | 78443457 | 15_V | Read | Always | 1000000000
MSA_Contador_BTF12.Volumen | 78443469 | 2_V | Read | Always
MSA_Contador_BTF12.Temperatura_impulsion | 78443469 | 4_V | Read | Always
MSA_Contador_BTF12.Temperatura_retorno | 78443469 | 5_V | Read | Always
MSA_Contador_BTF12.Diferencial_temperatura | 78443469 | 6_V | Read | Always
MSA_Contador_BTF12.Potencia | 78443469 | 7_V | Read | Always | 1000000000
MSA_Contador_BTF12.Caudal_instantaneo | 78443469 | 9_V | Read | Always
MSA_Contador_BTF12.Energia_acumulada_calor | 78443469 | 1_V | Read | Always | 1000000000
MSA_Contador_BTF12.Volumen_AF | 78443469 | 13_V | Read | Always | 10000000
MSA_Contador_BTF12.Energia_acumulada_frio | 78443469 | 15_V | Read | Always | 1000000000
MSA_Contador_BTF11.Volumen | 78443466 | 2_V | Read | Always
MSA_Contador_BTF11.Temperatura_impulsion | 78443466 | 4_V | Read | Always
MSA_Contador_BTF11.Temperatura_retorno | 78443466 | 5_V | Read | Always
MSA_Contador_BTF11.Diferencial_temperatura | 78443466 | 6_V | Read | Always
MSA_Contador_BTF11.Potencia | 78443466 | 7_V | Read | Always | 1000000000
MSA_Contador_BTF11.Caudal_instantaneo | 78443466 | 9_V | Read | Always
MSA_Contador_BTF11.Energia_acumulada_calor | 78443466 | 1_V | Read | Always | 1000000000
MSA_Contador_BTF11.Volumen_AF | 78443466 | 13_V | Read | Always | 10000000
MSA_Contador_BTF11.Energia_acumulada_frio | 78443466 | 15_V | Read | Always | 1000000000
MSA_Contador_BTF10.Volumen | 78443465 | 2_V | Read | Always
MSA_Contador_BTF10.Temperatura_impulsion | 78443465 | 4_V | Read | Always
MSA_Contador_BTF10.Temperatura_retorno | 78443465 | 5_V | Read | Always
MSA_Contador_BTF10.Diferencial_temperatura | 78443465 | 6_V | Read | Always
MSA_Contador_BTF10.Potencia | 78443465 | 7_V | Read | Always | 1000000000
MSA_Contador_BTF10.Caudal_instantaneo | 78443465 | 9_V | Read | Always
MSA_Contador_BTF10.Energia_acumulada_calor | 78443465 | 1_V | Read | Always | 1000000000
MSA_Contador_BTF10.Volumen_AF | 78443465 | 13_V | Read | Always | 10000000
MSA_Contador_BTF10.Energia_acumulada_frio | 78443465 | 15_V | Read | Always | 1000000000
MSA_Contador_BTF09.Volumen | 78443468 | 2_V | Read | Always
MSA_Contador_BTF09.Temperatura_impulsion | 78443468 | 4_V | Read | Always
MSA_Contador_BTF09.Temperatura_retorno | 78443468 | 5_V | Read | Always
MSA_Contador_BTF09.Diferencial_temperatura | 78443468 | 6_V | Read | Always
MSA_Contador_BTF09.Potencia | 78443468 | 7_V | Read | Always | 1000000000
MSA_Contador_BTF09.Caudal_instantaneo | 78443468 | 9_V | Read | Always
MSA_Contador_BTF09.Energia_acumulada_calor | 78443468 | 1_V | Read | Always | 1000000000
MSA_Contador_BTF09.Volumen_AF | 78443468 | 13_V | Read | Always | 10000000
MSA_Contador_BTF09.Energia_acumulada_frio | 78443468 | 15_V | Read | Always | 1000000000
MSA_Contador_BTF08.Volumen | 78443467 | 2_V | Read | Always
MSA_Contador_BTF08.Temperatura_impulsion | 78443467 | 4_V | Read | Always
MSA_Contador_BTF08.Temperatura_retorno | 78443467 | 5_V | Read | Always
MSA_Contador_BTF08.Diferencial_temperatura | 78443467 | 6_V | Read | Always
MSA_Contador_BTF08.Potencia | 78443467 | 7_V | Read | Always | 1000000000
MSA_Contador_BTF08.Caudal_instantaneo | 78443467 | 9_V | Read | Always
MSA_Contador_BTF08.Energia_acumulada_calor | 78443467 | 1_V | Read | Always | 1000000000
MSA_Contador_BTF08.Volumen_AF | 78443467 | 13_V | Read | Always | 10000000
MSA_Contador_BTF08.Energia_acumulada_frio | 78443467 | 15_V | Read | Always | 1000000000
MSA_Contador_BTF07.Volumen | 78443452 | 2_V | Read | Always
MSA_Contador_BTF07.Temperatura_impulsion | 78443452 | 4_V | Read | Always
MSA_Contador_BTF07.Temperatura_retorno | 78443452 | 5_V | Read | Always
MSA_Contador_BTF07.Diferencial_temperatura | 78443452 | 6_V | Read | Always
MSA_Contador_BTF07.Potencia | 78443452 | 7_V | Read | Always | 1000000000
MSA_Contador_BTF07.Caudal_instantaneo | 78443452 | 9_V | Read | Always
MSA_Contador_BTF07.Energia_acumulada_calor | 78443452 | 1_V | Read | Always | 1000000000
MSA_Contador_BTF07.Volumen_AF | 78443452 | 13_V | Read | Always | 10000000
MSA_Contador_BTF07.Energia_acumulada_frio | 78443452 | 15_V | Read | Always | 1000000000
MSA_Contador_BTF01.Volumen | 78443487 | 2_V | Read | Always
MSA_Contador_BTF01.Temperatura_impulsion | 78443487 | 4_V | Read | Always
MSA_Contador_BTF01.Temperatura_retorno | 78443487 | 5_V | Read | Always
MSA_Contador_BTF01.Diferencial_temperatura | 78443487 | 6_V | Read | Always
MSA_Contador_BTF01.Potencia | 78443487 | 7_V | Read | Always | 1000000000
MSA_Contador_BTF01.Caudal_instantaneo | 78443487 | 9_V | Read | Always
MSA_Contador_BTF01.Energia_acumulada_calor | 78443487 | 1_V | Read | Always | 1000000000
MSA_Contador_BTF01.Volumen_AF | 78443487 | 13_V | Read | Always | 10000000
MSA_Contador_BTF01.Energia_acumulada_frio | 78443487 | 15_V | Read | Always | 1000000000
MSA_Contador_BTF02.Volumen | 78443481 | 2_V | Read | Always
MSA_Contador_BTF02.Temperatura_impulsion | 78443481 | 4_V | Read | Always
MSA_Contador_BTF02.Temperatura_retorno | 78443481 | 5_V | Read | Always
MSA_Contador_BTF02.Diferencial_temperatura | 78443481 | 6_V | Read | Always
MSA_Contador_BTF02.Potencia | 78443481 | 7_V | Read | Always | 1000000000
MSA_Contador_BTF02.Caudal_instantaneo | 78443481 | 9_V | Read | Always
MSA_Contador_BTF02.Energia_acumulada_calor | 78443481 | 1_V | Read | Always | 1000000000
MSA_Contador_BTF02.Volumen_AF | 78443481 | 13_V | Read | Always | 10000000
MSA_Contador_BTF02.Energia_acumulada_frio | 78443481 | 15_V | Read | Always | 1000000000
MSA_Contador_BTF03.Volumen | 78443479 | 2_V | Read | Always
MSA_Contador_BTF03.Temperatura_impulsion | 78443479 | 4_V | Read | Always
MSA_Contador_BTF03.Temperatura_retorno | 78443479 | 5_V | Read | Always
MSA_Contador_BTF03.Diferencial_temperatura | 78443479 | 6_V | Read | Always
MSA_Contador_BTF03.Potencia | 78443479 | 7_V | Read | Always | 1000000000
MSA_Contador_BTF03.Caudal_instantaneo | 78443479 | 9_V | Read | Always
MSA_Contador_BTF03.Energia_acumulada_calor | 78443479 | 1_V | Read | Always | 1000000000
MSA_Contador_BTF03.Volumen_AF | 78443479 | 13_V | Read | Always | 10000000
MSA_Contador_BTF03.Energia_acumulada_frio | 78443479 | 15_V | Read | Always | 1000000000
MSA_Contador_BTF04.Volumen | 78443492 | 2_V | Read | Always
MSA_Contador_BTF04.Temperatura_impulsion | 78443492 | 4_V | Read | Always
MSA_Contador_BTF04.Temperatura_retorno | 78443492 | 5_V | Read | Always
MSA_Contador_BTF04.Diferencial_temperatura | 78443492 | 6_V | Read | Always
MSA_Contador_BTF04.Potencia | 78443492 | 7_V | Read | Always | 1000000000
MSA_Contador_BTF04.Caudal_instantaneo | 78443492 | 9_V | Read | Always
MSA_Contador_BTF04.Energia_acumulada_calor | 78443492 | 1_V | Read | Always | 1000000000
MSA_Contador_BTF04.Volumen_AF | 78443492 | 13_V | Read | Always | 10000000
MSA_Contador_BTF04.Energia_acumulada_frio | 78443492 | 15_V | Read | Always | 1000000000
MSA_Contador_BTF05.Volumen | 78443477 | 2_V | Read | Always
MSA_Contador_BTF05.Temperatura_impulsion | 78443477 | 4_V | Read | Always
MSA_Contador_BTF05.Temperatura_retorno | 78443477 | 5_V | Read | Always
MSA_Contador_BTF05.Diferencial_temperatura | 78443477 | 6_V | Read | Always
MSA_Contador_BTF05.Potencia | 78443477 | 7_V | Read | Always | 1000000000
MSA_Contador_BTF05.Caudal_instantaneo | 78443477 | 9_V | Read | Always
MSA_Contador_BTF05.Energia_acumulada_calor | 78443477 | 1_V | Read | Always | 1000000000
MSA_Contador_BTF05.Volumen_AF | 78443477 | 13_V | Read | Always | 10000000
MSA_Contador_BTF05.Energia_acumulada_frio | 78443477 | 15_V | Read | Always | 1000000000
MSA_Contador_BTF06.Volumen | 78443454 | 2_V | Read | Always
MSA_Contador_BTF06.Temperatura_impulsion | 78443454 | 4_V | Read | Always
MSA_Contador_BTF06.Temperatura_retorno | 78443454 | 5_V | Read | Always
MSA_Contador_BTF06.Diferencial_temperatura | 78443454 | 6_V | Read | Always
MSA_Contador_BTF06.Potencia | 78443454 | 7_V | Read | Always | 1000000000
MSA_Contador_BTF06.Caudal_instantaneo | 78443454 | 9_V | Read | Always
MSA_Contador_BTF06.Energia_acumulada_calor | 78443454 | 1_V | Read | Always | 1000000000
MSA_Contador_BTF06.Volumen_AF | 78443454 | 13_V | Read | Always | 10000000
MSA_Contador_BTF06.Energia_acumulada_frio | 78443454 | 15_V | Read | Always | 1000000000
MSA_Contador_BMF06.Volumen | 78600060 | 2_V | Read | Always
MSA_Contador_BMF06.Temperatura_impulsion | 78600060 | 4_V | Read | Always
MSA_Contador_BMF06.Temperatura_retorno | 78600060 | 5_V | Read | Always
MSA_Contador_BMF06.Diferencial_temperatura | 78600060 | 6_V | Read | Always
MSA_Contador_BMF06.Potencia | 78600060 | 7_V | Read | Always | 1000000000
MSA_Contador_BMF06.Caudal_instantaneo | 78600060 | 9_V | Read | Always
MSA_Contador_BMF06.Energia_acumulada_calor | 78600060 | 1_V | Read | Always | 1000000000
MSA_Contador_BMF06.Volumen_AF | 78600060 | 13_V | Read | Always | 10000000
MSA_Contador_BMF06.Energia_acumulada_frio | 78600060 | 15_V | Read | Always | 1000000000
MSA_Contador_BMF05.Volumen | 78443451 | 2_V | Read | Always
MSA_Contador_BMF05.Temperatura_impulsion | 78443451 | 4_V | Read | Always
MSA_Contador_BMF05.Temperatura_retorno | 78443451 | 5_V | Read | Always
MSA_Contador_BMF05.Diferencial_temperatura | 78443451 | 6_V | Read | Always
MSA_Contador_BMF05.Potencia | 78443451 | 7_V | Read | Always | 1000000000
MSA_Contador_BMF05.Caudal_instantaneo | 78443451 | 9_V | Read | Always
MSA_Contador_BMF05.Energia_acumulada_calor | 78443451 | 1_V | Read | Always | 1000000000
MSA_Contador_BMF05.Volumen_AF | 78443451 | 13_V | Read | Always | 10000000
MSA_Contador_BMF05.Energia_acumulada_frio | 78443451 | 15_V | Read | Always | 1000000000
MSA_Contador_BMF04.Volumen | 78443491 | 2_V | Read | Always
MSA_Contador_BMF04.Temperatura_impulsion | 78443491 | 4_V | Read | Always
MSA_Contador_BMF04.Temperatura_retorno | 78443491 | 5_V | Read | Always
MSA_Contador_BMF04.Diferencial_temperatura | 78443491 | 6_V | Read | Always
MSA_Contador_BMF04.Potencia | 78443491 | 7_V | Read | Always | 1000000000
MSA_Contador_BMF04.Caudal_instantaneo | 78443491 | 9_V | Read | Always
MSA_Contador_BMF04.Energia_acumulada_calor | 78443491 | 1_V | Read | Always | 1000000000
MSA_Contador_BMF04.Volumen_AF | 78443491 | 13_V | Read | Always | 10000000
MSA_Contador_BMF04.Energia_acumulada_frio | 78443491 | 15_V | Read | Always | 1000000000
MSA_BT_Contador_energia_Geotermia_AC.Volumen | 78611277 | 2_V | Read | Always
MSA_BT_Contador_energia_Geotermia_AC.Temperatura_impulsion | 78611277 | 4_V | Read | Always
MSA_BT_Contador_energia_Geotermia_AC.Temperatura_retorno | 78611277 | 5_V | Read | Always
MSA_BT_Contador_energia_Geotermia_AC.Diferencial_temperatura | 78611277 | 6_V | Read | Always
MSA_BT_Contador_energia_Geotermia_AC.Potencia | 78611277 | 7_V | Read | Always | 1000000000
MSA_BT_Contador_energia_Geotermia_AC.Caudal_instantaneo | 78611277 | 9_V | Read | Always
MSA_BT_Contador_energia_Geotermia_AC.Energia_acumulada_calor | 78611277 | 1_V | Read | Always | 1000000000000
MSA_BT_Contador_energia_Geotermia_AC.Volumen_AF | 78611277 | 13_V | Read | Always | 10000000
MSA_BT_Contador_energia_Geotermia_AC.Energia_acumulada_frio | 78611277 | 15_V | Read | Always | 1000000000000
MSA_BT_Contador_energia_Geotermia_AF.Volumen | 78611275 | 2_V | Read | Always
MSA_BT_Contador_energia_Geotermia_AF.Temperatura_impulsion | 78611275 | 4_V | Read | Always
MSA_BT_Contador_energia_Geotermia_AF.Temperatura_retorno | 78611275 | 5_V | Read | Always
MSA_BT_Contador_energia_Geotermia_AF.Diferencial_temperatura | 78611275 | 6_V | Read | Always
MSA_BT_Contador_energia_Geotermia_AF.Potencia | 78611275 | 7_V | Read | Always | 1000000000
MSA_BT_Contador_energia_Geotermia_AF.Caudal_instantaneo | 78611275 | 9_V | Read | Always
MSA_BT_Contador_energia_Geotermia_AF.Energia_acumulada_calor | 78611275 | 1_V | Read | Always | 1000000000000
MSA_BT_Contador_energia_Geotermia_AF.Volumen_AF | 78611275 | 13_V | Read | Always | 10000000
MSA_BT_Contador_energia_Geotermia_AF.Energia_acumulada_frio | 78611275 | 15_V | Read | Always | 1000000000000
MSA_BT_Contador_energia_Geotermia_Condens.Volumen | 78581699 | 2_V | Read | Always
MSA_BT_Contador_energia_Geotermia_Condens.Temperatura_impulsion | 78581699 | 4_V | Read | Always
MSA_BT_Contador_energia_Geotermia_Condens.Temperatura_retorno | 78581699 | 5_V | Read | Always
MSA_BT_Contador_energia_Geotermia_Condens.Diferencial_temperatura | 78581699 | 6_V | Read | Always
MSA_BT_Contador_energia_Geotermia_Condens.Potencia | 78581699 | 7_V | Read | Always | 1000000000
MSA_BT_Contador_energia_Geotermia_Condens.Caudal_instantaneo | 78581699 | 9_V | Read | Always
MSA_BT_Contador_energia_Geotermia_Condens.Energia_acumulada_calor | 78581699 | 1_V | Read | Always | 1000000000000
MSA_BT_Contador_energia_Geotermia_Condens.Volumen_AF | 78581699 | 13_V | Read | Always | 10000000
MSA_BT_Contador_energia_Geotermia_Condens.Energia_acumulada_frio | 78581699 | 15_V | Read | Always | 1000000000000
MSA_BT_Contador_energia_Climas.Volumen | 78581693 | 2_V | Read | Always
MSA_BT_Contador_energia_Climas.Temperatura_impulsion | 78581693 | 4_V | Read | Always
MSA_BT_Contador_energia_Climas.Temperatura_retorno | 78581693 | 5_V | Read | Always
MSA_BT_Contador_energia_Climas.Diferencial_temperatura | 78581693 | 6_V | Read | Always
MSA_BT_Contador_energia_Climas.Potencia | 78581693 | 7_V | Read | Always | 1000000000
MSA_BT_Contador_energia_Climas.Caudal_instantaneo | 78581693 | 9_V | Read | Always
MSA_BT_Contador_energia_Climas.Energia_acumulada_calor | 78581693 | 1_V | Read | Always | 1000000000000
MSA_BT_Contador_energia_Climas.Volumen_AF | 78581693 | 13_V | Read | Always | 10000000
MSA_BT_Contador_energia_Climas.Energia_acumulada_frio | 78581693 | 15_V | Read | Always | 1000000000000
MSA_BT_Contador_energia_AG_Local_Com_02_AC.Volumen | 78581689 | 2_V | Read | Always
MSA_BT_Contador_energia_AG_Local_Com_02_AC.Temperatura_impulsion | 78581689 | 4_V | Read | Always
MSA_BT_Contador_energia_AG_Local_Com_02_AC.Temperatura_retorno | 78581689 | 5_V | Read | Always
MSA_BT_Contador_energia_AG_Local_Com_02_AC.Diferencial_temperatura | 78581689 | 6_V | Read | Always
MSA_BT_Contador_energia_AG_Local_Com_02_AC.Potencia | 78581689 | 7_V | Read | Always | 1000000000
MSA_BT_Contador_energia_AG_Local_Com_02_AC.Caudal_instantaneo | 78581689 | 9_V | Read | Always
MSA_BT_Contador_energia_AG_Local_Com_02_AC.Energia_acumulada_calor | 78581689 | 1_V | Read | Always | 1000000000000
MSA_BT_Contador_energia_AG_Local_Com_02_AC.Volumen_AF | 78581689 | 13_V | Read | Always | 10000000
MSA_BT_Contador_energia_AG_Local_Com_02_AC.Energia_acumulada_frio | 78581689 | 15_V | Read | Always | 1000000000000
MSA_BT_Contador_energia_AG_Local_Com_02_AF.Volumen | 78635357 | 2_V | Read | Always
MSA_BT_Contador_energia_AG_Local_Com_02_AF.Temperatura_impulsion | 78635357 | 4_V | Read | Always
MSA_BT_Contador_energia_AG_Local_Com_02_AF.Temperatura_retorno | 78635357 | 5_V | Read | Always
MSA_BT_Contador_energia_AG_Local_Com_02_AF.Diferencial_temperatura | 78635357 | 6_V | Read | Always
MSA_BT_Contador_energia_AG_Local_Com_02_AF.Potencia | 78635357 | 7_V | Read | Always | 1000000000
MSA_BT_Contador_energia_AG_Local_Com_02_AF.Caudal_instantaneo | 78635357 | 9_V | Read | Always
MSA_BT_Contador_energia_AG_Local_Com_02_AF.Energia_acumulada_calor | 78635357 | 1_V | Read | Always | 1000000000000
MSA_BT_Contador_energia_AG_Local_Com_02_AF.Volumen_AF | 78635357 | 13_V | Read | Always | 10000000
MSA_BT_Contador_energia_AG_Local_Com_02_AF.Energia_acumulada_frio | 78635357 | 15_V | Read | Always | 1000000000000
|  |  | Read+Write | Always

## MBUS3
|  |  | (All) | (All)
MSA_Contador_UTF16.Volumen | 78443490 | 2_V | Read | Always
MSA_Contador_UTF16.Temperatura_impulsion | 78443490 | 4_V | Read | Always
MSA_Contador_UTF16.Temperatura_retorno | 78443490 | 5_V | Read | Always
MSA_Contador_UTF16.Diferencial_temperatura | 78443490 | 6_V | Read | Always
MSA_Contador_UTF16.Potencia | 78443490 | 7_V | Read | Always | 1000000000
MSA_Contador_UTF16.Caudal_instantaneo | 78443490 | 9_V | Read | Always
MSA_Contador_UTF16.Energia_acumulada_calor | 78443490 | 1_V | Read | Always | 1000000000
MSA_Contador_UTF16.Volumen_AF | 78443490 | 13_V | Read | Always | 10000000
MSA_Contador_UTF16.Energia_acumulada_frio | 78443490 | 15_V | Read | Always | 1000000000
MSA_Contador_UTF15.Volumen | 78443456 | 2_V | Read | Always
MSA_Contador_UTF15.Temperatura_impulsion | 78443456 | 4_V | Read | Always
MSA_Contador_UTF15.Temperatura_retorno | 78443456 | 5_V | Read | Always
MSA_Contador_UTF15.Diferencial_temperatura | 78443456 | 6_V | Read | Always
MSA_Contador_UTF15.Potencia | 78443456 | 7_V | Read | Always | 1000000000
MSA_Contador_UTF15.Caudal_instantaneo | 78443456 | 9_V | Read | Always
MSA_Contador_UTF15.Energia_acumulada_calor | 78443456 | 1_V | Read | Always | 1000000000
MSA_Contador_UTF15.Volumen_AF | 78443456 | 13_V | Read | Always | 10000000
MSA_Contador_UTF15.Energia_acumulada_frio | 78443456 | 15_V | Read | Always | 1000000000
MSA_Contador_UTF14.Volumen | 78443444 | 2_V | Read | Always
MSA_Contador_UTF14.Temperatura_impulsion | 78443444 | 4_V | Read | Always
MSA_Contador_UTF14.Temperatura_retorno | 78443444 | 5_V | Read | Always
MSA_Contador_UTF14.Diferencial_temperatura | 78443444 | 6_V | Read | Always
MSA_Contador_UTF14.Potencia | 78443444 | 7_V | Read | Always | 1000000000
MSA_Contador_UTF14.Caudal_instantaneo | 78443444 | 9_V | Read | Always
MSA_Contador_UTF14.Energia_acumulada_calor | 78443444 | 1_V | Read | Always | 1000000000
MSA_Contador_UTF14.Volumen_AF | 78443444 | 13_V | Read | Always | 10000000
MSA_Contador_UTF14.Energia_acumulada_frio | 78443444 | 15_V | Read | Always | 1000000000
MSA_Contador_UTF13.Volumen | 78443446 | 2_V | Read | Always
MSA_Contador_UTF13.Temperatura_impulsion | 78443446 | 4_V | Read | Always
MSA_Contador_UTF13.Temperatura_retorno | 78443446 | 5_V | Read | Always
MSA_Contador_UTF13.Diferencial_temperatura | 78443446 | 6_V | Read | Always
MSA_Contador_UTF13.Potencia | 78443446 | 7_V | Read | Always | 1000000000
MSA_Contador_UTF13.Caudal_instantaneo | 78443446 | 9_V | Read | Always
MSA_Contador_UTF13.Energia_acumulada_calor | 78443446 | 1_V | Read | Always | 1000000000
MSA_Contador_UTF13.Volumen_AF | 78443446 | 13_V | Read | Always | 10000000
MSA_Contador_UTF13.Energia_acumulada_frio | 78443446 | 15_V | Read | Always | 1000000000
MSA_Contador_UTF12.Volumen | 78443443 | 2_V | Read | Always
MSA_Contador_UTF12.Temperatura_impulsion | 78443443 | 4_V | Read | Always
MSA_Contador_UTF12.Temperatura_retorno | 78443443 | 5_V | Read | Always
MSA_Contador_UTF12.Diferencial_temperatura | 78443443 | 6_V | Read | Always
MSA_Contador_UTF12.Potencia | 78443443 | 7_V | Read | Always | 1000000000
MSA_Contador_UTF12.Caudal_instantaneo | 78443443 | 9_V | Read | Always
MSA_Contador_UTF12.Energia_acumulada_calor | 78443443 | 1_V | Read | Always | 1000000000
MSA_Contador_UTF12.Volumen_AF | 78443443 | 13_V | Read | Always | 10000000
MSA_Contador_UTF12.Energia_acumulada_frio | 78443443 | 15_V | Read | Always | 1000000000
MSA_Contador_UTF11.Volumen | 78443449 | 2_V | Read | Always
MSA_Contador_UTF11.Temperatura_impulsion | 78443449 | 4_V | Read | Always
MSA_Contador_UTF11.Temperatura_retorno | 78443449 | 5_V | Read | Always
MSA_Contador_UTF11.Diferencial_temperatura | 78443449 | 6_V | Read | Always
MSA_Contador_UTF11.Potencia | 78443449 | 7_V | Read | Always | 1000000000
MSA_Contador_UTF11.Caudal_instantaneo | 78443449 | 9_V | Read | Always
MSA_Contador_UTF11.Energia_acumulada_calor | 78443449 | 1_V | Read | Always | 1000000000
MSA_Contador_UTF11.Volumen_AF | 78443449 | 13_V | Read | Always | 10000000
MSA_Contador_UTF11.Energia_acumulada_frio | 78443449 | 15_V | Read | Always | 1000000000
MSA_Contador_UMF05.Volumen | 78443493 | 2_V | Read | Always
MSA_Contador_UMF05.Temperatura_impulsion | 78443493 | 4_V | Read | Always
MSA_Contador_UMF05.Temperatura_retorno | 78443493 | 5_V | Read | Always
MSA_Contador_UMF05.Diferencial_temperatura | 78443493 | 6_V | Read | Always
MSA_Contador_UMF05.Potencia | 78443493 | 7_V | Read | Always | 1000000000
MSA_Contador_UMF05.Caudal_instantaneo | 78443493 | 9_V | Read | Always
MSA_Contador_UMF05.Energia_acumulada_calor | 78443493 | 1_V | Read | Always | 1000000000
MSA_Contador_UMF05.Volumen_AF | 78443493 | 13_V | Read | Always | 10000000
MSA_Contador_UMF05.Energia_acumulada_frio | 78443493 | 15_V | Read | Always | 1000000000
MSA_Contador_UMF06.Volumen | 78443442 | 2_V | Read | Always
MSA_Contador_UMF06.Temperatura_impulsion | 78443442 | 4_V | Read | Always
MSA_Contador_UMF06.Temperatura_retorno | 78443442 | 5_V | Read | Always
MSA_Contador_UMF06.Diferencial_temperatura | 78443442 | 6_V | Read | Always
MSA_Contador_UMF06.Potencia | 78443442 | 7_V | Read | Always | 1000000000
MSA_Contador_UMF06.Caudal_instantaneo | 78443442 | 9_V | Read | Always
MSA_Contador_UMF06.Energia_acumulada_calor | 78443442 | 1_V | Read | Always | 1000000000
MSA_Contador_UMF06.Volumen_AF | 78443442 | 13_V | Read | Always | 10000000
MSA_Contador_UMF06.Energia_acumulada_frio | 78443442 | 15_V | Read | Always | 1000000000
MSA_Contador_UMF07.Volumen | 78443441 | 2_V | Read | Always
MSA_Contador_UMF07.Temperatura_impulsion | 78443441 | 4_V | Read | Always
MSA_Contador_UMF07.Temperatura_retorno | 78443441 | 5_V | Read | Always
MSA_Contador_UMF07.Diferencial_temperatura | 78443441 | 6_V | Read | Always
MSA_Contador_UMF07.Potencia | 78443441 | 7_V | Read | Always | 1000000000
MSA_Contador_UMF07.Caudal_instantaneo | 78443441 | 9_V | Read | Always
MSA_Contador_UMF07.Energia_acumulada_calor | 78443441 | 1_V | Read | Always | 1000000000
MSA_Contador_UMF07.Volumen_AF | 78443441 | 13_V | Read | Always | 10000000
MSA_Contador_UMF07.Energia_acumulada_frio | 78443441 | 15_V | Read | Always | 1000000000
MSA_Contador_UTF07.Volumen | 78443455 | 2_V | Read | Always
MSA_Contador_UTF07.Temperatura_impulsion | 78443455 | 4_V | Read | Always
MSA_Contador_UTF07.Temperatura_retorno | 78443455 | 5_V | Read | Always
MSA_Contador_UTF07.Diferencial_temperatura | 78443455 | 6_V | Read | Always
MSA_Contador_UTF07.Potencia | 78443455 | 7_V | Read | Always | 1000000000
MSA_Contador_UTF07.Caudal_instantaneo | 78443455 | 9_V | Read | Always
MSA_Contador_UTF07.Energia_acumulada_calor | 78443455 | 1_V | Read | Always | 1000000000
MSA_Contador_UTF07.Volumen_AF | 78443455 | 13_V | Read | Always | 10000000
MSA_Contador_UTF07.Energia_acumulada_frio | 78443455 | 15_V | Read | Always | 1000000000
MSA_Contador_UTF09.Volumen | 78443460 | 2_V | Read | Always
MSA_Contador_UTF09.Temperatura_impulsion | 78443460 | 4_V | Read | Always
MSA_Contador_UTF09.Temperatura_retorno | 78443460 | 5_V | Read | Always
MSA_Contador_UTF09.Diferencial_temperatura | 78443460 | 6_V | Read | Always
MSA_Contador_UTF09.Potencia | 78443460 | 7_V | Read | Always | 1000000000
MSA_Contador_UTF09.Caudal_instantaneo | 78443460 | 9_V | Read | Always
MSA_Contador_UTF09.Energia_acumulada_calor | 78443460 | 1_V | Read | Always | 1000000000
MSA_Contador_UTF09.Volumen_AF | 78443460 | 13_V | Read | Always | 10000000
MSA_Contador_UTF09.Energia_acumulada_frio | 78443460 | 15_V | Read | Always | 1000000000
MSA_Contador_UTF08.Volumen | 78443447 | 2_V | Read | Always
MSA_Contador_UTF08.Temperatura_impulsion | 78443447 | 4_V | Read | Always
MSA_Contador_UTF08.Temperatura_retorno | 78443447 | 5_V | Read | Always
MSA_Contador_UTF08.Diferencial_temperatura | 78443447 | 6_V | Read | Always
MSA_Contador_UTF08.Potencia | 78443447 | 7_V | Read | Always | 1000000000
MSA_Contador_UTF08.Caudal_instantaneo | 78443447 | 9_V | Read | Always
MSA_Contador_UTF08.Energia_acumulada_calor | 78443447 | 1_V | Read | Always | 1000000000
MSA_Contador_UTF08.Volumen_AF | 78443447 | 13_V | Read | Always | 10000000
MSA_Contador_UTF08.Energia_acumulada_frio | 78443447 | 15_V | Read | Always | 1000000000
MSA_Contador_UTF10.Volumen | 78443448 | 2_V | Read | Always
MSA_Contador_UTF10.Temperatura_impulsion | 78443448 | 4_V | Read | Always
MSA_Contador_UTF10.Temperatura_retorno | 78443448 | 5_V | Read | Always
MSA_Contador_UTF10.Diferencial_temperatura | 78443448 | 6_V | Read | Always
MSA_Contador_UTF10.Potencia | 78443448 | 7_V | Read | Always | 1000000000
MSA_Contador_UTF10.Caudal_instantaneo | 78443448 | 9_V | Read | Always
MSA_Contador_UTF10.Energia_acumulada_calor | 78443448 | 1_V | Read | Always | 1000000000
MSA_Contador_UTF10.Volumen_AF | 78443448 | 13_V | Read | Always | 10000000
MSA_Contador_UTF10.Energia_acumulada_frio | 78443448 | 15_V | Read | Always | 1000000000
MSA_Contador_UTF06.Volumen | 78443440 | 2_V | Read | Always
MSA_Contador_UTF06.Temperatura_impulsion | 78443440 | 4_V | Read | Always
MSA_Contador_UTF06.Temperatura_retorno | 78443440 | 5_V | Read | Always
MSA_Contador_UTF06.Diferencial_temperatura | 78443440 | 6_V | Read | Always
MSA_Contador_UTF06.Potencia | 78443440 | 7_V | Read | Always | 1000000000
MSA_Contador_UTF06.Caudal_instantaneo | 78443440 | 9_V | Read | Always
MSA_Contador_UTF06.Energia_acumulada_calor | 78443440 | 1_V | Read | Always | 1000000000
MSA_Contador_UTF06.Volumen_AF | 78443440 | 13_V | Read | Always | 10000000
MSA_Contador_UTF06.Energia_acumulada_frio | 78443440 | 15_V | Read | Always | 1000000000
MSA_Contador_UMF08.Volumen | 78443453 | 2_V | Read | Always
MSA_Contador_UMF08.Temperatura_impulsion | 78443453 | 4_V | Read | Always
MSA_Contador_UMF08.Temperatura_retorno | 78443453 | 5_V | Read | Always
MSA_Contador_UMF08.Diferencial_temperatura | 78443453 | 6_V | Read | Always
MSA_Contador_UMF08.Potencia | 78443453 | 7_V | Read | Always | 1000000000
MSA_Contador_UMF08.Caudal_instantaneo | 78443453 | 9_V | Read | Always
MSA_Contador_UMF08.Energia_acumulada_calor | 78443453 | 1_V | Read | Always | 1000000000
MSA_Contador_UMF08.Volumen_AF | 78443453 | 13_V | Read | Always | 10000000
MSA_Contador_UMF08.Energia_acumulada_frio | 78443453 | 15_V | Read | Always | 1000000000
MSA_Contador_UTF01.Volumen | 78443485 | 2_V | Read | Always
MSA_Contador_UTF01.Temperatura_impulsion | 78443485 | 4_V | Read | Always
MSA_Contador_UTF01.Temperatura_retorno | 78443485 | 5_V | Read | Always
MSA_Contador_UTF01.Diferencial_temperatura | 78443485 | 6_V | Read | Always
MSA_Contador_UTF01.Potencia | 78443485 | 7_V | Read | Always | 1000000000
MSA_Contador_UTF01.Caudal_instantaneo | 78443485 | 9_V | Read | Always
MSA_Contador_UTF01.Energia_acumulada_calor | 78443485 | 1_V | Read | Always | 1000000000
MSA_Contador_UTF01.Volumen_AF | 78443485 | 13_V | Read | Always | 10000000
MSA_Contador_UTF01.Energia_acumulada_frio | 78443485 | 15_V | Read | Always | 1000000000
MSA_Contador_UTF02.Volumen | 78443473 | 2_V | Read | Always
MSA_Contador_UTF02.Temperatura_impulsion | 78443473 | 4_V | Read | Always
MSA_Contador_UTF02.Temperatura_retorno | 78443473 | 5_V | Read | Always
MSA_Contador_UTF02.Diferencial_temperatura | 78443473 | 6_V | Read | Always
MSA_Contador_UTF02.Potencia | 78443473 | 7_V | Read | Always | 1000000000
MSA_Contador_UTF02.Caudal_instantaneo | 78443473 | 9_V | Read | Always
MSA_Contador_UTF02.Energia_acumulada_calor | 78443473 | 1_V | Read | Always | 1000000000
MSA_Contador_UTF02.Volumen_AF | 78443473 | 13_V | Read | Always | 10000000
MSA_Contador_UTF02.Energia_acumulada_frio | 78443473 | 15_V | Read | Always | 1000000000
MSA_Contador_UTF03.Volumen | 78443470 | 2_V | Read | Always
MSA_Contador_UTF03.Temperatura_impulsion | 78443470 | 4_V | Read | Always
MSA_Contador_UTF03.Temperatura_retorno | 78443470 | 5_V | Read | Always
MSA_Contador_UTF03.Diferencial_temperatura | 78443470 | 6_V | Read | Always
MSA_Contador_UTF03.Potencia | 78443470 | 7_V | Read | Always | 1000000000
MSA_Contador_UTF03.Caudal_instantaneo | 78443470 | 9_V | Read | Always
MSA_Contador_UTF03.Energia_acumulada_calor | 78443470 | 1_V | Read | Always | 1000000000
MSA_Contador_UTF03.Volumen_AF | 78443470 | 13_V | Read | Always | 10000000
MSA_Contador_UTF03.Energia_acumulada_frio | 78443470 | 15_V | Read | Always | 1000000000
MSA_Contador_UTF04.Volumen | 78443471 | 2_V | Read | Always
MSA_Contador_UTF04.Temperatura_impulsion | 78443471 | 4_V | Read | Always
MSA_Contador_UTF04.Temperatura_retorno | 78443471 | 5_V | Read | Always
MSA_Contador_UTF04.Diferencial_temperatura | 78443471 | 6_V | Read | Always
MSA_Contador_UTF04.Potencia | 78443471 | 7_V | Read | Always | 1000000000
MSA_Contador_UTF04.Caudal_instantaneo | 78443471 | 9_V | Read | Always
MSA_Contador_UTF04.Energia_acumulada_calor | 78443471 | 1_V | Read | Always | 1000000000
MSA_Contador_UTF04.Volumen_AF | 78443471 | 13_V | Read | Always | 10000000
MSA_Contador_UTF04.Energia_acumulada_frio | 78443471 | 15_V | Read | Always | 1000000000
MSA_Contador_UTF05.Volumen | 78443474 | 2_V | Read | Always
MSA_Contador_UTF05.Temperatura_impulsion | 78443474 | 4_V | Read | Always
MSA_Contador_UTF05.Temperatura_retorno | 78443474 | 5_V | Read | Always
MSA_Contador_UTF05.Diferencial_temperatura | 78443474 | 6_V | Read | Always
MSA_Contador_UTF05.Potencia | 78443474 | 7_V | Read | Always | 1000000000
MSA_Contador_UTF05.Caudal_instantaneo | 78443474 | 9_V | Read | Always
MSA_Contador_UTF05.Energia_acumulada_calor | 78443474 | 1_V | Read | Always | 1000000000
MSA_Contador_UTF05.Volumen_AF | 78443474 | 13_V | Read | Always | 10000000
MSA_Contador_UTF05.Energia_acumulada_frio | 78443474 | 15_V | Read | Always | 1000000000
MSA_Contador_UMF04.Volumen | 78443478 | 2_V | Read | Always
MSA_Contador_UMF04.Temperatura_impulsion | 78443478 | 4_V | Read | Always
MSA_Contador_UMF04.Temperatura_retorno | 78443478 | 5_V | Read | Always
MSA_Contador_UMF04.Diferencial_temperatura | 78443478 | 6_V | Read | Always
MSA_Contador_UMF04.Potencia | 78443478 | 7_V | Read | Always | 1000000000
MSA_Contador_UMF04.Caudal_instantaneo | 78443478 | 9_V | Read | Always
MSA_Contador_UMF04.Energia_acumulada_calor | 78443478 | 1_V | Read | Always | 1000000000
MSA_Contador_UMF04.Volumen_AF | 78443478 | 13_V | Read | Always | 10000000
MSA_Contador_UMF04.Energia_acumulada_frio | 78443478 | 15_V | Read | Always | 1000000000
MSA_Contador_UMF03.Volumen | 78443483 | 2_V | Read | Always
MSA_Contador_UMF03.Temperatura_impulsion | 78443483 | 4_V | Read | Always
MSA_Contador_UMF03.Temperatura_retorno | 78443483 | 5_V | Read | Always
MSA_Contador_UMF03.Diferencial_temperatura | 78443483 | 6_V | Read | Always
MSA_Contador_UMF03.Potencia | 78443483 | 7_V | Read | Always | 1000000000
MSA_Contador_UMF03.Caudal_instantaneo | 78443483 | 9_V | Read | Always
MSA_Contador_UMF03.Energia_acumulada_calor | 78443483 | 1_V | Read | Always | 1000000000
MSA_Contador_UMF03.Volumen_AF | 78443483 | 13_V | Read | Always | 10000000
MSA_Contador_UMF03.Energia_acumulada_frio | 78443483 | 15_V | Read | Always | 1000000000
MSA_Contador_UMF02.Volumen | 78443480 | 2_V | Read | Always
MSA_Contador_UMF02.Temperatura_impulsion | 78443480 | 4_V | Read | Always
MSA_Contador_UMF02.Temperatura_retorno | 78443480 | 5_V | Read | Always
MSA_Contador_UMF02.Diferencial_temperatura | 78443480 | 6_V | Read | Always
MSA_Contador_UMF02.Potencia | 78443480 | 7_V | Read | Always | 1000000000
MSA_Contador_UMF02.Caudal_instantaneo | 78443480 | 9_V | Read | Always
MSA_Contador_UMF02.Energia_acumulada_calor | 78443480 | 1_V | Read | Always | 1000000000
MSA_Contador_UMF02.Volumen_AF | 78443480 | 13_V | Read | Always | 10000000
MSA_Contador_UMF02.Energia_acumulada_frio | 78443480 | 15_V | Read | Always | 1000000000
MSA_Contador_UMF01.Volumen | 78443476 | 2_V | Read | Always
MSA_Contador_UMF01.Temperatura_impulsion | 78443476 | 4_V | Read | Always
MSA_Contador_UMF01.Temperatura_retorno | 78443476 | 5_V | Read | Always
MSA_Contador_UMF01.Diferencial_temperatura | 78443476 | 6_V | Read | Always
MSA_Contador_UMF01.Potencia | 78443476 | 7_V | Read | Always | 1000000000
MSA_Contador_UMF01.Caudal_instantaneo | 78443476 | 9_V | Read | Always
MSA_Contador_UMF01.Energia_acumulada_calor | 78443476 | 1_V | Read | Always | 1000000000
MSA_Contador_UMF01.Volumen_AF | 78443476 | 13_V | Read | Always | 10000000
MSA_Contador_UMF01.Energia_acumulada_frio | 78443476 | 15_V | Read | Always | 1000000000
MSA_UT_Contador_energia_Geotermia_AC.Volumen | 78611279 | 2_V | Read | Always
MSA_UT_Contador_energia_Geotermia_AC.Temperatura_impulsion | 78611279 | 4_V | Read | Always
MSA_UT_Contador_energia_Geotermia_AC.Temperatura_retorno | 78611279 | 5_V | Read | Always
MSA_UT_Contador_energia_Geotermia_AC.Diferencial_temperatura | 78611279 | 6_V | Read | Always
MSA_UT_Contador_energia_Geotermia_AC.Potencia | 78611279 | 7_V | Read | Always | 1000000000
MSA_UT_Contador_energia_Geotermia_AC.Caudal_instantaneo | 78611279 | 9_V | Read | Always
MSA_UT_Contador_energia_Geotermia_AC.Energia_acumulada_calor | 78611279 | 1_V | Read | Always | 1000000000000
MSA_UT_Contador_energia_Geotermia_AC.Volumen_AF | 78611279 | 13_V | Read | Always | 10000000
MSA_UT_Contador_energia_Geotermia_AC.Energia_acumulada_frio | 78611279 | 15_V | Read | Always | 1000000000000
MSA_UT_Contador_energia_Geotermia_AF.Volumen | 78611273 | 2_V | Read | Always
MSA_UT_Contador_energia_Geotermia_AF.Temperatura_impulsion | 78611273 | 4_V | Read | Always
MSA_UT_Contador_energia_Geotermia_AF.Temperatura_retorno | 78611273 | 5_V | Read | Always
MSA_UT_Contador_energia_Geotermia_AF.Diferencial_temperatura | 78611273 | 6_V | Read | Always
MSA_UT_Contador_energia_Geotermia_AF.Potencia | 78611273 | 7_V | Read | Always | 1000000000
MSA_UT_Contador_energia_Geotermia_AF.Caudal_instantaneo | 78611273 | 9_V | Read | Always
MSA_UT_Contador_energia_Geotermia_AF.Energia_acumulada_calor | 78611273 | 1_V | Read | Always | 1000000000000
MSA_UT_Contador_energia_Geotermia_AF.Volumen_AF | 78611273 | 13_V | Read | Always | 10000000
MSA_UT_Contador_energia_Geotermia_AF.Energia_acumulada_frio | 78611273 | 15_V | Read | Always | 1000000000000
MSA_UT_Contador_energia_Geotermia_Condens.Volumen | 78581698 | 2_V | Read | Always
MSA_UT_Contador_energia_Geotermia_Condens.Temperatura_impulsion | 78581698 | 4_V | Read | Always
MSA_UT_Contador_energia_Geotermia_Condens.Temperatura_retorno | 78581698 | 5_V | Read | Always
MSA_UT_Contador_energia_Geotermia_Condens.Diferencial_temperatura | 78581698 | 6_V | Read | Always
MSA_UT_Contador_energia_Geotermia_Condens.Potencia | 78581698 | 7_V | Read | Always | 1000000000
MSA_UT_Contador_energia_Geotermia_Condens.Caudal_instantaneo | 78581698 | 9_V | Read | Always
MSA_UT_Contador_energia_Geotermia_Condens.Energia_acumulada_calor | 78581698 | 1_V | Read | Always | 1000000000000
MSA_UT_Contador_energia_Geotermia_Condens.Volumen_AF | 78581698 | 13_V | Read | Always | 10000000
MSA_UT_Contador_energia_Geotermia_Condens.Energia_acumulada_frio | 78581698 | 15_V | Read | Always | 1000000000000
MSA_UT_Contador_energia_Climas.Volumen | 78581696 | 2_V | Read | Always
MSA_UT_Contador_energia_Climas.Temperatura_impulsion | 78581696 | 4_V | Read | Always
MSA_UT_Contador_energia_Climas.Temperatura_retorno | 78581696 | 5_V | Read | Always
MSA_UT_Contador_energia_Climas.Diferencial_temperatura | 78581696 | 6_V | Read | Always
MSA_UT_Contador_energia_Climas.Potencia | 78581696 | 7_V | Read | Always | 1000000000
MSA_UT_Contador_energia_Climas.Caudal_instantaneo | 78581696 | 9_V | Read | Always
MSA_UT_Contador_energia_Climas.Energia_acumulada_calor | 78581696 | 1_V | Read | Always | 1000000000000
MSA_UT_Contador_energia_Climas.Volumen_AF | 78581696 | 13_V | Read | Always | 10000000
MSA_UT_Contador_energia_Climas.Energia_acumulada_frio | 78581696 | 15_V | Read | Always | 1000000000000
MSA_UT_Contador_energia_AG_Ent_Vecinal_AC.Volumen | 78581708 | 2_V | Read | Always
MSA_UT_Contador_energia_AG_Ent_Vecinal_AC.Temperatura_impulsion | 78581708 | 4_V | Read | Always
MSA_UT_Contador_energia_AG_Ent_Vecinal_AC.Temperatura_retorno | 78581708 | 5_V | Read | Always
MSA_UT_Contador_energia_AG_Ent_Vecinal_AC.Diferencial_temperatura | 78581708 | 6_V | Read | Always
MSA_UT_Contador_energia_AG_Ent_Vecinal_AC.Potencia | 78581708 | 7_V | Read | Always | 1000000000
MSA_UT_Contador_energia_AG_Ent_Vecinal_AC.Caudal_instantaneo | 78581708 | 9_V | Read | Always
MSA_UT_Contador_energia_AG_Ent_Vecinal_AC.Energia_acumulada_calor | 78581708 | 1_V | Read | Always | 1000000000000
MSA_UT_Contador_energia_AG_Ent_Vecinal_AC.Volumen_AF | 78581708 | 13_V | Read | Always | 10000000
MSA_UT_Contador_energia_AG_Ent_Vecinal_AC.Energia_acumulada_frio | 78581708 | 15_V | Read | Always | 1000000000000
MSA_UT_Contador_energia_AG_Ent_Vecinal_AF.Volumen | 78581687 | 2_V | Read | Always
MSA_UT_Contador_energia_AG_Ent_Vecinal_AF.Temperatura_impulsion | 78581687 | 4_V | Read | Always
MSA_UT_Contador_energia_AG_Ent_Vecinal_AF.Temperatura_retorno | 78581687 | 5_V | Read | Always
MSA_UT_Contador_energia_AG_Ent_Vecinal_AF.Diferencial_temperatura | 78581687 | 6_V | Read | Always
MSA_UT_Contador_energia_AG_Ent_Vecinal_AF.Potencia | 78581687 | 7_V | Read | Always | 1000000000
MSA_UT_Contador_energia_AG_Ent_Vecinal_AF.Caudal_instantaneo | 78581687 | 9_V | Read | Always
MSA_UT_Contador_energia_AG_Ent_Vecinal_AF.Energia_acumulada_calor | 78581687 | 1_V | Read | Always | 1000000000000
MSA_UT_Contador_energia_AG_Ent_Vecinal_AF.Volumen_AF | 78581687 | 13_V | Read | Always | 10000000
MSA_UT_Contador_energia_AG_Ent_Vecinal_AF.Energia_acumulada_frio | 78581687 | 15_V | Read | Always | 1000000000000
|  |  | Read+Write | Always
|  |  | Read+Write | Always | 0.000000

## MBUS4
|  |  | (All) | (All)
MSA_UM_Contador_energia_Geotermia_AC.Volumen | 78611278 | 2_V | Read | Always
MSA_UM_Contador_energia_Geotermia_AC.Temperatura_impulsion | 78611278 | 4_V | Read | Always
MSA_UM_Contador_energia_Geotermia_AC.Temperatura_retorno | 78611278 | 5_V | Read | Always
MSA_UM_Contador_energia_Geotermia_AC.Diferencial_temperatura | 78611278 | 6_V | Read | Always
MSA_UM_Contador_energia_Geotermia_AC.Potencia | 78611278 | 7_V | Read | Always | 1000000000
MSA_UM_Contador_energia_Geotermia_AC.Caudal_instantaneo | 78611278 | 9_V | Read | Always
MSA_UM_Contador_energia_Geotermia_AC.Energia_acumulada_calor | 78611278 | 1_V | Read | Always | 1000000000000
MSA_UM_Contador_energia_Geotermia_AC.Volumen_AF | 78611278 | 13_V | Read | Always | 10000000
MSA_UM_Contador_energia_Geotermia_AC.Energia_acumulada_frio | 78611278 | 15_V | Read | Always | 1000000000000
MSA_UM_Contador_energia_Geotermia_AF.Volumen | 78611274 | 2_V | Read | Always
MSA_UM_Contador_energia_Geotermia_AF.Temperatura_impulsion | 78611274 | 4_V | Read | Always
MSA_UM_Contador_energia_Geotermia_AF.Temperatura_retorno | 78611274 | 5_V | Read | Always
MSA_UM_Contador_energia_Geotermia_AF.Diferencial_temperatura | 78611274 | 6_V | Read | Always
MSA_UM_Contador_energia_Geotermia_AF.Potencia | 78611274 | 7_V | Read | Always | 1000000000
MSA_UM_Contador_energia_Geotermia_AF.Caudal_instantaneo | 78611274 | 9_V | Read | Always
MSA_UM_Contador_energia_Geotermia_AF.Energia_acumulada_calor | 78611274 | 1_V | Read | Always | 1000000000000
MSA_UM_Contador_energia_Geotermia_AF.Volumen_AF | 78611274 | 13_V | Read | Always | 10000000
MSA_UM_Contador_energia_Geotermia_AF.Energia_acumulada_frio | 78611274 | 15_V | Read | Always | 1000000000000
MSA_UM_Contador_energia_Geotermia_Condens.Volumen | 78581697 | 2_V | Read | Always
MSA_UM_Contador_energia_Geotermia_Condens.Temperatura_impulsion | 78581697 | 4_V | Read | Always
MSA_UM_Contador_energia_Geotermia_Condens.Temperatura_retorno | 78581697 | 5_V | Read | Always
MSA_UM_Contador_energia_Geotermia_Condens.Diferencial_temperatura | 78581697 | 6_V | Read | Always
MSA_UM_Contador_energia_Geotermia_Condens.Potencia | 78581697 | 7_V | Read | Always | 1000000000
MSA_UM_Contador_energia_Geotermia_Condens.Caudal_instantaneo | 78581697 | 9_V | Read | Always
MSA_UM_Contador_energia_Geotermia_Condens.Energia_acumulada_calor | 78581697 | 1_V | Read | Always | 1000000000000
MSA_UM_Contador_energia_Geotermia_Condens.Volumen_AF | 78581697 | 13_V | Read | Always | 10000000
MSA_UM_Contador_energia_Geotermia_Condens.Energia_acumulada_frio | 78581697 | 15_V | Read | Always | 1000000000000
MSA_UM_Contador_energia_Climas.Volumen | 78581695 | 2_V | Read | Always
MSA_UM_Contador_energia_Climas.Temperatura_impulsion | 78581695 | 4_V | Read | Always
MSA_UM_Contador_energia_Climas.Temperatura_retorno | 78581695 | 5_V | Read | Always
MSA_UM_Contador_energia_Climas.Diferencial_temperatura | 78581695 | 6_V | Read | Always
MSA_UM_Contador_energia_Climas.Potencia | 78581695 | 7_V | Read | Always | 1000000000
MSA_UM_Contador_energia_Climas.Caudal_instantaneo | 78581695 | 9_V | Read | Always
MSA_UM_Contador_energia_Climas.Energia_acumulada_calor | 78581695 | 1_V | Read | Always | 1000000000000
MSA_UM_Contador_energia_Climas.Volumen_AF | 78581695 | 13_V | Read | Always | 10000000
MSA_UM_Contador_energia_Climas.Energia_acumulada_frio | 78581695 | 15_V | Read | Always | 1000000000000
MSA_Contador_Almacen_48.Volumen | 55 | 2_V | Read | Always
MSA_Contador_Almacen_48.Temperatura_impulsion | 55 | 4_V | Read | Always
MSA_Contador_Almacen_48.Temperatura_retorno | 55 | 5_V | Read | Always
MSA_Contador_Almacen_48.Diferencial_temperatura | 55 | 6_V | Read | Always
MSA_Contador_Almacen_48.Potencia | 55 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_48.Caudal_instantaneo | 55 | 9_V | Read | Always
MSA_Contador_Almacen_48.Energia_acumulada_calor | 55 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_48.Volumen_AF | 55 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_48.Energia_acumulada_frio | 55 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_46.Volumen | 78293719 | 2_V | Read | Always
MSA_Contador_Almacen_46.Temperatura_impulsion | 78293719 | 4_V | Read | Always
MSA_Contador_Almacen_46.Temperatura_retorno | 78293719 | 5_V | Read | Always
MSA_Contador_Almacen_46.Diferencial_temperatura | 78293719 | 6_V | Read | Always
MSA_Contador_Almacen_46.Potencia | 78293719 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_46.Caudal_instantaneo | 78293719 | 9_V | Read | Always
MSA_Contador_Almacen_46.Energia_acumulada_calor | 78293719 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_46.Volumen_AF | 78293719 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_46.Energia_acumulada_frio | 78293719 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_45.Volumen | 78293718 | 2_V | Read | Always
MSA_Contador_Almacen_45.Temperatura_impulsion | 78293718 | 4_V | Read | Always
MSA_Contador_Almacen_45.Temperatura_retorno | 78293718 | 5_V | Read | Always
MSA_Contador_Almacen_45.Diferencial_temperatura | 78293718 | 6_V | Read | Always
MSA_Contador_Almacen_45.Potencia | 78293718 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_45.Caudal_instantaneo | 78293718 | 9_V | Read | Always
MSA_Contador_Almacen_45.Energia_acumulada_calor | 78293718 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_45.Volumen_AF | 78293718 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_45.Energia_acumulada_frio | 78293718 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_44.Volumen | 78444935 | 2_V | Read | Always
MSA_Contador_Almacen_44.Temperatura_impulsion | 78444935 | 4_V | Read | Always
MSA_Contador_Almacen_44.Temperatura_retorno | 78444935 | 5_V | Read | Always
MSA_Contador_Almacen_44.Diferencial_temperatura | 78444935 | 6_V | Read | Always
MSA_Contador_Almacen_44.Potencia | 78444935 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_44.Caudal_instantaneo | 78444935 | 9_V | Read | Always
MSA_Contador_Almacen_44.Energia_acumulada_calor | 78444935 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_44.Volumen_AF | 78444935 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_44.Energia_acumulada_frio | 78444935 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_43.Volumen | 78293717 | 2_V | Read | Always
MSA_Contador_Almacen_43.Temperatura_impulsion | 78293717 | 4_V | Read | Always
MSA_Contador_Almacen_43.Temperatura_retorno | 78293717 | 5_V | Read | Always
MSA_Contador_Almacen_43.Diferencial_temperatura | 78293717 | 6_V | Read | Always
MSA_Contador_Almacen_43.Potencia | 78293717 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_43.Caudal_instantaneo | 78293717 | 9_V | Read | Always
MSA_Contador_Almacen_43.Energia_acumulada_calor | 78293717 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_43.Volumen_AF | 78293717 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_43.Energia_acumulada_frio | 78293717 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_42.Volumen | 78293716 | 2_V | Read | Always
MSA_Contador_Almacen_42.Temperatura_impulsion | 78293716 | 4_V | Read | Always
MSA_Contador_Almacen_42.Temperatura_retorno | 78293716 | 5_V | Read | Always
MSA_Contador_Almacen_42.Diferencial_temperatura | 78293716 | 6_V | Read | Always
MSA_Contador_Almacen_42.Potencia | 78293716 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_42.Caudal_instantaneo | 78293716 | 9_V | Read | Always
MSA_Contador_Almacen_42.Energia_acumulada_calor | 78293716 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_42.Volumen_AF | 78293716 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_42.Energia_acumulada_frio | 78293716 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_41.Volumen | 78293685 | 2_V | Read | Always
MSA_Contador_Almacen_41.Temperatura_impulsion | 78293685 | 4_V | Read | Always
MSA_Contador_Almacen_41.Temperatura_retorno | 78293685 | 5_V | Read | Always
MSA_Contador_Almacen_41.Diferencial_temperatura | 78293685 | 6_V | Read | Always
MSA_Contador_Almacen_41.Potencia | 78293685 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_41.Caudal_instantaneo | 78293685 | 9_V | Read | Always
MSA_Contador_Almacen_41.Energia_acumulada_calor | 78293685 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_41.Volumen_AF | 78293685 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_41.Energia_acumulada_frio | 78293685 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_40.Volumen | 78293683 | 2_V | Read | Always
MSA_Contador_Almacen_40.Temperatura_impulsion | 78293683 | 4_V | Read | Always
MSA_Contador_Almacen_40.Temperatura_retorno | 78293683 | 5_V | Read | Always
MSA_Contador_Almacen_40.Diferencial_temperatura | 78293683 | 6_V | Read | Always
MSA_Contador_Almacen_40.Potencia | 78293683 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_40.Caudal_instantaneo | 78293683 | 9_V | Read | Always
MSA_Contador_Almacen_40.Energia_acumulada_calor | 78293683 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_40.Volumen_AF | 78293683 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_40.Energia_acumulada_frio | 78293683 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_39.Volumen | 78293681 | 2_V | Read | Always
MSA_Contador_Almacen_39.Temperatura_impulsion | 78293681 | 4_V | Read | Always
MSA_Contador_Almacen_39.Temperatura_retorno | 78293681 | 5_V | Read | Always
MSA_Contador_Almacen_39.Diferencial_temperatura | 78293681 | 6_V | Read | Always
MSA_Contador_Almacen_39.Potencia | 78293681 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_39.Caudal_instantaneo | 78293681 | 9_V | Read | Always
MSA_Contador_Almacen_39.Energia_acumulada_calor | 78293681 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_39.Volumen_AF | 78293681 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_39.Energia_acumulada_frio | 78293681 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_38.Volumen | 78293682 | 2_V | Read | Always
MSA_Contador_Almacen_38.Temperatura_impulsion | 78293682 | 4_V | Read | Always
MSA_Contador_Almacen_38.Temperatura_retorno | 78293682 | 5_V | Read | Always
MSA_Contador_Almacen_38.Diferencial_temperatura | 78293682 | 6_V | Read | Always
MSA_Contador_Almacen_38.Potencia | 78293682 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_38.Caudal_instantaneo | 78293682 | 9_V | Read | Always
MSA_Contador_Almacen_38.Energia_acumulada_calor | 78293682 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_38.Volumen_AF | 78293682 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_38.Energia_acumulada_frio | 78293682 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_37.Volumen | 78444934 | 2_V | Read | Always
MSA_Contador_Almacen_37.Temperatura_impulsion | 78444934 | 4_V | Read | Always
MSA_Contador_Almacen_37.Temperatura_retorno | 78444934 | 5_V | Read | Always
MSA_Contador_Almacen_37.Diferencial_temperatura | 78444934 | 6_V | Read | Always
MSA_Contador_Almacen_37.Potencia | 78444934 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_37.Caudal_instantaneo | 78444934 | 9_V | Read | Always
MSA_Contador_Almacen_37.Energia_acumulada_calor | 78444934 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_37.Volumen_AF | 78444934 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_37.Energia_acumulada_frio | 78444934 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_36.Volumen | 78293692 | 2_V | Read | Always
MSA_Contador_Almacen_36.Temperatura_impulsion | 78293692 | 4_V | Read | Always
MSA_Contador_Almacen_36.Temperatura_retorno | 78293692 | 5_V | Read | Always
MSA_Contador_Almacen_36.Diferencial_temperatura | 78293692 | 6_V | Read | Always
MSA_Contador_Almacen_36.Potencia | 78293692 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_36.Caudal_instantaneo | 78293692 | 9_V | Read | Always
MSA_Contador_Almacen_36.Energia_acumulada_calor | 78293692 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_36.Volumen_AF | 78293692 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_36.Energia_acumulada_frio | 78293692 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_35.Volumen | 78293691 | 2_V | Read | Always
MSA_Contador_Almacen_35.Temperatura_impulsion | 78293691 | 4_V | Read | Always
MSA_Contador_Almacen_35.Temperatura_retorno | 78293691 | 5_V | Read | Always
MSA_Contador_Almacen_35.Diferencial_temperatura | 78293691 | 6_V | Read | Always
MSA_Contador_Almacen_35.Potencia | 78293691 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_35.Caudal_instantaneo | 78293691 | 9_V | Read | Always
MSA_Contador_Almacen_35.Energia_acumulada_calor | 78293691 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_35.Volumen_AF | 78293691 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_35.Energia_acumulada_frio | 78293691 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_34.Volumen | 78293693 | 2_V | Read | Always
MSA_Contador_Almacen_34.Temperatura_impulsion | 78293693 | 4_V | Read | Always
MSA_Contador_Almacen_34.Temperatura_retorno | 78293693 | 5_V | Read | Always
MSA_Contador_Almacen_34.Diferencial_temperatura | 78293693 | 6_V | Read | Always
MSA_Contador_Almacen_34.Potencia | 78293693 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_34.Caudal_instantaneo | 78293693 | 9_V | Read | Always
MSA_Contador_Almacen_34.Energia_acumulada_calor | 78293693 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_34.Volumen_AF | 78293693 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_34.Energia_acumulada_frio | 78293693 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_33.Volumen | 78293694 | 2_V | Read | Always
MSA_Contador_Almacen_33.Temperatura_impulsion | 78293694 | 4_V | Read | Always
MSA_Contador_Almacen_33.Temperatura_retorno | 78293694 | 5_V | Read | Always
MSA_Contador_Almacen_33.Diferencial_temperatura | 78293694 | 6_V | Read | Always
MSA_Contador_Almacen_33.Potencia | 78293694 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_33.Caudal_instantaneo | 78293694 | 9_V | Read | Always
MSA_Contador_Almacen_33.Energia_acumulada_calor | 78293694 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_33.Volumen_AF | 78293694 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_33.Energia_acumulada_frio | 78293694 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_32.Volumen | 78293695 | 2_V | Read | Always
MSA_Contador_Almacen_32.Temperatura_impulsion | 78293695 | 4_V | Read | Always
MSA_Contador_Almacen_32.Temperatura_retorno | 78293695 | 5_V | Read | Always
MSA_Contador_Almacen_32.Diferencial_temperatura | 78293695 | 6_V | Read | Always
MSA_Contador_Almacen_32.Potencia | 78293695 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_32.Caudal_instantaneo | 78293695 | 9_V | Read | Always
MSA_Contador_Almacen_32.Energia_acumulada_calor | 78293695 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_32.Volumen_AF | 78293695 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_32.Energia_acumulada_frio | 78293695 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_31.Volumen | 78293710 | 2_V | Read | Always
MSA_Contador_Almacen_31.Temperatura_impulsion | 78293710 | 4_V | Read | Always
MSA_Contador_Almacen_31.Temperatura_retorno | 78293710 | 5_V | Read | Always
MSA_Contador_Almacen_31.Diferencial_temperatura | 78293710 | 6_V | Read | Always
MSA_Contador_Almacen_31.Potencia | 78293710 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_31.Caudal_instantaneo | 78293710 | 9_V | Read | Always
MSA_Contador_Almacen_31.Energia_acumulada_calor | 78293710 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_31.Volumen_AF | 78293710 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_31.Energia_acumulada_frio | 78293710 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_30.Volumen | 78293709 | 2_V | Read | Always
MSA_Contador_Almacen_30.Temperatura_impulsion | 78293709 | 4_V | Read | Always
MSA_Contador_Almacen_30.Temperatura_retorno | 78293709 | 5_V | Read | Always
MSA_Contador_Almacen_30.Diferencial_temperatura | 78293709 | 6_V | Read | Always
MSA_Contador_Almacen_30.Potencia | 78293709 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_30.Caudal_instantaneo | 78293709 | 9_V | Read | Always
MSA_Contador_Almacen_30.Energia_acumulada_calor | 78293709 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_30.Volumen_AF | 78293709 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_30.Energia_acumulada_frio | 78293709 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_29.Volumen | 78293708 | 2_V | Read | Always
MSA_Contador_Almacen_29.Temperatura_impulsion | 78293708 | 4_V | Read | Always
MSA_Contador_Almacen_29.Temperatura_retorno | 78293708 | 5_V | Read | Always
MSA_Contador_Almacen_29.Diferencial_temperatura | 78293708 | 6_V | Read | Always
MSA_Contador_Almacen_29.Potencia | 78293708 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_29.Caudal_instantaneo | 78293708 | 9_V | Read | Always
MSA_Contador_Almacen_29.Energia_acumulada_calor | 78293708 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_29.Volumen_AF | 78293708 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_29.Energia_acumulada_frio | 78293708 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_28.Volumen | 78293707 | 2_V | Read | Always
MSA_Contador_Almacen_28.Temperatura_impulsion | 78293707 | 4_V | Read | Always
MSA_Contador_Almacen_28.Temperatura_retorno | 78293707 | 5_V | Read | Always
MSA_Contador_Almacen_28.Diferencial_temperatura | 78293707 | 6_V | Read | Always
MSA_Contador_Almacen_28.Potencia | 78293707 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_28.Caudal_instantaneo | 78293707 | 9_V | Read | Always
MSA_Contador_Almacen_28.Energia_acumulada_calor | 78293707 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_28.Volumen_AF | 78293707 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_28.Energia_acumulada_frio | 78293707 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_27.Volumen | 78293706 | 2_V | Read | Always
MSA_Contador_Almacen_27.Temperatura_impulsion | 78293706 | 4_V | Read | Always
MSA_Contador_Almacen_27.Temperatura_retorno | 78293706 | 5_V | Read | Always
MSA_Contador_Almacen_27.Diferencial_temperatura | 78293706 | 6_V | Read | Always
MSA_Contador_Almacen_27.Potencia | 78293706 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_27.Caudal_instantaneo | 78293706 | 9_V | Read | Always
MSA_Contador_Almacen_27.Energia_acumulada_calor | 78293706 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_27.Volumen_AF | 78293706 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_27.Energia_acumulada_frio | 78293706 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_26.Volumen | 78293701 | 2_V | Read | Always
MSA_Contador_Almacen_26.Temperatura_impulsion | 78293701 | 4_V | Read | Always
MSA_Contador_Almacen_26.Temperatura_retorno | 78293701 | 5_V | Read | Always
MSA_Contador_Almacen_26.Diferencial_temperatura | 78293701 | 6_V | Read | Always
MSA_Contador_Almacen_26.Potencia | 78293701 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_26.Caudal_instantaneo | 78293701 | 9_V | Read | Always
MSA_Contador_Almacen_26.Energia_acumulada_calor | 78293701 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_26.Volumen_AF | 78293701 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_26.Energia_acumulada_frio | 78293701 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_25.Volumen | 78293699 | 2_V | Read | Always
MSA_Contador_Almacen_25.Temperatura_impulsion | 78293699 | 4_V | Read | Always
MSA_Contador_Almacen_25.Temperatura_retorno | 78293699 | 5_V | Read | Always
MSA_Contador_Almacen_25.Diferencial_temperatura | 78293699 | 6_V | Read | Always
MSA_Contador_Almacen_25.Potencia | 78293699 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_25.Caudal_instantaneo | 78293699 | 9_V | Read | Always
MSA_Contador_Almacen_25.Energia_acumulada_calor | 78293699 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_25.Volumen_AF | 78293699 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_25.Energia_acumulada_frio | 78293699 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_24.Volumen | 78293700 | 2_V | Read | Always
MSA_Contador_Almacen_24.Temperatura_impulsion | 78293700 | 4_V | Read | Always
MSA_Contador_Almacen_24.Temperatura_retorno | 78293700 | 5_V | Read | Always
MSA_Contador_Almacen_24.Diferencial_temperatura | 78293700 | 6_V | Read | Always
MSA_Contador_Almacen_24.Potencia | 78293700 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_24.Caudal_instantaneo | 78293700 | 9_V | Read | Always
MSA_Contador_Almacen_24.Energia_acumulada_calor | 78293700 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_24.Volumen_AF | 78293700 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_24.Energia_acumulada_frio | 78293700 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_23.Volumen | 78293711 | 2_V | Read | Always
MSA_Contador_Almacen_23.Temperatura_impulsion | 78293711 | 4_V | Read | Always
MSA_Contador_Almacen_23.Temperatura_retorno | 78293711 | 5_V | Read | Always
MSA_Contador_Almacen_23.Diferencial_temperatura | 78293711 | 6_V | Read | Always
MSA_Contador_Almacen_23.Potencia | 78293711 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_23.Caudal_instantaneo | 78293711 | 9_V | Read | Always
MSA_Contador_Almacen_23.Energia_acumulada_calor | 78293711 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_23.Volumen_AF | 78293711 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_23.Energia_acumulada_frio | 78293711 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_22.Volumen | 78293715 | 2_V | Read | Always
MSA_Contador_Almacen_22.Temperatura_impulsion | 78293715 | 4_V | Read | Always
MSA_Contador_Almacen_22.Temperatura_retorno | 78293715 | 5_V | Read | Always
MSA_Contador_Almacen_22.Diferencial_temperatura | 78293715 | 6_V | Read | Always
MSA_Contador_Almacen_22.Potencia | 78293715 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_22.Caudal_instantaneo | 78293715 | 9_V | Read | Always
MSA_Contador_Almacen_22.Energia_acumulada_calor | 78293715 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_22.Volumen_AF | 78293715 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_22.Energia_acumulada_frio | 78293715 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_21.Volumen | 78293713 | 2_V | Read | Always
MSA_Contador_Almacen_21.Temperatura_impulsion | 78293713 | 4_V | Read | Always
MSA_Contador_Almacen_21.Temperatura_retorno | 78293713 | 5_V | Read | Always
MSA_Contador_Almacen_21.Diferencial_temperatura | 78293713 | 6_V | Read | Always
MSA_Contador_Almacen_21.Potencia | 78293713 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_21.Caudal_instantaneo | 78293713 | 9_V | Read | Always
MSA_Contador_Almacen_21.Energia_acumulada_calor | 78293713 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_21.Volumen_AF | 78293713 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_21.Energia_acumulada_frio | 78293713 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_20.Volumen | 78293712 | 2_V | Read | Always
MSA_Contador_Almacen_20.Temperatura_impulsion | 78293712 | 4_V | Read | Always
MSA_Contador_Almacen_20.Temperatura_retorno | 78293712 | 5_V | Read | Always
MSA_Contador_Almacen_20.Diferencial_temperatura | 78293712 | 6_V | Read | Always
MSA_Contador_Almacen_20.Potencia | 78293712 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_20.Caudal_instantaneo | 78293712 | 9_V | Read | Always
MSA_Contador_Almacen_20.Energia_acumulada_calor | 78293712 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_20.Volumen_AF | 78293712 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_20.Energia_acumulada_frio | 78293712 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_19.Volumen | 78293686 | 2_V | Read | Always
MSA_Contador_Almacen_19.Temperatura_impulsion | 78293686 | 4_V | Read | Always
MSA_Contador_Almacen_19.Temperatura_retorno | 78293686 | 5_V | Read | Always
MSA_Contador_Almacen_19.Diferencial_temperatura | 78293686 | 6_V | Read | Always
MSA_Contador_Almacen_19.Potencia | 78293686 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_19.Caudal_instantaneo | 78293686 | 9_V | Read | Always
MSA_Contador_Almacen_19.Energia_acumulada_calor | 78293686 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_19.Volumen_AF | 78293686 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_19.Energia_acumulada_frio | 78293686 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_18.Volumen | 78293714 | 2_V | Read | Always
MSA_Contador_Almacen_18.Temperatura_impulsion | 78293714 | 4_V | Read | Always
MSA_Contador_Almacen_18.Temperatura_retorno | 78293714 | 5_V | Read | Always
MSA_Contador_Almacen_18.Diferencial_temperatura | 78293714 | 6_V | Read | Always
MSA_Contador_Almacen_18.Potencia | 78293714 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_18.Caudal_instantaneo | 78293714 | 9_V | Read | Always
MSA_Contador_Almacen_18.Energia_acumulada_calor | 78293714 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_18.Volumen_AF | 78293714 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_18.Energia_acumulada_frio | 78293714 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_17.Volumen | 78293698 | 2_V | Read | Always
MSA_Contador_Almacen_17.Temperatura_impulsion | 78293698 | 4_V | Read | Always
MSA_Contador_Almacen_17.Temperatura_retorno | 78293698 | 5_V | Read | Always
MSA_Contador_Almacen_17.Diferencial_temperatura | 78293698 | 6_V | Read | Always
MSA_Contador_Almacen_17.Potencia | 78293698 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_17.Caudal_instantaneo | 78293698 | 9_V | Read | Always
MSA_Contador_Almacen_17.Energia_acumulada_calor | 78293698 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_17.Volumen_AF | 78293698 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_17.Energia_acumulada_frio | 78293698 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_16_15_14.Volumen | 78293697 | 2_V | Read | Always
MSA_Contador_Almacen_16_15_14.Temperatura_impulsion | 78293697 | 4_V | Read | Always
MSA_Contador_Almacen_16_15_14.Temperatura_retorno | 78293697 | 5_V | Read | Always
MSA_Contador_Almacen_16_15_14.Diferencial_temperatura | 78293697 | 6_V | Read | Always
MSA_Contador_Almacen_16_15_14.Potencia | 78293697 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_16_15_14.Caudal_instantaneo | 78293697 | 9_V | Read | Always
MSA_Contador_Almacen_16_15_14.Energia_acumulada_calor | 78293697 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_16_15_14.Volumen_AF | 78293697 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_16_15_14.Energia_acumulada_frio | 78293697 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_13_12.Volumen | 78293696 | 2_V | Read | Always
MSA_Contador_Almacen_13_12.Temperatura_impulsion | 78293696 | 4_V | Read | Always
MSA_Contador_Almacen_13_12.Temperatura_retorno | 78293696 | 5_V | Read | Always
MSA_Contador_Almacen_13_12.Diferencial_temperatura | 78293696 | 6_V | Read | Always
MSA_Contador_Almacen_13_12.Potencia | 78293696 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_13_12.Caudal_instantaneo | 78293696 | 9_V | Read | Always
MSA_Contador_Almacen_13_12.Energia_acumulada_calor | 78293696 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_13_12.Volumen_AF | 78293696 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_13_12.Energia_acumulada_frio | 78293696 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_11.Volumen | 78293702 | 2_V | Read | Always
MSA_Contador_Almacen_11.Temperatura_impulsion | 78293702 | 4_V | Read | Always
MSA_Contador_Almacen_11.Temperatura_retorno | 78293702 | 5_V | Read | Always
MSA_Contador_Almacen_11.Diferencial_temperatura | 78293702 | 6_V | Read | Always
MSA_Contador_Almacen_11.Potencia | 78293702 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_11.Caudal_instantaneo | 78293702 | 9_V | Read | Always
MSA_Contador_Almacen_11.Energia_acumulada_calor | 78293702 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_11.Volumen_AF | 78293702 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_11.Energia_acumulada_frio | 78293702 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_10.Volumen | 78293678 | 2_V | Read | Always
MSA_Contador_Almacen_10.Temperatura_impulsion | 78293678 | 4_V | Read | Always
MSA_Contador_Almacen_10.Temperatura_retorno | 78293678 | 5_V | Read | Always
MSA_Contador_Almacen_10.Diferencial_temperatura | 78293678 | 6_V | Read | Always
MSA_Contador_Almacen_10.Potencia | 78293678 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_10.Caudal_instantaneo | 78293678 | 9_V | Read | Always
MSA_Contador_Almacen_10.Energia_acumulada_calor | 78293678 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_10.Volumen_AF | 78293678 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_10.Energia_acumulada_frio | 78293678 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_9.Volumen | 78293676 | 2_V | Read | Always
MSA_Contador_Almacen_9.Temperatura_impulsion | 78293676 | 4_V | Read | Always
MSA_Contador_Almacen_9.Temperatura_retorno | 78293676 | 5_V | Read | Always
MSA_Contador_Almacen_9.Diferencial_temperatura | 78293676 | 6_V | Read | Always
MSA_Contador_Almacen_9.Potencia | 78293676 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_9.Caudal_instantaneo | 78293676 | 9_V | Read | Always
MSA_Contador_Almacen_9.Energia_acumulada_calor | 78293676 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_9.Volumen_AF | 78293676 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_9.Energia_acumulada_frio | 78293676 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_8.Volumen | 78293677 | 2_V | Read | Always
MSA_Contador_Almacen_8.Temperatura_impulsion | 78293677 | 4_V | Read | Always
MSA_Contador_Almacen_8.Temperatura_retorno | 78293677 | 5_V | Read | Always
MSA_Contador_Almacen_8.Diferencial_temperatura | 78293677 | 6_V | Read | Always
MSA_Contador_Almacen_8.Potencia | 78293677 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_8.Caudal_instantaneo | 78293677 | 9_V | Read | Always
MSA_Contador_Almacen_8.Energia_acumulada_calor | 78293677 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_8.Volumen_AF | 78293677 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_8.Energia_acumulada_frio | 78293677 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_7.Volumen | 78293679 | 2_V | Read | Always
MSA_Contador_Almacen_7.Temperatura_impulsion | 78293679 | 4_V | Read | Always
MSA_Contador_Almacen_7.Temperatura_retorno | 78293679 | 5_V | Read | Always
MSA_Contador_Almacen_7.Diferencial_temperatura | 78293679 | 6_V | Read | Always
MSA_Contador_Almacen_7.Potencia | 78293679 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_7.Caudal_instantaneo | 78293679 | 9_V | Read | Always
MSA_Contador_Almacen_7.Energia_acumulada_calor | 78293679 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_7.Volumen_AF | 78293679 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_7.Energia_acumulada_frio | 78293679 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_6.Volumen | 78293680 | 2_V | Read | Always
MSA_Contador_Almacen_6.Temperatura_impulsion | 78293680 | 4_V | Read | Always
MSA_Contador_Almacen_6.Temperatura_retorno | 78293680 | 5_V | Read | Always
MSA_Contador_Almacen_6.Diferencial_temperatura | 78293680 | 6_V | Read | Always
MSA_Contador_Almacen_6.Potencia | 78293680 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_6.Caudal_instantaneo | 78293680 | 9_V | Read | Always
MSA_Contador_Almacen_6.Energia_acumulada_calor | 78293680 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_6.Volumen_AF | 78293680 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_6.Energia_acumulada_frio | 78293680 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_5.Volumen | 78293690 | 2_V | Read | Always
MSA_Contador_Almacen_5.Temperatura_impulsion | 78293690 | 4_V | Read | Always
MSA_Contador_Almacen_5.Temperatura_retorno | 78293690 | 5_V | Read | Always
MSA_Contador_Almacen_5.Diferencial_temperatura | 78293690 | 6_V | Read | Always
MSA_Contador_Almacen_5.Potencia | 78293690 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_5.Caudal_instantaneo | 78293690 | 9_V | Read | Always
MSA_Contador_Almacen_5.Energia_acumulada_calor | 78293690 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_5.Volumen_AF | 78293690 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_5.Energia_acumulada_frio | 78293690 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_3_4.Volumen | 78293689 | 2_V | Read | Always
MSA_Contador_Almacen_3_4.Temperatura_impulsion | 78293689 | 4_V | Read | Always
MSA_Contador_Almacen_3_4.Temperatura_retorno | 78293689 | 5_V | Read | Always
MSA_Contador_Almacen_3_4.Diferencial_temperatura | 78293689 | 6_V | Read | Always
MSA_Contador_Almacen_3_4.Potencia | 78293689 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_3_4.Caudal_instantaneo | 78293689 | 9_V | Read | Always
MSA_Contador_Almacen_3_4.Energia_acumulada_calor | 78293689 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_3_4.Volumen_AF | 78293689 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_3_4.Energia_acumulada_frio | 78293689 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_2.Volumen | 78293688 | 2_V | Read | Always
MSA_Contador_Almacen_2.Temperatura_impulsion | 78293688 | 4_V | Read | Always
MSA_Contador_Almacen_2.Temperatura_retorno | 78293688 | 5_V | Read | Always
MSA_Contador_Almacen_2.Diferencial_temperatura | 78293688 | 6_V | Read | Always
MSA_Contador_Almacen_2.Potencia | 78293688 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_2.Caudal_instantaneo | 78293688 | 9_V | Read | Always
MSA_Contador_Almacen_2.Energia_acumulada_calor | 78293688 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_2.Volumen_AF | 78293688 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_2.Energia_acumulada_frio | 78293688 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_1.Volumen | 78293687 | 2_V | Read | Always
MSA_Contador_Almacen_1.Temperatura_impulsion | 78293687 | 4_V | Read | Always
MSA_Contador_Almacen_1.Temperatura_retorno | 78293687 | 5_V | Read | Always
MSA_Contador_Almacen_1.Diferencial_temperatura | 78293687 | 6_V | Read | Always
MSA_Contador_Almacen_1.Potencia | 78293687 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_1.Caudal_instantaneo | 78293687 | 9_V | Read | Always
MSA_Contador_Almacen_1.Energia_acumulada_calor | 78293687 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_1.Volumen_AF | 78293687 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_1.Energia_acumulada_frio | 78293687 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_46B.Volumen | 78293704 | 2_V | Read | Always
MSA_Contador_Almacen_46B.Temperatura_impulsion | 78293704 | 4_V | Read | Always
MSA_Contador_Almacen_46B.Temperatura_retorno | 78293704 | 5_V | Read | Always
MSA_Contador_Almacen_46B.Diferencial_temperatura | 78293704 | 6_V | Read | Always
MSA_Contador_Almacen_46B.Potencia | 78293704 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_46B.Caudal_instantaneo | 78293704 | 9_V | Read | Always
MSA_Contador_Almacen_46B.Energia_acumulada_calor | 78293704 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_46B.Volumen_AF | 78293704 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_46B.Energia_acumulada_frio | 78293704 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_46C.Volumen | 78293705 | 2_V | Read | Always
MSA_Contador_Almacen_46C.Temperatura_impulsion | 78293705 | 4_V | Read | Always
MSA_Contador_Almacen_46C.Temperatura_retorno | 78293705 | 5_V | Read | Always
MSA_Contador_Almacen_46C.Diferencial_temperatura | 78293705 | 6_V | Read | Always
MSA_Contador_Almacen_46C.Potencia | 78293705 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_46C.Caudal_instantaneo | 78293705 | 9_V | Read | Always
MSA_Contador_Almacen_46C.Energia_acumulada_calor | 78293705 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_46C.Volumen_AF | 78293705 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_46C.Energia_acumulada_frio | 78293705 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_221_paletas.Volumen | 78293703 | 2_V | Read | Always
MSA_Contador_Almacen_221_paletas.Temperatura_impulsion | 78293703 | 4_V | Read | Always
MSA_Contador_Almacen_221_paletas.Temperatura_retorno | 78293703 | 5_V | Read | Always
MSA_Contador_Almacen_221_paletas.Diferencial_temperatura | 78293703 | 6_V | Read | Always
MSA_Contador_Almacen_221_paletas.Potencia | 78293703 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_221_paletas.Caudal_instantaneo | 78293703 | 9_V | Read | Always
MSA_Contador_Almacen_221_paletas.Energia_acumulada_calor | 78293703 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_221_paletas.Volumen_AF | 78293703 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_221_paletas.Energia_acumulada_frio | 78293703 | 15_V | Read | Always | 1000000000
MSA_Contador_Almacen_46CBis.Volumen | 78293684 | 2_V | Read | Always
MSA_Contador_Almacen_46CBis.Temperatura_impulsion | 78293684 | 4_V | Read | Always
MSA_Contador_Almacen_46CBis.Temperatura_retorno | 78293684 | 5_V | Read | Always
MSA_Contador_Almacen_46CBis.Diferencial_temperatura | 78293684 | 6_V | Read | Always
MSA_Contador_Almacen_46CBis.Potencia | 78293684 | 7_V | Read | Always | 1000000000
MSA_Contador_Almacen_46CBis.Caudal_instantaneo | 78293684 | 9_V | Read | Always
MSA_Contador_Almacen_46CBis.Energia_acumulada_calor | 78293684 | 1_V | Read | Always | 1000000000
MSA_Contador_Almacen_46CBis.Volumen_AF | 78293684 | 13_V | Read | Always | 10000000
MSA_Contador_Almacen_46CBis.Energia_acumulada_frio | 78293684 | 15_V | Read | Always | 1000000000
|  |  | Read+Write | Always